## Sheet1
BEGIN_DATE | END_DATE | FACILITY_NAME | COUNTY | CITY | OVERFLOW_LOCATION | QUANTITY | NOTES | OVERFLOW_TYPE | DISTRICT | PERMIT_NUMBER | WASTEWATER_FACILITY_TYPE | SPILL_RECV_WATERBODY_TYPE | SPILL_POSTING_LOCATION | SPILL_PRIMARY_CAUSE | INCIDENT_REPORTED_BY | CALL_RECEIVED_BY | SPILL_ENTERED_BY | EMPLOYEE_RESPONSIBLE | INCIDENT_REPORTED_DATE | RIVER_BASIN | POSTING_BEGIN_DATE | MONITORING_BEGIN_DATE | MONITORING_END_DATE | IS_ENTERED_WATERWAY | WATERWAY_IMPACTED | IS_SIGN_POSTED | IS_MEDIA_CONTACTED | IS_DEAD_FISH_REPORTED | IS_PUB_NOTICE_UND | IS_WQ_VIOLATION | IS_CHATTAHOOCHEE_NOTIF | IS_FISHERY_NOTIF | IS_OUTFALL_SPILL | IS_COASTAL_NOTIF | IS_DW_NOTIF | IS_EMERG_NOTIF | IS_MAJ_SAMPLING_UND | IS_MAJOR | IS_SEVEN_DAY_SAMPL_RCV | FECAL_COLIFORM | IS_BORDER_ST_NOTIF | CAUSE_COMMENT | CORR_ACTION_COMMENT | CALL_RECV_BY_EMP_ID | EMP_RESP_ID | SPILL_ENTERED_BY_ID | ENTRY_DATE | IS_DIST_ENV_NOTIF | IS_HEALTH_NOTIF | IS_DOWNSTREAM_USERS_NOTIF | IS_THIRD_MONTH_SAMPLING_RECD | IS_TWELFTH_MONTH_SAMPLING_RECD | IS_IMPACTED_WATERWAY_303 | CONTACT_PERSON | CONTACT_PHONE | CONTACT_ORGANIZATION | CONTACT_ADDRESS | PERSON_REPORTING_SPILL | PERSON_REPORTING_SPILL_PHONE | PERSON_REPORTING_SPILL_ORG | PERSON_REPORTING_SPILL_ADDRESS | RESPONSIBLE_AUTHORITY | RESPONSIBLE_AUTHORITY_PHONE | RESPONSIBLE_AUTHORITY_ADDRESS | BOD | TSS | DURATION_MIGRATED
2015-03-24 | 2015-03-24 | CITY OF SMYRNA - PUB WORKS | Cobb | Smyrna | 3778 Lake Drive | 2000 | The affected site was cleaned of debris, limed to neutralize the area and deodorant applied to neutralize odor. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Mansoor Alaeddini | Reginald Williamson | Reginald Williamson | 3/26/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Nickjack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The City of Smyrna took corrective action by removing a blockage in the pipe. | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-12 | 2016-01-07 | Cobb County MS4 | Cobb |  | 1306 Old Powder Springs Road | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Cobb Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of South Cobb Creek. | The crew stopped the overflow at 2:45 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5939 Springview Drive, Morrow MH # 2199022 | 2700 | Fax received on 03/28/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Vandalism |  |  | Paul Moisan | Paul Moisan | 3/28/2017 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was vandalism. | Cleared blockage (removed debris) from manhole (rocks and sticks). |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0 | Charles Ecton |  | Clayton Co Water Authority
2018-07-06 | 2018-07-06 | Lowndes County (South Regional WPCP) | Lowndes | Valdosta | Val-Tech Road - Lowndes County | 9300 | Email sent 2018-07-06 | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Collection System | Ground |  | Pipe failure |  |  |  | Alys Hannum | 7/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Split in the force main | Pump truck bypass, lime spread. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Conley | 3936 Honeysuckle Lane | 7200 | REC FAX 2/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Storm Drain, Stream | Stream | Grease |  |  | Emily Wingo | Emily Wingo | 2/18/2015 12:00:00 AM | Ocmulgee | 2/17/2015 12:00:00 AM |  |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | GREASE | Cleared Blockage. Televise Line |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-18 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY
2015-03-11 | 2015-03-11 |  | Columbia |  | Wooded area behind 4059 Payton Place | 8500 | fax received 3/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Marzieh Shahbazah | Marzieh Shahbazah | Kim Hembree | 3/12/2015 12:00:00 AM |  |  |  |  | 1 | Walton Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 33e3f7fa-ee02-11e0-b8d8-000c29971acc | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 33e3f7fa-ee02-11e0-b8d8-000c29971acc | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-03-15 | 2015-03-15 | East Point (City of)- Sewers | Fulton | East Point | 2670 Rolling Brook Trail between manhole ID C-195-045 and C-196-026 | 3000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The probable cause of the spill was due to debris in the main resulting into a discharge into the Camp Creek Basin. | The City's crew jetted and vacuumed out the main to remove the blockage, and cleaned the affected area as required. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-30 | 2017-05-30 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Duralee Ln Extension - Douglasville MH #10957 | 4800 | email received on 05/30/2017; fax received on 05/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 5/30/2017 12:00:00 AM | Chattahoochee | 5/30/2017 12:00:00 AM |  |  | 1 | Slater Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction grade stake in the outlet pipe of the manhole, causing a buildup of debris and then blockage. | The debris was removed, and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-18 | 2016-05-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 134 Lucerne Street, Decatur | 41250 | Notification received on May 20, , 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 5/18/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 19:45 hours, when a crew situated abypass pump to contain the spill until the repair was made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-23 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-11 | 2018-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 5675 Bucknell Dr. SW - ATL | 870000 | Unknown as of 2018-01-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  |  | Alys Hannum | 1/12/2018 12:00:00 AM |  | 1/11/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Unknown |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-09 | 2017-10-09 | West Point, City of (West Point WPCP) | Troup | West Point | West 8th Street on Bank of Chattahoochee River, West Point. | 1000 | Telephone call received on 10/09/2017; report emailed to EPD on 10/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020052 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to 6" - 6.5" of heavy rains associated with Hurricane Nate over a 12 - 16 hour period which flooded some areas and covered manholes forcing water into the system at a higher rate than it is designed to receive. | Once the flood waters from the heavy rain receded, the manholes that were under water stopped filling and the leaking stopped. The city will check the rubber gasket in the bolted ring and cover to see if replacement is necessary. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-20 | 0 | 1 | 1 | 0 | 0 | 0
2016-11-08 | 2016-11-08 | Jackson, City of (Yellow Water Creek WPCP) | Butts | Jackson | Brownlee Rd. Right of Way - Jackson | 0 | No spill entered state waters | Raw Sewage | Wastewater Regulatory Program | GA0021831 | Collection System | Ditch |  | Grease |  |  | Alys Hannum | Hsin Yeh | 11/10/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The 8" SS was jetted and vacuumed. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-08 | 2016-02-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2086 Lenox Road, NE | 4090 | fax received 2/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/9/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-05 | 2017-09-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1380 Battle View Dr. NW - ATL | 1110 | Fax received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 9/6/2017 12:00:00 AM |  | 9/5/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 901 North Ridge Dr. | 500 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defect in Pipe |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-02-20 | Hazlehurst, City of (Bully Creek WPCP) | Jeff Davis | Hazlehurst | Bully Creek and the Ogmulgee River | 1000000 |  | Raw Sewage | Coastal District | GA0036765 |  | Stream | Stream |  |  | Bill Hawthorne | Bill Hawthorne |  | 1/23/2017 2:10:00 PM |  | 1/25/2017 12:00:00 AM | 2017-03-23 |  | 1 | Bully Creek & Ogmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall, I&I and WWTP at half capacity caused the major spill onto Bully Creek and the Ogmulgee River. | No corrective actions were conducted as the City claimed that they had no control measures to stop the spill. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-03-24 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-17 | 2016-02-18 |  | Fulton | Sandy Springs | 5450 Interstate North Parkway Sandy Springs 30328 | 7120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/17/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 639 North Ave. - ATL | 100 | Fax received 2017-03-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/28/2017 12:00:00 AM |  | 3/27/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2836 Fairlane Drive, SE | 5 | fax received 10/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/12/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-12 | 2015-02-12 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2102 Lenox Road, NE | 200 | fax received 2/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 2/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-13 | 2016-07-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 8644 Covington Highway, Lithonia | 44000 | Notification received on July 15, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 7/13/2016 12:00:00 AM |  |  |  |  | 0 | Tom George Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 12:15 hours, when a crew replaced eight (8) feet of the force main with ten (10) inch ductile iron pipe. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-26 | 2016-04-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Road, SW | 20 | fax received 4/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/27/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-17 | 2015-02-17 | Winder, City of (Marburg Creek WPCP) | Barrow | Winder | City of Winder - Marburg Creek WWTP | 21250 | Verbal and email notification received 2/18/2015. | Undisinfected Secondary Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Power failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/23/2015 12:00:00 AM |  |  |  |  | 1 | Marburg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to a power outage, the facility was unable to pump to reject pond or treat with UV. When the influent holding tank was full, the facility had to send the flow through the plant and out the outfall without UV disinfection. This facility does not have any backup power. | Power restored | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER | 770-868-0863
2017-08-24 | 2017-08-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3480 Mill Creek Road, Atlanta | 25 | Notification received on August 29, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 8/24/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tissue blockage | The problem was corrected immediately when the contractor removed the sewer plug and stopped the spill. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Wadley, City of (Wadley WPCP) | Jefferson |  |  | 1616 |  | Primary Effuent | Northeast District - Augusta | GA0021024 | WWTP | Other | Stream | Wet weather |  | Madara Tyler | Madara Tyler | Madara Tyler | 1/14/2016 12:00:00 AM | Ogeechee | 1/13/2016 12:00:00 AM | 2016-01-13 |  | 0 | Williamson Swamp creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill caused by high rainfall amount of Dec 2015 | sampling for fecal, measuring pH, DO and temperature | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 2016-01-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-18 | 2016-08-18 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 42.1 Plant flow was 0.934 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 42.1
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 500 Block of Rouse Road | 1290 | Verbal/Email notification received 2/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive Rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Argonne Drive - Augusta | 123000 | Fax received 2017-01-03, update received 2017-01-12 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-05 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding caused highly diluted wastewater to begin running out of several manholes by 11:00 AM on January 2, 2017. | Line is being monitored until normal flow resumes. Notifications posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-30 | 2016-03-30 | Cobb County MS4 | Cobb |  | 2940 Blue Sky Place | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/30/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Soapy creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel and Grease | Lime and Cleanup around spill | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-23 | 2017-11-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2448 Colorado Trl. SW - ATL | 1440 | Fax sent 2017-11-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/27/2017 12:00:00 AM |  | 11/23/2017 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to control the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 6560 Oakwood Drive, Douglasville MH #10484 | 650 | Fax received on 03/28/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 3/28/2017 12:00:00 AM | Chattahoochee | 3/27/2017 12:00:00 AM |  |  | 1 | Tributary J to Anneewakee Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was asphalt lodged in the outlet pipe of the manhole. | Crews cleared the blockage and cleaned and disinfected the area around the manhole. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0 | Lyndsey Sargent |  | Douglasville - Douglas County Water and Sewer Authority
2016-02-24 | 2016-02-24 | Tifton, City of (New River WPCP) | Tift | Tifton | 61 TC Gordon Road, Tifton | 2000 | Telephone call received on 02/24/2016; report received via email on 02/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/24/2016 12:00:00 AM |  |  |  |  | 1 | Cow House Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | Mitigated with hydrated lime | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-03 | 0 | 1 | 0 | 0 | 0 | 0 | Trey Crisp | 478.335.4612 | TIFTON NEW RIVER WPCP
2015-04-12 | 2015-04-12 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2631 Cascade Road, SW | 405 | fax received 4/13/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 4/13/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | The crew repaired the bypass pump. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-25 | 2015-03-25 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 641 Hemlock Circle, SE | 258 | fax received 3/26/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/26/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-04 | 2016-09-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1300 Block of North Ashley Street | 5675 | verbal notification received 9/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Equipment failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/4/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | Repaired bypass pump | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-03-25 | 2015-03-25 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 50.0 mg/l
2018-04-28 | 2018-04-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4542 Bexley Drive, Stone Mountain GA 30083 | 1560 | manhole 15-224-s200 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/28/2018 5:00:00 PM | Ocmulgee | 4/28/2018 12:00:00 AM |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Chandler Haulk Lift Station | 22200 | CTS No. 78635 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/26/2015 12:00:00 AM |  |  |  |  | 1 | `Little Haynes Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2017-05-03 | 2017-05-03 | Buford, City of (Southside WPCP) | Gwinnett | Buford | Brickton Station, Hamilton Mill Rd - Buford. | 15001 | Phone notification 2017-05-03. Fax received 2017-05-05. | Raw Sewage | Wastewater Regulatory Program | GA0023167 | Collection System | Ground |  | Other |  | Alys Hannum | Alys Hannum | Alys Hannum | 5/5/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | A large tree fell on an aerial line in the woods, broke the line, and knocked the supporting pier down. | City initialized repairs. A berm was put in place around the spill to prevent it from reaching state waters. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-05 | 2018-04-05 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 3339 Country Club VLG Ln - Norcross | 6248 | Fax sent 2018-04-05 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/5/2018 12:00:00 AM |  | 4/5/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Bromolow Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked area and spread lime; placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 1010000 | call from Kris Garcia received 11/02/2015, 10:45am | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-02 | 2016-04-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1600 Block James P Rogers | 92150 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2017-10-20 | 2017-10-20 | Marietta (City of)- Sewers | Cobb | Marietta | 1070 Atlanta Industrial | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 1hp submersible pump for a service line at a bakery failed and caused service leakage into a nearby storm drain. | Detail in report | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 140 Block of Gornto Road | 80650 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2017-07-26 | 2017-07-26 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 4342 Roswell Drive - Martinez | 4500 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/26/2017 12:00:00 AM |  |  | 1 | Tributary to Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive Rainfall | Monitored area. Follow-up inspection of area. Continue to look for points of inflow. Posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-11 | 2016-11-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3731 Buford Hwy, Atlanta | 4080 | Notification received on November 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/12/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:50 hours, when a crew pressure washed the 8" sewer main 235ft, clearing the grease and rages blockage which restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-19 | 2017-03-19 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 4745 Lowell Court - Cumming | 4200 | Email received 2017-03-20 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/20/2017 12:00:00 AM |  |  |  |  | 1 | Cheatham Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bricks, paper, heavy grease buildup. | Jetted lines, removed bricks, large pieces of grease and paper. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 198 Darque Road, Savannah, GA | 3000 | Initial notification via phone and full report received via email 9/12. | Raw Sewage | Coastal District | GA0038326 | Lift Station | Canal | Canal | Natural Disaster |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/12/2017 12:00:00 AM | Savannah | 10/12/2017 12:00:00 AM |  |  | 1 | Pipemaker's Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The transfer switch at LS 40 failed to switch the power source over to the generator when power was lost during Hurricane Irma. | Turned power on to station. Investigated cause of transfer failure. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2016-02-23 | 2016-02-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8890 Roberts Road, Jonesboro Manhole 2202496 | 1581 | Fax and voice mail received on 02/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/23/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Pumped out, and pumps were brought back on line and were able to keep up with the flows. | Pumped out, and pumps were brought back on line and were able to keep up with the flows. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-29 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-22 | 2017-06-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | - Spill Report Cancelled See Documents- | 0 | - Spill Report Cancelled See Documents- | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream |  |  |  | Alys Hannum | Alys Hannum | 6/23/2017 12:00:00 AM |  | 6/22/2017 12:00:00 AM |  |  | 0 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | - Spill Report Cancelled See Documents- | - Spill Report Cancelled See Documents- |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-27 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-17 | 2018-09-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3954 Memorial College Avenue Clarkston GA 30021 | 4800 | manhole 18-043-s058 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  |  | Dillon Rodenbaugh | 9/18/2018 10:56:00 AM | Ocmulgee |  |  |  | 1 | Snapfinger Creek Tributary C | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed to remove grease and debris |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 |  | 2018-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-07 | 2015-07-21 |  | Cobb | Austell | 3891 Doe Run Dr. | 1200 | Cobb County Crew found the spill and contacted Austell and met with City Crew. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sweetwater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole not sealed | Cobb | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-15 | 2018-01-15 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 2734 Sterling Dr. - Lawrenceville | 5629 | Fax sent 2018-01-15 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System |  | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/15/2018 12:00:00 AM |  | 1/15/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Little Suwanee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper and other products | Raked area and spread lime; placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-02 | 2017-05-02 | Forsyth County (Fowler WRF) | Forsyth | Cumming | 5110 Skylark Creek Ct. - Cumming | 3200 | Fax received 2017-05-03 | Raw Sewage | Wastewater Regulatory Program | GA0038695 | Collection System | Ground | Ditch | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/3/2017 12:00:00 AM |  | 5/2/2017 12:00:00 AM |  |  | 0 | Dry Land | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Portion of concrete from the manhole broke and fell into pipe, clogged it. Grease contributed. | Removed concrete from table, removed gravel and grease, jetted and vacced the line. Signs posted. 20 bags of lime applied to affected area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-09 | 2018-01-09 | Cobb County Water System | Cobb | Marietta | 1644 Sir Galahad Drive | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Olley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped the overflow at 7:21 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | City of Fort Oglethorpe | Catoosa |  |  | 1 |  | Raw Sewage | Mountain District - Cartersville | GAU060002 | Pump Station | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/8/2016 12:00:00 AM | Tennessee |  |  |  | 0 | Spring Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rainfall |  | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3203 East Lindsay Drive, Columbus | 19941 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Lindsay Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-04 | 2016-03-04 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 7654 Connell Drive, Jonesboro Manhole #2215621 | 32000 | Telephone call and fax received on 03/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/6/2016 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | The pipes failed. | Sewage was pumped out, and down stream manhole was pumped down. Sewer lines will be replaced. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-10 | 0 | 1 | 1 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3221 Broadway, Macon MH ID 57899 | 3275 | Telephone call and fax received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Ditch | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  | 1/21/2017 12:00:00 AM |  |  | 1 | Ephemeral ditch with no known outlet | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Debris was removed, and the line is scheduled to be cleaned with grease emulsifier and televised. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-06 | 2015-05-06 | Cobb County MS4 | Cobb |  | 1867 Waldrep Circle | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/6/2015 12:00:00 AM | Chattahoochee | 5/6/2015 12:00:00 AM |  |  | 1 | Nickajack Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the 8 inch clay sewer main | Cleaned area and Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-19 | 2016-02-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4422 Sentinel View, NW | 100 | fax received 2/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 2/20/2016 12:00:00 AM |  |  |  |  | 1 | Long Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-21 | 2017-01-21 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2820 Pierce Drive S, Macon MH ID 64565 | 3450 | Email received on 01/24/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Wet weather |  |  | Paul Moisan | Paul Moisan | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was hydraulic overload due to heavy rains in the MWA service area. | Debris has been removed from the area and affected area disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 506 S. McDonough Street, Decatur | 3000 | Notification received on February 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 2/3/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 18:30 hours, when the heavy rain subsides and the flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-03 | 2016-06-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1544 Piedmont Avenue, NE | 805 | fax received 6/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-24 | 2015-06-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1355 Huntington Place Circle, Lithonia | 3760 | Notification received on July 6, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/24/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary to North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:47 hours when a crew pressure washed the 8" sewer main upstream 600ft, clearing the grease blocakge, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-07-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-18 | 2015-11-18 | Columbus Water Works (South WRF) | Muscogee | Columbus | Cherokee and Poplar | 4030 | Fax received on November 19, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhoile overflowed into Weracoba Creek. The basin is the Weracoba Creek Basin. | Once the rain subsided and flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-16 | 2016-11-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1277 Niles Ave, NW, ATL | 5 | Fax received on 11/17/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Paul Moisan |  | 11/17/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | Placed on a periodic inspection schedule |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-30 | 2016-09-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 448 Milledge Heights, Athens | 886 | Initial email notification 9/30, follow up report sent 10/4 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Pipe failure |  |  | Dagny Pariani | Dagny Pariani | 9/30/2016 12:00:00 AM | Oconee | 9/30/2016 12:00:00 AM |  |  | 1 | Sleepy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cracked bell on sewer line | Repaired the line, rodded and flushed |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481 ext 238
2016-12-12 | 2016-12-12 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawrenceville | 320 Forest Valley Rd, Lawrenceville | 2306 |  | Raw Sewage | Wastewater Regulatory Program | GA0026433 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/13/2016 12:00:00 AM |  |  |  |  | 0 | Pew Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Removed all deposited solids, washed down impervious and collected run-off. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-23 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-15 | 2017-04-15 | Cobb County Water System | Cobb |  | 3421 Washington RCommoms Ave. | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/15/2017 12:00:00 AM | Chattahoochee | 4/15/2017 12:00:00 AM |  |  | 0 | Blue Springs Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 7:10 p.m. and the crew stopped the overflow at 9:22 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-09 | 2017-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 570 Spring St. NW - ATL | 10000 | Email received 2017-06-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 6/12/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a breach in the mainline. | Crew used a by-pass pump to contain the spill. Repairs are still ongoing. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-17 | 2015-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 220 | fax received 12/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/17/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-24 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton | 0 | Verbal notification received 2/23/2016. Email follow received 2/25/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill due to TSS: Permit Limit = 25 mg/L; Reported Value = 188 mg/L; Approximate flow volume = 91.7 MG |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-31 | 2015-12-31 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 296 The Plaza, Athens | 18800 | Initial email received 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Oconee | 12/31/2015 12:00:00 AM | 2016-01-02 |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Overflow during flood event | Cleaned area. Sewer upgrade under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-01-12 | 2015-01-12 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1960 Allison Court, SW | 1450 | fax received 1-13-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/13/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-21 | 2017-09-21 | Rome, City of (Rome WRF) | Floyd |  | West Rome Community in front of 100 Webster Street | 6000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 9/21/2017 12:00:00 AM | Coosa |  |  |  | 0 | Little Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was a result of a blockage due to a manhole in a commercial pipe yard being severely damaged. | Cleanup and pumping operations are ongoing. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-10-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-27 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | City of Social Circle - Little River WPCP - 187 Vine Circle | 3039687 | CTS No. 78641 | Treated Effluent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 12/27/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain (7.25"). Operators had to shut down motors in aeration basin and start diesel pump to handle all fo the flow. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2017-05-15 | 2017-05-15 | Cobb County Water System | Cobb |  | 957 Umland Rd | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-14 | 2017-09-14 | Richmond Hill, City of (Sterling Creek WRF) | Bryan | Richmond Hill | 31.934730, -81.285687 | 3000 | initial call was on 9-14-17 full report received 9-19-17 | Raw Sewage | Coastal District | GA0037648 | Lift Station | Storm Drain |  | Equipment failure |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 9/14/2017 12:00:00 AM | Ogeechee |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | one of the stations we were bypassing had a hose that failed at a lift station | . Within a half hour of discovering, we replaced the hose and recovered about 4000 gallons of water from the culvert (basically until the water was clear) and returned it back to the collection system. We immediately used powered hydrated lime to neutralize the small grass area that was affected | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2017-09-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF RICHMOND HILL | 912-445-0050
2017-08-07 | 2017-08-07 | Cobb County Water System | Cobb |  | 831 Pat Mell Rd | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/7/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Limed around manhole | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 701 North Cherokee Road | 400 | fax received 10/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/9/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage caused by shop towels | Cleared blockage using jet machine. Lime applied to spill site. Sign posted. Proper agencies notified. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2015-09-25 | 2015-09-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | called in by Kris Garcia 9/28/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Unknown |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/28/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This is an outfall spill. Reported TSS = 37 mg/L. Total gallons: 27.2 million |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-05 | 2016-09-05 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 4380 Gunnin Road | 1484 | fax received 9/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/5/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Repaired pie and removed logs that washed down the creek causing the separation. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-14 | 2015-01-14 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1770 Richmond Avenue, SE | 920 | fax received 1/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/15/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-04 | 2017-04-04 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 2400 Sweet Shrub Cir. - Lawrenceville | 7779 | Fax received 2017-04-04 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/4/2017 12:00:00 AM |  | 4/4/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Sweetwater Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products; Grease | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-12 | 2018-01-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5400 Memorial Drive, Stone Mountain GA 30083 | 200 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/12/2018 9:09:00 PM | Ocmulgee | 1/12/2018 12:00:00 AM |  |  | 1 | Snapfinger Creek/ Tributary D | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4" private cleanout overflowed from grease blockage in the 8" public sewer main | Pressure washed sewer main from manhole 18-069-s083 to 18-069-s076 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Artis Benton |  | Dekalb Co Dept. Watershed Management
2018-03-03 | 2018-03-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2500 Block of Marathon Drive - Valdosta | 2625 | Call received 2018-03-04 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream | Stream | Grease |  | Alys Hannum | Alys Hannum | Alys Hannum | 3/4/2018 12:00:00 AM |  | 3/3/2018 12:00:00 AM |  |  | 1 | Knight's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Blockage cleared, discharge point cleaned and disinfected. Signs posted. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-29 | 2016-06-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Conley | 3942 Moore Road, Conley | 2720 | Notification received on July 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/30/2016 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 18:08 hours when a crew pressure washed the sewer main 385ft, clearing the blockage at 200ft, distributed twio buckets of degreaser into the manhole, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-05 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-12 | 2018-02-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 406 Inman St. SW - ATL | 50 | Fax sent 2018-02-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/15/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-31 | 2017-12-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4675 Bryn Mawr Cir NW - ATL | 5 | Fax sent 2018-02-20 after discrepancies noted in the semi-annual report. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-09 | 2015-03-09 | Cartersville, City of (Cartersville WPCP) | Bartow |  | 243 South Tennessee Street | 500 | Will video area to look for pipe defects and/or needed repairs | Raw Sewage | Mountain District - Cartersville | GA0024091 | WWTP | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 3/9/2015 12:00:00 AM | Coosa |  |  |  | 0 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Accumulation of fibrous cloth shop towels and grease | Jetted line to remove obstruction which restored normal flow to system. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-03-10 | 0 | 0 | 0 | 0 | 0 | 0 | Bob Jones | 770-387-5653 | City of Cartersville
2016-03-10 |  |  | DeKalb |  | 1957 Glenwood Avenue | 500 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Reconnect by pass pump hose and washed area |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-20 | 2016-04-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 2852 Hickory Trail | 5422 | fax received 4/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/20/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to No Business Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY | 678-376-7000
2018-01-13 | 2018-01-13 | MACON WATER AUTHORITY - ROCKY CREEK WPCP | Bibb | Macon | 1404 Lake Valley Drive MH 52535 | 7200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/13/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Ditch feeding Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Debris has been removed from the area and the affected area is being disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Tony Rojas |  | MACON WATER AUTHORITY
2018-01-13 | 2018-01-13 | MACON WATER AUTHORITY - ROCKY CREEK WPCP | Bibb | Macon | 1404 Lake Valley Drive MH 52535 | 7200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/13/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Ditch feeding Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Debris has been removed from the area and the affected area is being disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Tony Rojas |  | MACON WATER AUTHORITY
2015-12-28 | 2015-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1056 Lester Avenue, SE | 155 | fax received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-28 | 2016-12-28 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 238 Hampton Station Blvd. Canton | 3300 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Contractor |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 12/28/2017 12:00:00 AM | Coosa |  |  |  | 0 | Smithwick Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor left a sewer plug in the line. This caused debris to build up in the sewer line and wastewater to overflow from a manhole. | CCWSA Construction Crews jetted the line and removed the debris | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4027 Cusseta Road, Columbus | 3151 | Telephone call and fax received on 03/14/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/14/2016 12:00:00 AM | Chattahoochee | 3/14/2016 12:00:00 AM |  |  | 1 | Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 15-inch main was clogged with debris causing a manhole to overflow. | Once the debris was cleared (removed) from the main, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-23 | 2015-03-23 | Cobb County MS4 | Fulton |  | 1049 Triad Court | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/23/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of roots in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The Water System was notified at 1:05 p.m. and our crew stopped the overflow at 2:20 pm | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-25 | 2017-06-25 | Cobb County Water System | Cobb |  | 1250 Powder Springs Road | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/25/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | solids | The cobb crew stopped the spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-29 | 2018-03-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snapfinger woods drive Decatur GA 30035 | 30300 | manhole 16-008-s004 and 16-008-s003 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/30/2018 2:40:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | grease | rodded main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-04 | 2015-10-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | J Warren Lift Station | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 10/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | North Fork of Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Torrential Rains |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-894-3085 | CITY OF CORNELIA WPCP
2015-04-06 | 2015-04-06 |  | Columbia |  | 4581 Colonial Road | 7000 | fax received 4/06/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/6/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Chunk of asphalt in manhole | Removed debris from manhole |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-12-30 | 2015-12-30 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4514 18th Ave., Columbus | 3683 | Fax and email received on 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal, the overflow sstopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-22 | 2016-02-22 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | IRMA F MATTHEWS SCHOOL building on Academy Drive | 110 |  | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Rags |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 2/23/2016 12:00:00 AM | Coosa |  |  |  | 0 | Weaver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage of rags | Jetted and freed blockage, cleaned up debris and limed infected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-19 | 2016-01-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Road, SW | 3220 | fax received 1/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/20/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-04 | 2015-01-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Alpine Lift Station/ Flat Street | 7000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Sam Buckles | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Fork of Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain |  | 455ebb3c-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-490-4613 | CITY OF CORNELIA
2016-02-20 | 2016-02-20 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Cown Drive Lift Station Manhole No. J1 | 13500 | email notification received 2/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 2/20/2016 12:00:00 AM |  |  | 2016-02-20 | 2017-03-14 | 1 | Little Haynes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Electrical failure |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-23 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF LOGANVILLE
2016-12-11 | 2016-12-11 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2617 Cranbrook Dr. - Augusta | 250 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Ditch |  | Grease |  |  | Alys Hannum | Hsin Yeh | 12/12/2016 12:00:00 AM |  |  |  |  | 0 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Line opened and resumed normal flow. Storm ditch was flushed and vacuumed out. Will assess the line with CCTV to determine what actions need to be taken to prevent future issues. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-08 | 2016-08-08 | Tifton, City of (New River WPCP) | Tift | Tifton | 61 TC Gordon Rd., Tifton | 22500 | Email came in on 08/09/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 8/9/2016 12:00:00 AM |  | 8/8/2016 12:00:00 AM | 2016-08-09 | 2017-08-28 | 1 | Little River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was due to heavy rainfall and flooding. | Hydrated lime was spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-08-09 | 0 | 1 | 1 | 1 | 1 | 0
2017-10-18 | 2017-10-18 |  | DeKalb | Atlanta | 1500 Sheffield Drive, Atlanta | 100 | Notification received on October 23, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/18/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage | The problem was corrected at 11:05 hours when the first responder rew rodded the 6" clean out 25-ft, clearing the blockage at 15-ft and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1601 Johns Road | 600 | fax received 2/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 2/3/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Oates Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2018-06-05 | 2018-06-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 980 Nawench Dr. NW - Atlanta | 250 | Fax sent 2018-06-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 6/6/2018 12:00:00 AM |  | 6/5/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, debris, and roots in the mainline | Spill was self-contained. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Smith Drive - Augusta | 123000 | Email received 2017-01-13 | Raw Sewage | Wastewater Regulatory Program | GA0037621 |  | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/13/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County Area. | Line is being monitored until normal flow is resumed. Notifications were posted in the area. Will assess the system via flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-31 | 2018-01-31 | Marietta (City of)- Sewers | Cobb | Marietta | 736 Lawrence St | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/31/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Marietta Water personnel quickly revlieved the blockkage by hydro jetting thus resotring normal service. Restaurants tied into this line will be inspected for gease trap compliance and pumping schedules increased, etc. CCTV also revealed a belly in a section of the main allowing for grease buildup. This main will be put on a higher frequency cleaning schedule as well. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-14 | 0 | 0 | 0 | 0 | 0 | 0 | Tim Marshall |  | MARIETTA WATER & SEWER
2017-09-12 | 2017-09-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRF | 0 | TSS =166 mg/L. Permit limit = 25 mg/L Email notification received 20174-09-13. Letter sent 2017-09-19. Letter received 2017-10-02. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/13/2017 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Severe storm event (Hurricane Irma) | Self-contained. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-11 | 2017-12-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | RM Clayton WRC - ATL | 0 | Also entered under GA0039012 TSS Violation December 11 - 205 mg/L December 12 - 67 mg/L | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 12/13/2017 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to heavy flows from snowmelt |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-29 |  | Meriwether | Manchester | west end of Peach Street | 100000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Dagny Pariani |  | 12/29/2015 12:00:00 AM | Flint | 12/29/2015 12:00:00 AM | 2015-12-29 |  | 1 | tributary to Pigeon Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Structural failure to manhole caused by surcharge event during extremely heavy rainfall |  |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-30 | 0 | 1 | 0 | 1 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1200 Block of Lake Drive | 105365 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2018-04-23 | 2018-04-23 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 1171 Ga Hwy 100 Tallapoosa | 800 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 4/24/2018 12:00:00 AM | Tallapoosa |  |  |  | 1 | Private Lake, Gold Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage | Carroll EMC restored power, suggest installation of back up power | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-24 | 1 | 0 | 0 | 0 | 0 | 0
2015-12-27 | 2015-12-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1058 Viking Drive, Stone Mountain | 7475 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 12/27/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 10" sewer main. | The problem was corrected at 16:40 hours, when a crew replaced 12ft of the pipe and returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 500 Dairy Pak | 689 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/14/2018 12:00:00 AM | Oconee |  |  |  | 1 | North Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain event | Sewer upgrade under design |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-15 | 2016-08-15 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | corner of Bryant Street and Hwy 115 | 250 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Debris |  | Brian Koehler | Kathy Lewis | Brian Koehler | 8/17/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Soque River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown object entered the sewer system and blocked the line | Jetted the sewer line and put lime on the ground around the area | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-08-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-20 | 2017-02-20 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3637 Monmouth Rd - Augusta | 5400 | Manhole #BC130M0543 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 2/21/2017 12:00:00 AM |  |  |  |  | 0 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, debris, and roots. | Line being monitored and assessed to determine the source of the grease. Line will be sawed to remove roots. Will assess the line via CCTV to determine if there is any structural damage. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-16 | 2015-08-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1988 Plaza Lane, SW | 1360 | Fax received on 08/17/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/17/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Hydraulic pressure cleaner was used to contain spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-21 | 2015-09-21 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 4 East Gazebo Lane, Wilmington Island, Savannah GA 31410 | 1200 |  | Raw Sewage | Coastal District |  | WWTP | Storm Drain | Canal | Equipment failure |  | Steve Fox | Steve Fox | Steve Fox | 9/21/2015 12:00:00 AM | Savannah | 9/21/2015 12:00:00 AM |  |  | 1 | Betz Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | y | 0 | Air release valve failure on LS 39 force main failure (1 ¼” hole) | Lift station was shut down and air release valve will be replaced. Will also enlarge manhole and install manhole level alarm in the future. The ditch was contained and by-pass pumps were set up. Lime is being placed on area that came in contact with the discharge. City jet vacs removed water from the ditch and then discharged the contaminated water into the City sewer system. Spill notifications will be placed at spill site, behind 218 Deerwood Drive, and where the detention ponds flows into Betz Creek. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who will send out a news release to the media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-09-22 | 1 | 0 | 0 | 0 | 0 | 0
2017-11-02 | 2017-11-02 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 196 Old Mill Trail | 14220 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Almand Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1791 Harper Street, NW | 620 | fax received 3/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/15/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-02 | 2016-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2545 Forest Hills Dr., SW, Atlanta | 2145 | Fax received on 11/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/3/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Pressure cleaner was used to clear the line. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-15 | 0 | 1 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2015-12-24 | 2015-12-26 | Carrollton, City of | Carroll | Carrollton | WWTP | 54000 | Facility called in complaint to EPD on 12/25/2015. Report received via mail on 01/04/2016. | Treated Effluent | Wastewater Regulatory Program | GAJ020126 | WWTP | Stream |  |  |  |  | Paul Moisan | Paul Moisan | 12/26/2015 12:00:00 AM | Tallapoosa |  |  |  | 1 | Little Tallapoosa River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Heavy rainfall from December 23-26. | When the rainfall ended, flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 0 | 1 | 0 | 1 | 0 | 0
2017-06-19 | 2017-06-19 | Cobb County Water System | Cobb |  | 2372 Moseley Place | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The crew stopped the spill at 3:15 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 215 Beaumont Avenue | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | low restored |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 2227 Baker Carter Drive (Outfall) - Loganville | 9000 |  | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/23/2017 12:00:00 AM |  | 1/21/2017 12:00:00 AM | 2017-01-22 |  | 1 | Unnamed Trib. to Little Haynes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overloading of the collection system. | Site cleared of debris, lime and straw spread, signs placed at location of spill. Local newspaper notified. Sampling started. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-26 | 2018-06-26 | Pearson, City of (Pearson WPCP) | Atkinson | Pearson | WWTP outfall into unnamed tributary to Little Red Bluff Creek to Red Bluff Creek. | 295840 |  | Treated Effluent | Coastal District | GA0038334 | WWTP | Stream | Stream | Equipment failure |  | Brett Berry | Brett Berry | Brett Berry | 7/5/2018 12:00:00 AM | Satilla | 7/5/2018 12:00:00 AM | 2018-07-05 | 2019-07-05 | 1 | Red Bluff Creek | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The violation occurred following electrical damage due to lightning. Damage occurred on May 23, 2018 and again on June 2, 2018. During both instances no power was delivered to blower systems causing septic conditions in the treatment process. | Signage was placed at the discharge point. Local health department and local media were notified. Sampling is being conducted to ensure there are no harmful effects in accordance with the current NPDES permit and EPD protocol. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-07-09 | 1 | 1 | 0 | 0 | 0 | 0
2017-05-17 | 2017-05-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3255 Valley Rd. NW - ATL | 280 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 5/18/2017 12:00:00 AM |  | 5/17/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 305 Kelso Drive, SW | 244 | fax received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | The crew performed a point repair |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-08 | 2015-01-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 7 Collier Lane, NW | 10 | fax recieved 1-10-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Roots |  |  | Kim Hembree | Kim Hembree | 1/10/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-20 | 2017-05-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1205 Lake Hearn Drive, Atlanta. | 1500 | Notification received on May 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 5/20/2017 12:00:00 AM |  |  |  |  | 0 | Perimeter Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | The problem was corrected at 11:00 hours when the crew removed the flow monitor and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-23 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-15 | 2017-06-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Rd. NE - ATL | 1100 | Email received 2017-06-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 6/16/2017 12:00:00 AM |  | 6/15/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | Crew made repairs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-31 | 2017-10-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 9 Linden Court, Columbus. | 502 | Fax received on 11/01/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 10" sewer main was clogged with debris causing the overflow. | Once the debris was cleared, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-10 | 2017-07-10 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 6090 Pine Grove Road, Riverdale | 744000 | Telephone call and email received on 07/11/2017; Fax received on 07/12/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 7/11/2017 12:00:00 AM | Flint | 7/11/2017 12:00:00 AM | 2017-07-11 |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 0 | Pipe broken under waterway. Bypass pumps were installed to stop and divert the sewage around the pipe failure. | Bypass pumps installed to divert sewer around pipe defect. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4353 Clement Dr, SW - ATL | 1443 | Fax received on 01/21/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crew performed a point repair. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-8466 | ATLANTA, CITY OF
2016-12-22 | 2016-12-22 | Cobb County Water System | Cobb |  | 3728 Mars Hill Road | 490 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/22/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The Water System was notified at 1:29 p.m and our crew stopped the overflow at 2:50 p/m. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-03 | 2017-10-03 | East Point (City of)- Sewers | Fulton | East Point | 4200 N. Commerce | 8540 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Cleaned, jetted and Vacuumed line and spread lime on the affected area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 308 2nd Avenue | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 4200 |  | Raw Sewage | Wastewater Regulatory Program | GA0025771 | WWTP | Stream |  | Hydraulic Overload |  |  | Dagny Pariani | Sarita Banjade | 2/26/2015 12:00:00 AM | Ochlockonee |  |  |  | 1 | Parker's Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall and failure of an influent pump at the WWTP | No immediate action taken. Ground to be cleaned and limed as needed. |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025 x162
2016-02-11 | 2016-02-11 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Intersection of Charlton Street and Martin Luther King Jr. Drive | 675 | Dryland overflow | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System |  |  | Roots |  |  | Dagny Pariani | Dagny Pariani | 2/12/2016 12:00:00 AM | Oconee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer line. | Rodded and jetted the sewer line. Removed the tree that caused the blockage. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2016-02-16 | 2016-02-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Woodbine Circle, SE | 10 | fax received 2/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/17/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-08 | 2015-11-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 828 Peebles Street, SW | 340 | fax received 11/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-17 | 2018-05-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 318 Kelso Dr. SW - Atlanta | 10 | Fax sent 2018-05-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/18/2018 12:00:00 AM |  | 5/17/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-31 | 2016-08-31 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 417 Halifax Drive | 1500 | fax received 8-31-2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 8/31/2016 12:00:00 AM |  |  |  |  | 1 | Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipeline crossing creek was leaking due to misalignment. | Plugged manhole, cut and replaced section of pipe removing badly misaligned joint. Planning permanent creek crossing replacement. Posted signs. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-01-29 | 2015-01-29 | Sylvania, City of (Sylvania WPCP) | Screven | Sylvania | Blaylock L.S. | 400 | Cont.- Crews are cleaning the area and will apply lime to areas we can access. I will notify the local health inspector of the spill and place signs at the lift station area. The local heath inspector was also notified." | Raw Sewage | Coastal District |  | WWTP |  |  | Hydraulic Overload |  | Steve Fox | Steve Fox | Steve Fox | 1/29/2015 12:00:00 AM | Ogeechee | 1/29/2015 12:00:00 AM |  |  | 1 | Bucks Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Hydraulic Oveload- blockage in the drainage area that let loose and the resulting water over taxed the pumps | This is an excerpt from the City's Spill response report. "Crews were immediately dispatched along with myself. When we arrived at 1513 hours we found the lift station starting to overflow. We found both lift station pumps running and pressures indicated they were pumping as designed. I immediately dispatched a crew to the manhole where the force main dumps. The flow there indicated the same as the pump data. The flow indicated no blockage in the force main. The crew then immediately began to open manholes in the Sylvan Heights area to assess the severity of the back up. The only one backed up was the manhole located at West Ogeechee Street above the lift station. Another crew was dispatched to the Bi Lo Lift Station and it was found to be operating as designed and no back up. This station was placed in the off position until the problem could be determined. This station was placed back in service at 1535 hours.At 1530 hours the crewmember at Blalock reported the flow was stopped. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-02-03 | 1 | 1 | 0 | 0 | 0 | 0
2015-02-07 | 2015-02-07 |  | Fulton | Fairburn | Near 2047 Broadmoor Way, Fairburn, GA | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Bear Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station failure | Repair Lift Station | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-12 | 2017-10-12 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | James Avenue Lift Station in Eastman, GA. | 25000 | Spill monitoring initiated 9/12/2017. | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 9/11/2017 12:00:00 AM | Ocmulgee | 9/11/2017 12:00:00 AM | 2017-09-12 | 2018-08-28 | 1 | Gum Swamp Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rainfall and power outages from Hurricane Irma. | 9/20/2017 - Received report of spills in writing and copy of PN distributed in legal organ (The Dodge County News) on 9/20/2017. 10/11/2017 - Written report received including start and stop times, and documentation showing TV, Radio, and health department were notified of incidents. Pictures of PN at spill location also provided. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-10-03 | 1 | 1 | 1 | 1 | 1 | 0
2016-03-01 |  |  | DeKalb |  | 5726 Southland Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-29 | 2018-08-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3330 Northlake Parkway, Atlanta GA 30345 | 1200 | manhole 18-210-p129 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Equipment failure |  |  | Dillon Rodenbaugh |  | 8/30/2018 11:20:00 AM | Ocmulgee |  |  |  | 1 | North Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Found private manhole#18-210-p129 | Sunbelt was on site making repairs to sewer pump which restored flow back to the sewer main |  |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-16 | 2015-06-16 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1312 Hunt Avenue | 1218 | REC Call 6/16/2015. REC EMAIL 6/17/15 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 6/17/2015 12:00:00 AM | Chattahoochee | 6/16/2015 12:00:00 AM |  |  | 1 | Mill Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A leaking bell discharging into Mill Branch Creek | The leaking bell was repaired and the discharge was stopped . The basin is Mill Branch Creek. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-17 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2018-05-24 | 2018-05-24 | Patterson, City of (Patterson WPCP) | Pierce | Patterson |  | 8500 | Stated that there are no downstream suppliers within twenty (20) miles of the spill site. | Raw Sewage | Coastal District | GA0037206 | Collection System | Ditch | Stream | Wet weather |  | Bill Hawthorne | Brett Berry | Brett Berry | 5/25/2018 8:22:00 AM | Satilla |  |  |  | 1 | Patterson Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to sewer lines being hydraulically overloaded by five inches of rainfall in less than one hour. |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-06-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-16 | 2015-11-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1751 Lakewood Way, SW | 3600 | fax received 11/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/17/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-09 | 2017-05-09 | Columbus Water Works (South WRF) | Muscogee | Columbus | 17 Woodlawn Circle, Columbus | 7500 | Telephone call received on 05/09/2017; email received on 05/10/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 5/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A force main developed a lead and caused an overflow. | Once the lead was discovered, the pump at the lift station was turned off causing the leak to stop. Once repairs were made, the pump was returned to service. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-26 | 2016-07-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3526 Midvale Cove, Tucker | 280 | Notification received on July 28, 2016 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/26/2016 12:00:00 AM |  |  |  |  | 0 | Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 10:10 hours when the crew pressure washed the 8" sewer main 83 feet, cleared blockage of grease at 57 ft to restore service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-28 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Rome, City of (Rome WRF) | Floyd |  | 27 Horseleg Creek Road in the Horseleg Creek community | 11000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Storm Drain, Stream |  | Other |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 4/4/2016 12:00:00 AM | Coosa |  |  |  | 0 | Coosa River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Riverbank collapse | The sewer main was repaired | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Lake City | 1518 Huie Road, Lake City | 9000 | Fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/25/2015 12:00:00 AM | Flint | 12/25/2015 12:00:00 AM |  |  | 1 | East Jester's Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Due to the excessive rainfall, it appears that infiltration/inflow and capacity are the cause. | Multiple lines will be inspected for the source of inflow and infiltration to resolve capacity issue. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 1 | 1 | 0 | 0 | 0
2015-12-29 | 2015-12-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 78500 | CTS No. 78670 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  | 2015-12-30 | 2017-01-20 | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-30 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-06 | 2018-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Richmond St. SE - ATL | 252 | Fax sent 2018-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/7/2018 12:00:00 AM |  | 2/6/2018 12:00:00 AM |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Tifton, City of (New River WPCP) | Tift | Tifton | Manhole located at 61 TC Gordon Road, Tifton | 2500 | Telephone call on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | Cow House Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excess rainfall which created surcharges in the system. | Mitigated by hydrated lime | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3260 Mercer University Drive, Chamblee | 4980 | Notification received on March 29, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/27/2017 12:00:00 AM |  |  |  |  | 0 | Warren Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags blockage | The problem was corrected at 11:46 hours when a crew rodded between manholes, cleared the blockage at 72ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-29 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-10 | 2017-12-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | RM Clayton WRC - ATL | 0 | This incident is also entered as a violation under GA0039012. TSS Violation December 10 - 150 mg/L December 11 - 205 mg/L | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 12/11/2017 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to heavy flows from snowmelt. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-19 | 2015-06-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1430 Skyhaven Road, Atlanta | 3520 | Notification received on June 24, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 6/20/2015 12:00:00 AM |  |  |  |  | 0 | Entrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage of rock and sand. | The problem was corrected at 19:35 hours when a crew pressure washed the 8" sewer main upstream 125ft, cleared the blockage, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-06-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5900 North Cheryl Drive, Morrow MH # 23032290 | 171000 | Fax received on 01/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/23/2016 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Capacity. | Multiple lines are being inspected for source of inflow and infiltration to resolve capacity issue. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 1 | 1 | 1 | 0 | 0 | 0
2017-08-01 | 2017-08-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3131 Manchester Expressway, Columbus | 2923 | Telephone call received on August 1, fax received on August 2. They did not know exact volume during first notice. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 8/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 18" sewer main developed a break causing an overflow. | Once the break was discovered a pump around was installed stopping the overflow. Repairs are underway. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-30 | 2018-05-31 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Southeast WPCP outfall (BOD Spill) | 6200000 | Insufficient DO in the aeration basins caused a BOD spill at the WPCP's outfall. | Other | Coastal District | GA0024431 | WWTP | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 6/6/2018 11:20:00 AM | Satilla | 6/6/2018 12:00:00 AM | 2018-06-06 |  | 1 | Unnamed tributary of the Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Operator states that heavy rainfall flooded the aeration basins and the gearbox pits which shut down the mechanical aerators. | Operator states they are seeking out inflow problems on the north side of town. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-06-08 | 1 | 1 | 1 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1550 Peachtree St. NW - ATL | 1420 | Fax sent 2018-01-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 1/17/2018 12:00:00 AM |  | 1/16/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Boston Avenue Lift Station in McRae-Helena | 5000 |  | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ground, Stream |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM | Ocmulgee |  |  |  | 1 | Little Ocmulgee River | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma storms | Had power restored. Cleaned up spill; lime was applied liberally to the area. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-04 | 1 | 0 | 0 | 0 | 0 | 0
2016-04-27 | 2016-04-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 1618 Eric Circle | 6692 | fax received 4/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/28/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Lee Daniel Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | rags and flushables | raked area and spread lime; placed signs at spill and affected waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-06-25 | 2018-06-25 | Albany, City of (Joshua Street WPCP) | Dougherty | City of Albany | Old river bypass gate at LS 26. | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0037222 |  |  | Stream |  |  |  | Juan Robles |  | 6/25/2018 12:00:00 AM |  |  |  |  | 0 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Higher levels of flow. | The City intend to install a masonry plug in the 24" bypass pipe and permanently seal that off in the near future. |  |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-12 | 2015-11-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 255 S Columbia Drive, Decatur | 860 | Notification received on November 16, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/12/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The problem was corrected at 10:46 hours when a crew rodded the manhole downstream, clare the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-22 | Cobb County Water System | Cobb |  | 5550 South Cobb Dr. | 2160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solid Buildbup in 12" main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-18 | 2015-05-18 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 251 Harlan Road, SW | 2400 | fax received 5/18/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/18/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-14 | 2017-03-14 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2535 Shalimar Dr - Augusta | 1125 | Email received 2017-03-14 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 3/14/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, rags and debris. | Sewer gravity main was cleaned and the downstream storm pipe was flushed and vacuumed out. The sewer main will be videoed to assess pipe structure. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-12 | 2016-01-12 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Highway 92 and Hospital Drive N., Douglasville MH # 9741 | 2300 | Telephone call and email received on 01/14/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream |  | 3rd party contractor |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/14/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Unknown Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 10:30 AM Plug on MH 9741 started to leak due to failure on plug in MH 9741. Sewer flowing towards New MH Construction site at Sta. 81 25 /- Lt. 10:35 AM WSA Construction Inspector informed Contractor of the raw sewer water leak and advised that a pump truck was needed to remove the sewer water from excavation (there was also groundwater accumulation in the excavation site) 10:35 AM Contractor decides to pump water from excavation site and discharge it close to the nearby creek located approximately 100 Ft away from construction site. 10:35AM-11:00 AM Contractor is informed that the discharge is illegal. For 25 minutes pumping continues. | 11:40 AM WSA brings in a sewer pump truck to remove raw sewer spilled water. 12:05 PM WSA Pump truck finished removing approximately 1200 gallons of sewer water. 4:00 PM Sewer line cut in construction site is tied back in temporarily. Estimated volume of raw water spilled is 92 gall/min x 25 min = 2,300 gallons | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-16 | 2017-04-16 | Cobb County Water System | Cobb |  | 3321 Valley Vista Road | 720 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Adams Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-09 | 2016-11-10 | Marietta (City of)- Sewers | Cobb | Marietta | 305 Cherokee St. | 2500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Detail in report | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-13 | 2017-04-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1402 Foxhall Lane, Atlanta | 2196 | Notification received on April 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/14/2017 12:00:00 AM |  |  |  |  | 0 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease / Rags blockage | The problem was corrected at April 14, 2017 at 02:00 hours when a crew pressure washed the 8" sewer main 308ft, clearing the blockage at 297ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-06 | 2015-09-12 | Rochelle, City of (Northwest WPCP) | Wilcox | Rochelle | Rochelle Northwest WPCP | 20000 | Weekly BOD and TSS concentration and loading violations during 09/06/2015 through 09/12/2015 period. Through plant major spill as defined. | Treated Effluent | Southwest District | GA0024244 | WWTP | Stream | Stream | Debris |  |  | Linda Stevens | Jay Howell | 10/20/2015 12:00:00 AM | Suwannee |  | 2015-10-21 | 2016-11-11 | 1 | Mill Creek Tributary | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | There were blockages in the effluent line at the plant during the sampling period of 09/06/2015 through 09/12/2015. | We have cleared the blockages. All public notifications have been performed - on file in SW District Office. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-05-24 | 0 | 1 | 1 | 1 | 1 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Carnegie Wy. NW - ATL | 300 | Fax received 2017-08-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 8/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain-induced | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1948 East Starmount Way, Decatur | 12400 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Dooolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 20:30 hours when the heavy subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 0 | Initial phone call 9/2/16 | Treated Effluent | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Natural Disaster |  |  | Dagny Pariani | Dagny Pariani | 9/2/2016 12:00:00 AM | Ochlockonee | 9/2/2016 12:00:00 AM | 2016-09-02 |  | 1 | Parker's Mill Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Tropical Storm Hermine. Flows hydraulically overloaded the Plant. Flow volume = 28,050 gallons. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-02 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025 x162
2015-02-04 | 2015-02-04 |  | DeKalb | Atlanta | 3540 Inman Drive, Atlanta | 3540 | Notification received on February 5, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 2/4/2015 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | The problem was corrected at 12:45 hours when a crew rodded & pressure washed the 10" sewer main 265ft upstream, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 2017-06-28 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Andrews St and Wilkinson St., Milledgeville | 200 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | WWTP | Stream |  | Natural Disaster |  |  | Hsin Yeh | Hsin Yeh | 6/29/2017 12:00:00 AM |  |  |  |  | 0 | Fishing Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Erosion | Corrective action were taken immediately and included containing the spill, repairing, the line, raking the soil, putting out lime, and removing the debris. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-11 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-05 | 2017-09-05 | Cobb County Water System | Cobb |  | 4050 Jordon Lake Drive | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/7/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The crew stoppedthe overflow at 10:00 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5900 North Cheryl Drive | 126000 | Fax received on 02/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 2/25/2016 12:00:00 AM |  |  | 2016-02-25 | 2017-03-02 | 1 | Angel Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 |  |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-04 | 0 | 1 | 1 | 1 | 1 | 0
2017-01-17 | 2017-01-17 | Cobb County Water System | Cobb |  | 3171 Burnt Hickory Rd | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mudd Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-01 | 2018-07-01 | Rome, City of (Rome WRF) | Floyd |  | In front of 1112 Old Dalton Road | 500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Unknown |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/2/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed tributary leading to the Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown at time of report | Sewer main has been thoroughly cleaned and will be inspected by CCTV to determine and correct the problem | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-10 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-07 | 2017-01-07 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2517 Argonne Drive - Augusta | 15000 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/8/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Additional volume of rainfall caused flows to exceed the pumping capacity of the facility, and highly diluted wastewater to overflow out of a customer's residential makeshift cleanout. | A backwater valve was installed on the customer's property to stop the overflow and prevent future overflows of this nature. Standing water removed from the area. Plan to remove the affected soil, spread lime and topsoil as needed. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-05 | 2018-08-05 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 2990 Creek Tree Lance - Cumming | 750 | Fax sent 2018-08-06 ~100 gallons entered stream | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 8/6/2018 12:00:00 AM |  | 8/5/2018 12:00:00 AM |  |  | 1 | Bagley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags | Jetted to remove grease & rags, cleaned up, spread lime, posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-25 | 2015-03-25 |  | Gwinnett | Sugar Hill | 4346 Frontier Way | 9450 | fax received 3/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/25/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe was broken in the creek. | Repaired the pipe and restored the flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-03-25 | 2015-03-25 |  | Gwinnett |  | 4346 Frontier Way | 9450 | fax received 3/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/25/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe was broken in the creek. | Repaired the pipe and restored the flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-08-07 | 2018-08-08 | Arlington, City of (Arlington WPCP) | Early | Arlington | 116 Azalea Street in Arlington, GA. | 0 |  | Raw Sewage | Southwest District | GA0026204 | Collection System | Ground, Storm Drain, Stream |  | Pipe failure |  | Linda Stevens | Jay Howell | Linda Stevens | 8/7/2018 2:00:00 PM | Flint |  |  |  | 1 | Perry Creek | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Spill of raw sewage (unknown volume provided yet, but estimated greater than 10,000 gallons) from collapsed pipe in distribution system. Received via CTS#87135. | Line repaired and placed back into service on 8/8/2018. | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2018-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-17 | 2016-10-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2396 Miriam Lane, Decatur | 2540 | Notification received on October 18, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/17/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease/Roots | The problem was corrected at 13:26 hours, when a crew pressure washed the sewer main 200ft, removed the blockage at 130ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-18 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Barnes Rd. & Croft Rd. - Augusta | 151200 | Fax received 2017-01-03, update received 2017-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding caused highly diluted wastewater to begin running out of several manholes by 11:00 AM on January 2, 2017. | Line is being monitored until normal flow resumes. Notifications posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 |  | DeKalb | Atlanta | 1694 Chantilly Drive, Atlanta | 2600 | Notification received on February 18, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/18/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:45 hours when a crew pressure washed upstream 417ft, removed grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-13 | 2015-04-13 | McRae-Helena, City of (McRae-Helena WPCP) | Dodge | Helena | Homer Avenue Lift Station that serves Telfair State Prison in Helena, GA. | 3500 | All PN notification requirements met on 4/13/2015. Copies of PN provided to SW District Office and are attached. | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ditch | Ditch | Power failure |  | Jay Howell | Jay Howell | Jay Howell | 4/13/2015 11:30:00 AM | Ocmulgee | 4/13/2015 12:00:00 AM |  |  | 1 | Unnamed tributary to Little Ocmulgee River Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | bar screen inundated with trash and muffin monster not working. Occurred something on late 4/12/2015 to early 4/23/2015. Heavy rainfall also present during time of spill. | muffin monster being repaired - trash removed from bar screen. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-04-28 | 1 | 1 | 1 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1301 Riverside Drive, Macon MH ID 66885 | 281220 | Phone call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee | 4/1/2016 12:00:00 AM | 2016-04-05 |  | 1 | Vineville Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this major spill was hydraulic overload due to heavy rains in the MWA service area. According to the National Weather Service, Macon-Bibb County received 5.42 inches of rain on Friday, April 1st. | Debris has been removed from the area and the affected area has been disinfected with lime. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 1 | 0 | 0
2017-05-25 | 2017-05-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1968 Peachtree Rd. NW - ATL | 1710 | Email received 2017-05-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/26/2017 12:00:00 AM |  | 5/25/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-04 | 2018-08-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 180 Howell Dr. SW - Atlanta | 176 | Fax sent 2018-08-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6909 Dixie Street | 432453 | Fax sent 5/26/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  |  |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Bull Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain | Rainfall has stopped, manhole has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-04 | 2016-11-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 380 Ardmore Cir, NW, Atlanta | 540 | Fax received on 11/05/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/5/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-11-01 | 2017-11-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2914 Concord Drive, Decatur | 3320 | Notification received on November 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/1/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage. | The problem was corrected at 13:30 hours when the first responder crew rodded the 8-inch sewer main, clearing the grease blockage from the invert, and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-11-03 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1440 Sowell Estate, Stone Mountain | 52600 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 08:45 hours on April 6, 2017, when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-02 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 819 Barrett Lane - Augusta | 300 | Fax received 2017-01-03 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Ditch | Grease |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/2/2017 12:00:00 AM |  |  | 0 | Tributary to Raes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Line opened and resumed normal flow. Lime spread in the affected areas and notices posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Warrenton, City of (South Pond WPCP) | Warren |  |  | 0 |  | Primary Effuent | Northeast District - Augusta | GA0032786 | WWTP | Other | N/A | Other |  | Madara Tyler | Madara Tyler | Madara Tyler | 11/3/2016 12:00:00 AM | Ocmulgee | 11/3/2016 12:00:00 AM | 2016-11-03 |  | 0 | Goldens Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | BOD-5 loading exceeded the permitted weekly average by greater than 50% |  | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 2016-11-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-30 | 2015-11-30 | Hinesville, City of (Peacock Creek WPCP) | Liberty | Hinesville | Next to Hinesville Master Pump Station (HPS) in the force main that runs parallel to Peacock Canal. | 325000 | This force main is 7-8 miles long and has 13 maintenance access point with ARV. The entire system is constantly under pressure and to replace any of the ARVs would require 9 hours of down time ( a spill) A study has been done and it was determined that a parallel line be built next to this old crumbling rebar reinforced concrete force main. the project is being funded and construction is to start in March 2016 and will take approx 6 months. | Raw Sewage | Coastal District | GA0038792 | Force Main | Canal | Canal | Rags |  | John Kalp | John Kalp | John Kalp | 11/4/2015 2:09:00 PM | Ogeechee | 11/30/2015 12:00:00 AM | 2015-11-30 | 2016-11-22 | 1 | Peacock Creek | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | yes | 0 | Rags and mop type material got caught in the air relief valve (ARV) inside the maintenance access hole (a confined space that builds up H2S) adjacent to the Hinesville Master Pump Station (HPS) along the 24" force main. This main is under constant pressure and the valve was in a confined space causing several problems. To eliminate the H2S the top of the access lid had to be removed to allow adequate ventilation before entrance was safe. See Documents Section | Since the ARV was thirty (30) years old and plans had already been made to replace it the valve was replaced with a new ARV. | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2015-12-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-05 | 2016-02-05 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2761 Walnut Creek Road, Macon MH ID 58339 | 2100 | Fax recieved on 02/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 2/8/2016 12:00:00 AM | Ocmulgee | 2/5/2016 12:00:00 AM |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this spill was grease and roots. | Debris was removed from the area, and the area was disinfected with lime. This line is scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly hot spot inspection list and will be chemically treated for root control. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-19 | 2018-05-19 | Adairsville, City of (North WPCP) | Bartow |  | Manhole on the outfall line at 106 Cass Street, Adairsville | 3840 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Wet weather |  | Eric Dykes | Kathy Lewis | Katie Meade | 5/22/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed Tributary to Oothkalooga Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line backed up and spilled from manhole after heavy rain event. We suspect major inflow and infiltration contributed to a capacity overload in the collection system. | City of Adairsville construction personnel found the overflowing manhole at 4 am on 5.19.18. When it stopped raining, the water receded and stopped overflowing from the clean out. City sewer crews will investigate the lines through camera inspection throughout the week. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-23 | 1 | 0 | 0 | 0 | 0 | 0
2015-01-27 | 2015-01-27 | Cobb County MS4 | Cobb |  | 3280 Ground Pine Dr. | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | ADMINTEST ADMINTEST | Reginald Williamson |  | 1/28/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing Failed/ 8" Ductile Iron Main. | Cleaned and spread lime at spill area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-02 | 2018-01-02 | Marietta (City of)- Sewers | Cobb | Marietta | 1019 Franklin Gateway | 3350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/2/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Marietta personnel quickly relieved the blockage by hydro jetting thus restoring normal service. The sewer main will be examined by CCTV to check for defects, etc. There is new controctuion in this area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-09 | 2016-12-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 451 Sawtell Ave, SE, ATL | 610 | Fax received on 12/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/10/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-1328 | ATLANTA, CITY OF
2017-01-16 | 2017-01-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 785 Gary Rd NW - ATL | 700 | Fax received 01/17/2017 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/17/2017 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2015-12-30 | 2015-12-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 130 Duncan Springs Rd., Athens | 2370 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Oconee | 12/30/2015 12:00:00 AM |  |  | 1 | un-named tributary to Middle Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowed during flood event | Cleaned area. Sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-26 | 2017-02-26 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 1976 Crescent Drive - Snellville | 851 | Fax received 2017-02-27 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Force Main | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 2/27/2017 12:00:00 AM |  | 2/26/2017 12:00:00 AM |  |  | 1 | Watson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Removed all deposited solids, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-12 | 2016-12-12 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Central Ave @ Glenn Avenue - Augusta | 975 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Ditch |  | Grease |  |  | Alys Hannum | Hsin Yeh | 12/13/2016 12:00:00 AM |  |  |  |  | 0 | Tributary to Oates Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Line was opened and resumed normal flow. Storm ditch was flushed and vacuumed out. Will assess the line with CCTV to determine what actions need to be taken to prevent future issues. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-12 | 2017-02-13 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 701 North Cherokee Road - Social Circle | 100 | Email received 2017-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Ditch | Rags |  |  | Alys Hannum | Alys Hannum | 2/13/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage caused by rags. | Jet machine used to clear blockage. Lime applied to spill site. Proper agencies notified. Sign posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-23 | 2017-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2462 Colorado Trl. SW - ATL | 50 | Fax sent 2017-11-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/27/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to control the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-28 | 2016-11-02 |  | Clarke | Athens | 240 Meredith Ridge Rd. | 2215 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/1/2016 12:00:00 AM | Oconee |  |  |  | 0 | North Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | disposable wipes clogged sewer | rodded sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-16 | 2015-09-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 2580 | fax received 8/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/17/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-11 | 2016-10-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3643 Camp Circle, Decatur | 6480 | Notification received on October 13, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 10/11/2016 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 12:36 hours, when a crew pressure washed the sewer main 80ft, removed the blockage at 50ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-28 | 2017-07-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 5313 Waverly Trace | 2984 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/28/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-10 | 2018-07-10 | Cornelia, City of (Cornelia WPCP) | Habersham |  | 514 Nicolon Drive | 8000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream | Stream | Pipe failure |  | Brian Koehler | Kathy Lewis | Brian Koehler | 7/10/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | South Fork of Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage spill occurred due to an aging manhole partly collapsing. | The manhole was completely cleaned out and back on line by 1:15 On Tuesday July 10, 2018. The affected area leading to the tributary was cleaned and treated with hydrated calcium carbonate. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-12 | 1 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2016-01-23 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 1383 Cambridge Drive | 19800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/23/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Big Inidan Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Inflow and infiltration |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2562 Tilly Mill Road, Atlanta | 100 | Notification received on September 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/13/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The first responder crew inspected the upstream and downstream manholes and found 10-inch sewer main to be clear and flowing normal at 12:50 hours. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-15 | 2016-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3136 Martin L King Jr. Drive, SW | 1128 | fax received 2/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/16/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-14 | 2017-09-14 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 228 Morrow Rd, Forest Park Manhole No. 2199035 | 600 | Fax received on 09/15/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 9/15/2017 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-18 | 0 | 1 | 1 | 0 | 0 | 0
2018-06-11 | 2018-06-11 | Stonegate Subdivision WPCP | Bryan |  |  | 47872 |  | Undisinfected Primary Effluent | Coastal District | GAJ030952 | N/A | Ground | N/A | Equipment failure |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 6/11/2018 12:00:00 AM |  | 6/12/2018 12:00:00 AM | 2018-06-11 | 2018-11-01 | 0 | Marsh area | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 |  | 0 | The design of the facility has separated tanks with sealer in between the joints. One of the joints from the first aeration tank blew open an 8” x 1” separation of the tank the prior day emptying the contents of 2 EQ tanks and 2 aeration tanks. Upon inspection of the facility on Monday the 11th of May, the operator noticed the blower was faulted out and looked to see what had happened and noticed the leak coming out of the tank. The operator notified his direct supervisor and he arrived on site at 1:30pm to help correct the rupture | The operator on site at the time of the incident sealed off the crack with quick dry epoxy sealant and once dried sealed it once again with quick dry cement when the leak had subsided. The operators on site then used lime to disperse over the spill area. Water Utility Management is locating a contractor to give a quote on resealing all tanks that way future incidents will not occur. Sampling protocol has been initiated and will continue for the duration specified by the EPD. | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-06-19 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-02 | 2016-05-03 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 0 | Stream monitoring ceased on 6/08/2016 - the facility experienced another effluent major spill. Stream monitoring will be initiated and conducted for the May 25th spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 5/10/2016 12:00:00 AM | Savannah | 5/16/2016 12:00:00 AM | 2016-05-10 | 2016-06-08 | 1 | Tributary to Chandler's Branch | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. | Stream monitoring initiated 6/3/16. Public notification posted at City Hall on 6/3/16. Notification to the Burke Co. Health Department completed on 5/13/16; and notification published in the May 18, 2016 edition of The True Citizen newspaper. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0 | Jonathan Tindall | 912-449-0999 | Tindall Enterprises, Inc.
2016-11-22 | 2016-11-22 | Cobb County Water System | Cobb | Marietta | 4920 Hampton Lake Dr. / Little Willeo Road | 150 |  | R-2 Water | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/22/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids and Debris | Clean and Lime Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-18 | 2018-06-18 | Fayetteville, City of (Fayetteville WPCP) | Fayette | Fayetteville | 260 N Glynn Street | 5400 | Fax sent on 06/19/2018 | Raw Sewage | Wastewater Regulatory Program | GA0035807 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/19/2018 12:00:00 AM |  |  |  |  | 0 | Pye Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Sewer line cleaned with a jet truck and the City will follow up with camera inspection to verify that cleaning was successful, if further cleaning is necessary, City will follow up with additional cleaning. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-06-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-29 | 2016-06-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 84 Peachtree Street, NE | 800 | fax received 6/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/30/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-03 | 2015-08-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5099 Rockbridge Road, Stone Mountain | 900 | Notification received on August 5, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/3/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary to Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:55 hours when a crew pressure washed the 8" sewer main upstream 103 ft, clearing the grease blockage at 60 ft and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-15 | 2018-03-15 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 484 Ronthor Drive - Social Circle | 300 | Email sent 2018-03-16 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Swale | Grease |  |  | Alys Hannum | Alys Hannum | 3/16/2018 12:00:00 AM |  | 3/15/2018 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Jet machine to clear blockage. Signs posted, lime applied to spill site. All public agencies notified including county health dept. local newspaper, local radio station. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-12 | 2017-04-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 600 New Town Cir. SE - ATL | 1800 | Fax received 2017-04-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/13/2017 12:00:00 AM |  | 4/12/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-20 | 2015-10-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 Handley Avenue, SW | 259 | fax received 10/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Other |  |  | Kim Hembree | Kim Hembree | 10/21/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Leaking mainline | The crew performed a point repair |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-06 | 2016-09-06 | Cobb County (RL Sutton WRF) | Cobb | Marietta | 771 Appleton Dr. | 260 |  | Raw Sewage | Wastewater Regulatory Program | GA0026140 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked Debris and Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-15 | 2016-09-15 | Canton, City of (Canton WPCP) | Cherokee |  | Manhole at the Anderson Apartments | 10000 | Being handled by EECO | Raw Sewage | Mountain District - Cartersville | GA0025674 | WWTP | Stream | Stream | Equipment failure |  | Ebony Johnson | Kathy Lewis | Eric Dykes | 9/16/2016 12:00:00 AM | Coosa | 9/16/2016 12:00:00 AM | 2016-09-16 |  | 1 | Etowah River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failed level controller at the Culwell LS |  | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-26 |  | Lowndes | Valdosta | 626 Scott Drive | 5250 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/25/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-11-09 | 2015-11-09 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn |  | Lift Station #4005 - location: 3700 block of Branham Avenue and 3836 Johnston Street | 40000 |  | Raw Sewage | Coastal District | GA0025313 | Lift Station | Ditch | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 11/9/2015 4:12:00 PM | Satilla | 11/9/2015 12:00:00 AM | 2015-11-09 |  | 1 | Branham Ditch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Power disruption and equipment failure caused the lift station to fail to keep up with income flows. | Lift station pump repaired and placed back into service. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-12-07 | 1 | 1 | 0 | 0 | 0 | 0
2016-10-03 | 2016-10-03 | Cobb County Water System | Cobb |  | 2315 Dallas Highway | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Creek | Stopped Spill | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Pipe failure near Crescent Circle. | 11700 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Canal | Canal | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/24/2016 3:00:00 PM | Satilla | 2/25/2016 12:00:00 AM | 2016-02-25 |  | 1 | 17 Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | A 8" ductile iron sewer pipe that crosses over a drainage creek became entangled with limbs and debris creating a dam. The hydraulic force broke the pipe. | The pipe was repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-03-09 | 1 | 1 | 0 | 0 | 0 | 0
2017-10-23 | 2017-10-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 5000 | Notification received on October 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 10/23/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 12:00 hours when the first responder crew waited on the storm event to subside and the flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-11-28 | 2017-11-28 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1501 Milstead rd. | 3300 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System |  | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/28/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-06 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 4000 Marseille Terrace | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded Sewer Main to Restore Flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-07 | 2018-08-07 | East Point (City of)- Sewers | Fulton | East Point | 3400 Creek Pointe Drive | 276000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/14/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | damaged pipe with DIP |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-01 | 2016-12-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Wood St., NW, ATL | 750 | Fax received on 12/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 12/2/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | The crew repaired the by-pass pump. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-16 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-1328 | ATLANTA, CITY OF
2015-09-18 | 2015-09-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1903 Sunbury Place, NW | 1183 | fax received 9/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/20/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-18 | 2017-05-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1467 Woodbine Ave. SE - ATL | 500 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/18/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was equipment failure. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-27 | 2015-01-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1033 Hollywood Road, NW | 1600 | fax received 1/28/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/28/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-29 | 2017-08-29 | Cobb County Water System | Cobb |  | 5860 Dunn Road | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/29/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Pine Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Cobb crews stopped the spill at 10:25 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 307 2nd Avenue, Decatur | 22000 | Notification received on November 4, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/2/2015 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 19:30 hours when the rain receded; a crew rechecked the 8" sewer main after the storm and notice the line is cleared and flowing regular. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-02 | 2017-09-02 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Spearman's Pond Lift Station - Social Circle | 100 | Fax sent 2017-09-03; received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Lift Station | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 9/3/2017 12:00:00 AM |  | 9/2/2017 12:00:00 AM |  |  | 1 | Tributary of Stroud's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Floats in lift station were wrapped up and now allowing operation. | Untangled floats, posted signs, and contacted downstream users. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 |  |  | DeKalb |  | 1440 Sowell Estate | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event, flow restored on own |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1953 South Hairston Road, Stone Mountain | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event cause overflow | Waited until storm passed and flow returned to normal |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-29 | 2015-02-02 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6100 Bayonne Drive | 4826 | REC Initial CALL1/29/15. REC EMAIL 2/1/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/29/2015 1:00:00 PM | Chattahoochee | 1/29/2015 12:00:00 AM |  |  | 1 | Flatrock Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 12 inch pipe broke due to bank erosion causing a spill into the creek. The basin is Flatrock Creek Basin | A pump around was performed and the overflow stopped. Repairs are being made to the pipe and the area is being reinforced. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2016-07-28 | 2016-07-28 |  | Henry | Stockbridge | 678 Fairhaven Blvd. Stockbridge, GA 30281 | 1400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/28/2016 12:00:00 AM | Unknown |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease from upline users | Cleaned up spill area around manhole, placed spill notifications signs around spill area, started stream monitoring program and notified all of the proper agencies. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-13 | 2018-06-13 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | WSA Manhole 8148 – 9130 Hwy 5, Douglasville, GA 30134 | 8150 |  | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Ground, Stream |  | Roots |  | Juan Robles | Juan Robles | Juan Robles | 6/13/2018 12:00:00 AM |  |  |  |  | 0 | Anneewakee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken clay line and root infiltration. | - Vac Truck crews were dispatched to the site and were able to clear the blockage. - Crews cleaned and disinfected the area around the manhole where the spill occurred. - Signs were posted in the area to notify residents and the public of the spill. - Notification given to EPD, the Health Department, and local media. | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-17 | 2017-08-17 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 5943 Yellow Wood Court, College Park | 13500 | Fax Received 08/18/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 8/18/2017 12:00:00 AM | Flint |  | 2017-08-18 |  | 1 | Camp Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 0 | Grease | Line was cleared of blockage, and flow returned to normal |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-21 | 0 | 1 | 1 | 0 | 0 | 0 | Jennifer Brandon | 770-302-3462 | CLAYTON COUNTY WATER AUTHORITY
2015-03-24 | 2015-03-24 |  | Fulton | East Point | 1063 Glendale Drive Betwween Manhole ID# SR-124-090 and SR-124-088 | 10 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South River Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The probable cause of the spill was due to debris in the main resulting into a discharge into the South River Basin. | The City's crew jetted and vacuumed out the Main to remove the blockage, and cleaned the affected area as required. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-20 | 2015-11-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 Handley Avenue, SW | 986 | fax received 11/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/21/2015 12:00:00 AM |  |  |  |  | 1 | Utoy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-15 | 2018-07-15 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Alpharetta | 2055 Grand Junction - Alpharetta | 29250 | Email(s) sent 2018-07-16 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/16/2018 12:00:00 AM |  | 7/15/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. to Big Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | PVC pipe, other construction debris | Jetted lines to clear blockage, vac truck, removed all solids, spread lime, posted signs, CCTV |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-21 | 2015-04-21 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2545 Forrest Hills Drive, SW | 1180 | fax received 4/21/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/21/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-15 | 2015-04-15 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2545 Forrest Hills Drive, SW | 990 | fax received 4/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/16/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-20 | 2015-04-20 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 600 New Town Circle, SE | 2095 | FAX received 4/21/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/21/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-28 | 2017-11-02 |  | DeKalb |  |  | 20 |  | Raw Sewage | Mountain District - Metro |  | Private Lateral | Stream | Stream | Equipment failure |  | Collan Campbell | Chance Grzesik | Chance Grzesik | 8/28/2017 12:00:00 AM | Unknown | 11/30/2017 12:00:00 AM |  |  | 1 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Sewer line was repaired by the owner. | 00821c09-89e5-4ae1-9781-36f426463098 | ad0db192-662d-47fb-9323-115816bb6cc1 | ad0db192-662d-47fb-9323-115816bb6cc1 | 2017-11-02 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 424 Lindbergh Dr NE - ATL | 25 | Fax received on 01/22/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Paul Moisan | Paul Moisan | 1/22/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown at this time. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRF | 0 | Verbal notification received ? | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill from BOD violation: Reported BOD = 32 mg/L. Estimated volume = ~91.7 MG |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-30 | 2015-09-30 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/14/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 43.4 mg/L on 09/30/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-06 | 2018-03-06 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 963 Bridge Mill Avenue, Canton | 11484 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/7/2018 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Asphalt in line | Construction crew jetted line and removed debris | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-03-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-13 | 2016-03-13 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 466 Adrian Place, Macon MH ID 71489 | 1800 | Email received on 03/15/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/15/2016 12:00:00 AM | Upper Ocmulgee | 3/13/2016 12:00:00 AM |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that the cause was grease and rags. | After the blockage was removed, the affected area was disinfected with lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-16 | 0 | 1 | 0 | 0 | 0 | 0
2017-11-16 | 2017-11-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 501 Connell Ave. SW - ATL | 825 | EDIT 2018-02-21: Spill volume updated from 30 to 825 gallons Fax sent 2017-11-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  | Alys Hannum |  | Alys Hannum | 11/17/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2016-01-13 | Thomaston, City of | Upson | Thomaston | Industrial LIft Station | 6950 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/13/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The cause of this spill was hydraulic overload due to heavy rain in the COT service area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-26 | 2016-09-26 | Cobb County Water System | Cobb |  | 1933 Falcon Wood Drive | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/26/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2017-07-25 | Rome, City of (Rome WRF) | Floyd |  | 360 Feet south of the City of Rome's Green Acre lift station in the sewer right of way | 21600 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Other |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/26/2017 12:00:00 AM | Coosa |  |  |  | 1 | Oostanaula River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was the result of a large tree falling on a manhole. The impact of the tree broke the manhole cover in half which landed at the bottom of the manhole causing the outlet pipe to become obstructed. | The sewer main was thoroughly cleaned | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-05 | 2017-06-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2020 Peachtree Rd. NE - ATL | 95 | Email received 2017-06-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/6/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-20 | 2016-12-20 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 1965 Winding Trail Crossing | 1800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/20/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Line Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | disposable rags, maybe roots | Jet the city sewer main | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-28 | 2017-04-28 | Paulding County (Coppermine Road WPCP) | Paulding |  | Enterprise Drive and Highway 278, Hiram | 1000 | Check all grease traps and manholes in the area to insure they are being maintained properly Violation is being addressed by EECO | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Matthew Stickney | Kathy Lewis | Eric Dykes | 4/28/2017 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease build up and rags | Jet lines | 77dbdd3c-0b48-49c2-b623-a78b1b0170cf | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3924 Roman Court, Tucker | 1620 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | South fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 14:24 hours when the heavy rain stopped and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-21 | 2017-08-21 | Cobb County Water System | Cobb |  | 2570 North Cobb Pkwy | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleaned and Limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-20 | 2016-05-20 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 455 Newton Bridge Rd., Athens | 178 | Initial email and full report faxed 5/20 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 5/20/2016 12:00:00 AM | Oconee | 5/20/2016 12:00:00 AM |  |  | 1 | unnamed tributary to North Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Towels clogged the sewer line causing a manhole to overflow | Rodded the line, cleaned and limed area |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-10-31 | 2017-10-31 | East Point (City of)- Sewers | Fulton | East Point | North of Leith Ave. | 51300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Branch of Utoy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Diapers | The city removed the blockage. Details in report. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-17 | 2016-07-17 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 3434 Pinemont Drive, Douglasville Manhole #9683 | 40500 | Fax received on 07/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 7/18/2016 12:00:00 AM | Chattahoochee | 7/18/2016 12:00:00 AM | 2016-07-18 | 2017-08-07 | 1 | Anneewakee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Possible debris in line. | Mechanics and VacCon crews were dispatched to the site and, due to redundancy at the Soouthside L.S., crews were able to divert flow into the second wet well to stop the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-22 | 0 | 1 | 0 | 1 | 1 | 0 | Keith Higgs | 770-920-3872 | Douglasville Douglas County Water and Sewer Authority (DDCWSA)
2017-06-20 | 2017-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 424 Lindbergh Dr. NE - ATL | 110100 | Email received 2017-06-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  | 6/20/2017 12:00:00 AM | 2017-06-21 | 2018-07-12 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The spill was rain-induced. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 1 | 1 | 0
2017-04-03 | 2017-04-05 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 30000 | Stream monitoring ceased. Stream monitoring initiated under the January 16, 2018 major effluent spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream | Other |  | Delaine Scott | Delaine Scott | Delaine Scott | 4/12/2017 12:00:00 AM | Savannah | 4/12/2017 12:00:00 AM | 2017-04-04 |  | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The weekly max BOD effluent limitation was exceeded by greater than 50% resulting in a major effluent spill of treated wastewater. The exceedance was due to the construction upgrades at the treatment plant effluent structure. In order to construct the new/upgraded effluent structure, the treatment pond levels had to be significantly lowered, resulting in insufficient BOD reduction. | Stream monitoring initiated. Public notification posted at City Hall on 4/12/17; notification to the Burke Co. Health Department on 4/12/17; and notification published in the Burke County True Citizen newspaper on 4/19/17. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2017-04-19 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-14 | 2016-04-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 217 Hillside Drive, NW | 640 | fax received 4/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/15/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-15 | 2016-01-15 | Tifton, City of (New River WPCP) | Tift | Tifton | Intersection of Hwy. 82 at I-75 (Exit 62), in the southwest intersection off ramp heading south, Tifton. | 2000 | Email was received on 01/15/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/16/2016 12:00:00 AM |  | 1/15/2016 12:00:00 AM |  |  | 1 | Cowhouse River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to a grease blockage. | Hydrated lime was spread to mitigate and sanitize the area. The blockage of grease was cleared |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-23 | 2016-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | verbal notification received 2/24/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/24/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill for TSS. Permit Limit = 25 mgL; Reported Value = 110 mg/L. Spill volume ~91.7 MG. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-30 | 2016-01-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 5251 Peachtree Industrial Boulevard, Chamblee | 2640 | Notification received on February 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 1/30/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 18:30 hours, when a crew installed two 4" bypass pumps to route the flow around the blockage and restored normal flow until repair can be made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-02 | 2017-06-02 | Dekalb County (Snapfinger Creek WPCP) |  | Decatur | 1301 Oakview Road, Decatur | 3360 | Notification received on June 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/2/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:55 hours when the crew pressure washed the sewer 50ft, cleared the grease blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Savannah, City of (President Street WRF) | Chatham | Savannah | 1210 Murphy Ave., Savannah, GA | 240 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Storm Drain, Stream | Canal | Natural Disaster |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM | Savannah | 10/9/2016 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage during Hurricane Matthew. Lift station has no generator. | Cleaned spill site with vac trucks. Checking station more frequently until power is restored. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-19 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1918 Delowe Place, SW | 900 | emailed spill report recieved 12/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/26/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-20 | 2016-01-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 9817 Ivey Ridge Circle, Jonesboro MH # 22668369 | 520 | Fax received on 01/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/20/2016 12:00:00 AM | Flint |  |  |  | 1 | Swamp Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-22 | 0 | 1 | 1 | 0 | 0 | 0
2018-05-15 | 2018-05-15 | Cobb County Water System | Cobb |  | 1155 South Cobb Drive | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Olley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Clay Main | Stopped spill at 18:08 and washed road down | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | Effluent box located adjacent to the Casey Plant, and the Flint River. | 43750 | Complaint called in by CCWA on 12/24/15, and emailed Paul Moisan on 12/28/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  | 0 | The effluent box located at a point by the Flint River, adjacent to the Casey Plant overflowed highly treated plant effluent due to the total rainfall of 6.24 inches in two days. | Clayton County Water Authority is working to eliminate all inflow and infiltration in the wastewater conveyance system. The CCWA staff inspect, test, and perform direct repairs to a sewer system that includes over 1,250 miles of sewer lines, carrying sewerage to three water reclamation facilities. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-14 | 2018-02-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2197 Martin L King Jr. Dr. NW - ATL | 35 | Fax sent 2018-02-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/15/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-23 | 2016-06-23 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Dacula | 3438 Jordan Lea Lane | 2351 | fax received 6/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/24/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Apalachee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | raked area and spread lime; placed signs at spill and affected waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-04-03 | 2018-04-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3854 West Nancy Creek Place, Atlanta GA 30319 | 2160 | manhole 18-327-s031 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System |  |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/4/2018 2:00:00 PM | Ocmulgee |  |  |  | 1 | Perimeter Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-26 | 2018-03-26 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1060 Scott St. | 14 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/26/2018 12:00:00 AM | Upper Ocmulgee |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ragging and Debris in Sag |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-22 | 2016-07-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2097 Vineyard Walk, Atlanta | 3400 | Notification received on July 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/22/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 18:02 hours, when a crew pressure washed the sewer main, cleared the blockage at 63 ft. and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-09 | 2017-08-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 245 Riverside Dr | 134 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/9/2017 12:00:00 AM | Oconee |  |  |  | 0 | Middle Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | damaged pipe at manhole structure | patched pipe and resealed manhole | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-09 | 2015-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1064 Parsons Street, SW | 250 | fax received 10/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/11/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-16 | 2015-11-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2145 Lawrenceville Hwy, Decatur | 3225 | Notification received on November 18, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 11/16/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 15:07 hours when a crew rodded the sewer main 100ft upstream, root-cut the sewer main 1000ft, clearing the blockage at 785ft and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-12 | 2017-01-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 348 Armour Dr NE - ATL | 6900 | Fax received on 01/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/13/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. Steps taken to prevent reoccurence. Placed on periodic inspection schedule - need for upgrading, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-09-07 | 2017-09-07 | Columbus Water Works (South WRF) | Muscogee | Columbus | Behind Bldg #2853 off Way St. in Ft. Benning | 335 | Telephone call and fax received on 09/07/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Roots |  | Paul Moisan |  | Paul Moisan | 9/7/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Laundry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the SSO was root infiltration in an 8" line. | Stop-up was cleared and flow returned to normal | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-24 | 2017-02-24 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1281 Bass Road, Macon MH ID 65316 | 1680 | Email received on 02/28/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/28/2017 12:00:00 AM |  |  |  |  | 1 | Beaverdam Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that the cause of this spill was grease. | Debris was removed from the affected area and the area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-01 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-21 | 2015-05-21 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawrenceville | Alcovy Trails Pump Station | 1000 | fax received 5/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/21/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Alcovy River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Clogged ARV | Changed out ARV |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY | 678.376.7000
2018-04-01 | 2018-04-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3831 East Avenue Clarkston GA 30021 | 880 | manhole not named | Raw Sewage |  | GA0024147 | Collection System |  |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/1/2018 9:40:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | structural damage | Used bent shovel in the mouth to knock debris loose |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-06 | 2015-02-06 | Savannah, City of (President Street WRF) | Chatham | Savannah | 2101 Kollack Street West | 2480 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 2/6/2015 12:00:00 AM | Savannah | 2/6/2015 12:00:00 AM |  |  | 1 | Springfield canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Lift Station 26 – Stiles Avenue Force Main Break – crack in bell of 12” PVC pipe | Turned off lift station and repaired force main break. Contained ditch to stop sewage from entering Springfield Canal. Samples were taken upstream and downstream of spill and will place spill notification markers at Springfield Canal near Bowles Ford Park, West Gwinnett Street at Springfield Canal, and at West Oglethorpe Avenue / Springfield Canal. A 5,000 gallon frac Tank was placed at Lift Station 26 to handle the flows at that station. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who notifies local media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-02-23 | 1 | 1 | 1 | 0 | 0 | 0
2015-03-20 | 2015-03-20 | Robins Air Force Base | Houston |  | Bay #3, Repair Hangar, Building 131 | 0 | Notification received by call and later report sent to EPD. | Solvent | Wastewater Regulatory Program |  | N/A | Stream |  | Equipment failure |  |  | Sarita Banjade | Sarita Banjade | 3/21/2015 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fire alarm activation in bay #3, causing release of Aqueous Film Forming Foams (AFFF) inside the bay to suppress the suspected fire. | AFFF diverted to a storage tank as designed. AFFF washed inside the hangar |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-04-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ROBINS AIR FORCE BASE | 4789269645
2015-04-07 | 2015-04-07 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 900 Garden Walk Blvd | 7200 | REC FAX 4/8/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/8/2015 12:00:00 AM | Flint | 4/8/2015 12:00:00 AM |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Cleared Blockage. Televise line | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-08 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 678-422-2834
2016-07-25 | 2016-07-25 | Columbia County (Crawford Creek WPCP) | Columbia | Grovetown | 307 Lochleven Court | 2000 | fax received 7/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Other |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/25/2016 12:00:00 AM |  |  |  |  | 1 | Private Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, rags, and debris | Unstopped sewer main with high pressure jet machine. Cleaned up overflow. Spread lime. Posted signs. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2016-12-27 | 2016-12-28 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 25000 | Stream monitoring ceased for the December 27th effluent major spill upon the facility initiating stream monitoring for the January 4-5th major effluent spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/4/2017 12:00:00 AM | Savannah | 1/6/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Chandler's Branch | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. | Stream monitoring initiated 1/4/17. Public notification posted at City Hall 1/5/17. Notification to the Burke Co. Health Department completed on 1/4/16; and notification was published in the Burke County True Citizen newspaper in the January 11, 2017 edition. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2017-01-05 | 1 | 1 | 0 | 1 | 0 | 0
2018-08-08 | 2018-08-08 | Pine Mountain, Town of (Pine Mountain WPCP) | Harris |  |  | 500 |  | Raw Sewage | West Central District | GA0025691 | Lift Station | Stream | Stream | Equipment failure |  |  |  | Stephanie Edwards | 8/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 426838fe-eb6e-11e0-b8d8-000c29971acc |  | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-01 | 2018-08-02 | Polk County (Aragon WPCP) | Polk |  | Chlorine contact chamber at Aragon WPCP | 6000 |  | Raw Sewage | Mountain District - Cartersville | GA0026182 | WWTP | Stream |  | Wet weather |  | Katie Meade | Kathy Lewis | Katie Meade | 8/7/2018 12:00:00 AM | Coosa |  |  |  | 1 | Euharlee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain and flooding in the area. | Pumped chlorine contact chamber out back to oxidation ditch and turn aerator to auto to keep solids from leaving oxidation ditch | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-10 | 1 | 0 | 0 | 0 | 0 | 0
2018-03-17 | 2018-03-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1928 Shawn Wayne Circle, Atlanta GA 30316 | 3040 | manhole 15-140-s207 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/17/2018 5:40:00 PM | Ocmulgee |  |  |  | 1 | Intrenchment Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Pressure wash sewermain |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-19 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-04 | 2017-04-04 | Athens-Clarke County (North Oconee WPCP) | Clarke | athens | 853 Bobbin Mill Road | 2970 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/4/2017 12:00:00 AM | Oconee |  |  |  | 0 | Brooklyn Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure | Rodded and repaired line | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-12 | 2015-11-12 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 12/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to go up to 27.0 mg/L on 11/12/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-05 | 2018-06-05 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8277 Dunellen Lane | 2500 | Fax sent 5/7/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Juan Robles | Juan Robles | 6/7/2018 12:00:00 AM |  |  |  |  | 0 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine cause. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-30 | 2018-05-30 | MACON WATER AUTHORITY - ROCKY CREEK WPCP | Bibb | Macon | Easement to Riverside Cemetery Lift Station, MH ID 66892. | 405000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/30/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Ocmulgee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause of this major spill was a lift station malfunction. There was a power outage at the station and the generator did not start. | Debris has been removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-29 | 2018-03-29 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Swainsboro Crooked Creek WWTP | 62500 | Phone call made 2018-03-30. This spill is also entered as a violation. | Treated Effluent | Wastewater Regulatory Program | GA0039225 | WWTP | Stream |  | Contractor |  |  | Alys Hannum | Alys Hannum | 3/30/2018 12:00:00 AM |  |  |  |  | 1 | Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | "on March 30th, 2018, at approximately 6:15 pm on March 29th, 2018, our main effluent line was ruptured during contractor construction." | "Flow was diverted to storage pond at 8:15 pm. Area of line damage is in a creek waterbed of at least 4 to 5 feet of water, not counting effluent flow from damaged line. We will divert flow to our former discharge site, Crooked Creek on today’s date. We anticipate this diversion until at least April 14th, circumstances permitting, to allow us to divert natural creek flow and get to and repair the damaged line." |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1160 Peachtree Battle Ave. NW - ATL | 1000 | Fax sent 2018-02-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/16/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-24 | 2016-04-24 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | Carlton Woods Lift Station, 0 Wood Ridge Rd., Moultrie | 2000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System | Stream |  | Power failure |  |  | Dagny Pariani | Dagny Pariani | 4/24/2016 12:00:00 AM | Ochlockonee |  |  |  | 1 | unnamed tributary to Ochlockonee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power tripped at a lift station | Reset power |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2015-12-17 | 2015-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2479 Abner Terrace, NW | 3180 | fax received 12/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/18/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-16 | 2017-03-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2170 Defoor Hills Rd. NW - ATL | 399 | Fax received 2017-03-17. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 3/17/2017 12:00:00 AM |  | 3/16/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-07 | 2015-03-07 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | This is an outfall spill. Reported TSS = 228 mg/L; Volume = ~35,000,000 | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/8/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | The facility experienced a failure of the TWAS centrifuges and the facility was unable to remove sufficient solids from the waste stream. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-21 | 2016-04-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1011 Welch Street, SE | 1020 | fax received 4/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/21/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-17 | 2018-08-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3019 Fields Drive Lithonia GA 30038 | 200 | manhole#16-087-s031 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 8/18/2018 12:04:00 AM | Ocmulgee |  |  |  | 0 | Pole bridge Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | Pressurewashed manhole to clear blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-28 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 36225 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/20/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | The problem was corrected at 18:45 hours when the crew waited for the storm event to subside. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-16 | 2015-02-16 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Manhole beside Forrest Street | 100 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 |  | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 2/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage overflowed the manhole as a result of grease build up blocking the sewer line. | The line was jetted out, unclogged, and returned to service. The affected area leading to the tributary was treated with hydrated calcium carbonate. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-02-19 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-894-3085 | CITY OF CORNELIA
2015-09-23 | 2015-09-23 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/14/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 65.6 mg/L. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-04 | 2018-08-04 | Polo Golf & Country Club WPCP | Forsyth |  | On the N.E. side of 6135 Polo Drive, Cumming GA. Manhole on Golf Course in rough | 2000 |  | Raw Sewage | Mountain District - Cartersville | GAJ030950 | WWTP | Stream |  | Power failure |  | Katie Meade | Kathy Lewis | Katie Meade | 8/6/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Cheatham Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lightening strike, power surge. Breaker, autodialer, and 2 pumps burst and open | Pumps pulled, spare breaker, pump installed. Dialer ordered. Cleaned area approx. 7' x 10' and removed to dumpster. | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-14 | 1 | 0 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1000 Peachtree St. - ATL | 2610 | Email received 2017-06-20 Update 8/22/17 - Spill is private, not public. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-30 | 2016-04-30 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Sugar Hill | 4804 Highland Avenue | 4655 | fax received 4/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/3/2016 12:00:00 AM |  |  |  |  | 1 | Level Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks or construction material | raked area and spread lime; placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-06-08 | 2015-06-08 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Atlanta | 1321 Interstate Parkway | 450 | fax received 6/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/10/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The line was opened and resumed normal flow. The line will be added to the grease control program |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-12-08 | 2015-12-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forrest Park | 1465 Cherokee Trail, Forest Park MH #2204641 | 3200 | Fax received 12/08/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  |  |  |  | Paul Moisan | Paul Moisan | 12/8/2015 12:00:00 AM |  |  |  |  | 1 | Conley Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Probable cause - grease | Cleared blockage. Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-09 | 0 | 1 | 1 | 0 | 0 | 0
2018-09-17 | 2018-09-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1123 Braemar Ave. SW - Atlanta | 1900 | Fax sent 2018-09-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/18/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew made mechanical repairs to the mainline to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-08 | 2016-11-08 |  | Clarke | Athens | 130 Easy St. | 3660 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/8/2016 12:00:00 AM | Oconee |  |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | sewer joint leaking and entered storm drain pipe. | repaired sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-25 | Cochran WPCP | Bleckley | Cochran | Three manholes nearest S 5th St and E Lewis St, nearest E Peter St and S 5th St, and S 5th St. and E Peacock St. | 15000 | REC email 2/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0032107 | Collection System | Storm Drain | Stream | Wet weather |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/26/2015 12:00:00 AM | Ocmulgee | 2/26/2015 12:00:00 AM |  |  | 1 | Jordon Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Rain | Solids removed around manholes and jet line | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN
2018-02-15 | 2018-02-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1784 North Decatur Road, Atlanta | 1740 | manhole 16-052-s125 | Raw Sewage |  | GA0024147 |  |  |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/15/2018 5:23:00 PM | Ocmulgee | 2/15/2018 12:00:00 AM |  |  | 1 | Peavine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-13 | 2017-02-13 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 831 Sweet Briar Lane | 1000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/13/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Honey Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Grease and Debris | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-13 | 2017-02-13 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 831 Sweet Briar Lane | 1000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/13/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Honey Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Grease and Debris | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-15 | 2015-12-15 | Cobb County MS4 | Cobb |  | 70 Rhodes Drive | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of roots in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The crew stopped the overflow at 10:22 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-18 | 2016-12-18 | Marietta (City of)- Sewers | Cobb | Marietta | 808 N Saint Marys LN | 8700 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Debris |  | Reginald Williamson | Reginald Williamson |  | 12/20/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A sewer line had a piece of rip rap at the line which gatered debris and caused flow issues and backing up. Some sewage flow escaped the pipe and entered the creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2017-08-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 4664 Flat Bridge Road, Lithonia | 5 | Notification received on September 5, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/30/2017 12:00:00 AM |  |  |  |  | 0 | Polebridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Coupling disconnected on water hose causing a spill | The problem was corrected at 08:30 hours when the hose was repaired by reattaching the coupling. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-06 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-12 | 2016-10-12 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Dacula | 190 Hebron Church Road | 4320 | fax received 10/12/2016. Corrected fax received 10/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 10/12/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Hopkins Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-10-01 | 2016-10-01 | Fulton County (Big Creek WPCP) | Fulton | Atlanta | 7040 Tangletree Drive | 2580 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-16 | 2017-05-16 | Ashburn, City of (Airport WPCP) | Turner | ashburn | MLK Lift Station | 300000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/16/2017 12:00:00 AM | Suwannee |  |  |  | 0 | ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | wet weather |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-13 | 2015-11-13 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 1831 Warren Place | 69750 | ERT notified 11/13/2015. CTS No. 78296. Fax received 11/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  |  |  |  | Kim Hembree | Kim Hembree | 11/13/2015 12:00:00 AM |  |  | 2015-11-13 | 2016-11-29 | 1 | North Fork Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-13 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | GWINNETT COUNTY
2015-11-02 | 2015-11-02 | Marietta (City of)- Sewers | Cobb | Marietta | 554 Heyward Cir | 2040 |  | Raw Sewage | Mountain District - Cartersville |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Capacity Failure and Wet Weather I/I |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-09 | 2018-03-09 | Fulton County (Big Creek WPCP) | Fulton | Johns Creek | 160 Norwick Way Johns Creek | 7960 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/9/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Johns Creek | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 1 Knowlton Way - Crossroads Lift Station 155 force main | 270 |  | Raw Sewage | Coastal District |  | WWTP | Storm Drain | Ditch | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 8/18/2015 12:00:00 AM | Savannah | 8/18/2015 12:00:00 AM |  |  | 0 | Savannah River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Force main failure (split on bottom of pipe) | Turned station off and utilized City Contractor, City contracted jet-vacs, along with City of Savannah staff and City jet-vacuum trucks to clean sewage and remove extraneous / residual flows from ditch and area. Ditch was contained to stop sewage from continuing to flow into ditch. Replacement of force main is being planned. Spill notifications will be placed at spill site near lift station 155 and where the storm drainage system crosses Crossroads Parkway. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who will send out a news release to the media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-08-20 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way, SW | 840 | Fax received 2/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/26/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 788 Wesley Drive, NW | 17250 | fax received 12/24/2015. CTS No. 78623 Volume originally entered as 32,100 gal. Volume on final SMP = 17,250 gal. Changed 2017-04-04. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  | 2015-12-24 | 2017-01-13 | 1 | Peachtree Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-17 | 2018-09-17 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 219 Mincey St - Dublin | 7000 | Email sent 2018-09-18 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Collection System | Stream | Stream | 3rd party contractor |  |  | Alys Hannum | Alys Hannum | 9/18/2018 12:00:00 AM |  | 9/17/2018 12:00:00 AM |  |  | 1 | Ferry Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure and debris in the line | Crew repaired damage caused by 3rd party contractor. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-18 | 1 | 1 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1496 Country Squire Drive, Decatur | 11350 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/21/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | The problem was corrected at 21:30 hours when the crew waited for the storm event to subside. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-20 | 2016-08-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3169 Lynnray Drive, Doraville | 4720 | Notification received on August 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/23/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:20 hours when a crew pressure washed the sewer main, cleared the blockage, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-06 | 2018-03-06 | Cobb County Water System | Cobb | Marietta | 1260 Timberland Dr. | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/6/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Terrell Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" clay | Limed Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 2017-08-14 | Cobb County Water System | Cobb |  | 1291 Stanley Road | 560 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/14/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped the overflow at 11:20 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-17 | 2016-03-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1990 Alison Court, SW | 425 | fax received 3/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/21/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-07 | 2016-08-07 | Thomaston, City of | Upson | Thomaston | Old City Hall Lift Station 3rd Ave & L St. SW | 800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/7/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was due to a power outage. | The affected area was clean and disinfected. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-18 | 2016-04-18 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Behind the chemical building off of Central Shop Road | 420 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Debris |  |  | Dagny Pariani | Dagny Pariani | 4/18/2016 12:00:00 AM | Oconee | 4/18/2016 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blocked the sewer line | Unclogged sewer line, cleaned area, put out lime |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2017-06-08 | 2017-06-08 | Douglas, City of (Southeast WPCP) | Coffee |  | South East WPCP at 622 Iron Road | 12000 |  | Raw Sewage | Coastal District | GA0024431 | Lift Station | Ditch | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 6/16/2017 3:00:00 PM | Satilla | 6/8/2017 12:00:00 AM | 2017-06-08 |  | 1 | Unnamed tributary of Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Faulty submersible backup pump with excessive rainfall. | Pump is to be repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-06-16 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-03 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 3488 Boring Road | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded and pressure washed sewer main to remove blockage and restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-08 | 2017-01-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3352 North Druid Hills Road, Decatur | 6500 | Notification received on January 11, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/8/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:45 hours, when a crew pressure washed the 8" sewer main 355ft, clearing the grease/rags blockage at 300ft and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-29 | 2016-02-29 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 3765 Maple Valley Drive | 3550 | verbal notification received 2/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/1/2016 12:00:00 AM |  |  |  |  | 1 | Tributary of Sawmill Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The blockage was jetted and the spill stopped. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CUMMING
2017-07-11 | 2017-07-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 5365 Wellborn Creek Drive, Lithonia | 1580 | Notification received on July 13, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/11/2017 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creekl | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:40 hours when a first responder crew pressure washed the 8 inch sewer main 100 ft, removed the grease blockage at 65 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-13 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-31 | 2016-01-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4227 Victory Drive, Columbus, GA | 29445 | Fax and email received on 01/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into the Chattahoochee River. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2018-05-13 | 2018-05-13 | Dekalb County (Snapfinger Creek WPCP) | Clarke | Athens | 296 The Plaza | 2493 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/15/2018 12:00:00 AM | Oconee |  |  |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | wipes | rodded and flushed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-06 | 2018-06-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4801 Summerford Drive Dunwoody GA 30338 | 2680 | 18-362-s011 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/7/2018 4:55:00 PM | Ocmulgee |  |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | pressurewashed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-13 | 2018-07-13 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 6 Lee Street - Winder | 3375 | Fax sent 2018-07-13 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/13/2018 12:00:00 AM |  | 7/13/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. to Fort Yargo Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Jetted main to relieve blockage; sanitized area with powdered lime; CCTV |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3279 Ohara Drive N, (MH ID 52091). | 4445 | Fax received on 12/23/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/23/2015 12:00:00 AM |  |  |  |  | 1 | Ditch feeding Rocky Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause was hydraulic overload. The MWA service area received 3.18 inches of rainfall on Decemver 21 and 22. | Debris will be moved from the area, and the affected area will be disinfected with lime. The MWA Maintenance Department bought a by-pass pump to assist the station during the heavy rainfall. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1518 Cherokee Ave., Columbus, GA | 9560 | Fax received 12/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-21 | 2015-01-21 |  | DeKalb | Brookhaven | 2801 Buford Hwy, Brookhaven | 4500 | Notification received on January 22, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/22/2015 12:00:00 AM |  |  |  |  | 0 | Northfork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:10 hours when a crew pressure washed the 8" sewer main 450ft clearing the grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-03 | 2015-12-03 | Cobb County (RL Sutton WRF) | Cobb |  | 811 Dorado Cir | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/14/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Cleaned spill area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | Chuck Roshak |  | Cobb Co Public Works
2018-05-29 | 2018-05-29 | Chatham County | Chatham | Savannah | 130 Cardinal St., Savannah, GA | 2500 | Initial phone call 5/30/18. Full report emailed 5/31/18. | Raw Sewage | Coastal District | GAU060099 | Collection System | Storm Drain, Stream | Stream | Equipment failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 5/30/2018 12:00:00 AM | Savannah |  |  |  | 1 | Herb River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The Central Avenue lift station was running on a bypass pump when the pump lost prime resulting in seepage from a manhole. | 2 bypass pumps were installed at the lift station. 24 hour monitoring by personnel until the primary and secondary pumps at the station can be replaced. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-05-31 | 0 | 1 | 0 | 0 | 0 | 0
2018-09-12 | 2018-09-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1890 Austin Rd. SW - Atlanta | 460 | Fax sent 2018-09-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/13/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-09 | 2017-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 455 E Paces Ferry Rd. NE - ATL | 5925 | Fax sent 2017-10-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/10/2017 12:00:00 AM |  | 10/9/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-01 | 2018-07-01 | Cobb County Water System | Cobb |  | 6563 Mitchell Ln | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 7/1/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Queen Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The crews stopped the spill at 1:30 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-28 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Woods St., NW, Atlanta | 744500 | Telephone call and fax received on 10/28/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/28/2016 12:00:00 AM |  |  | 2016-10-28 | 2017-10-27 | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed main line. | The crew repaired a by-pass pump to contain the spill. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-02 | 0 | 1 | 0 | 1 | 1 | 0 | Chris Jefferson |  | ATLANTA, CITY OF
2016-10-28 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Woods St., NW, Atlanta | 744500 | Telephone call and fax received on 10/28/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/28/2016 12:00:00 AM |  |  | 2016-10-28 | 2017-10-27 | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed main line. | The crew repaired a by-pass pump to contain the spill. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-02 | 0 | 1 | 0 | 1 | 1 | 0 | James Mitchell |  | ATLANTA, CITY OF
2015-02-26 | 2015-02-26 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Rd. and Syvia Dr. | 70000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/26/2015 12:00:00 AM | Suwannee | 2/26/2015 12:00:00 AM |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was due to flows that exceded the capacity of the Rockhouse Rd lift station. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-29 | 2015-11-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1320 Memorial Drive, SE | 2000 | fax received 11/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-23 | 2015-03-23 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 41.6 mg/l
2017-07-10 | 2017-07-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 645 DeKalb Industrial Way, Decatur | 20 | Notification received on July 11, 32017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/10/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:09 hours when a crew pressure washed the sewer main 324 ft, removed the grease blockage at 273 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-11 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-13 | 2017-04-13 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2035 Dove St., Macon MH ID 69792 | 3120 | Email received on 04/17/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 4/17/2017 12:00:00 AM | Ocmulgee | 4/14/2017 12:00:00 AM |  |  | 1 | Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that the cause of this spill was grease and roots. | Debris was removed, and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-24 | 2016-09-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 104 Sedgefield Drive, Riverdale Manhole 2211009 | 7000 | Fax received on 09/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System |  |  | Roots |  |  | Paul Moisan | Paul Moisan | 9/25/2016 12:00:00 AM | Flint |  |  |  | 1 | Unnamed tributary of Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Roots | Cleared blockage, and flow was returned to normal. Site was cleaned, and work orders generated for additional work to determine cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-09-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-16 | 2015-01-16 |  | Fulton |  | 4355 Cascade Road-Atlanta | 1800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The section of the sytem will be inspected. The area impacted has been cleaned. Inhibitors have been applied to minimize odors. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-03 | 2015-11-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 595 | fax received 11/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/4/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-28 | 2017-07-28 | Columbia County (Crawford Creek WPCP) | Columbia | Grovetown | 4562 Country Glen Circle - Grovetown | 2500 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/28/2017 12:00:00 AM |  |  | 1 | Euchee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Dirt and construction debris | Unstopped sewer main with high pressure jet machine. Cleaned up spill area. Posted signs. Planned follow up cleaning to remove dirt. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 359 Fielding Ln. SW - ATL | 19200 | Fax received 2017-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM | 2017-04-12 | 2018-04-27 | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rain-induced. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 1 | 1 | 0
2016-06-23 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 77 Peachtree Place, NE | 1364 | This is a private spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Kim Hembree | Kim Hembree | 6/24/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-04 | 2018-06-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 241 Scott St. NW - Atlanta | 2850 | Fax sent 2018-06-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Alys Hannum | 6/5/2018 12:00:00 AM |  | 6/4/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism and debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-21 | 2016-08-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3545 International Park Drive, Atlanta | 15505 | Notification received on August 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/21/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main due to soil erosion. | A DeKalb County crew responded immediately and found an 18" sewer main broken due to bank erosion; causing a spill of approximately 15,505 gallons into the South river. The spill was contained at 12:20 hours and is undergoing repairs to the pipe presently. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Savannah, City of (President Street WRF) | Chatham | Savannah | 414 Lee Blvd., Savannah, GA | 1475 | Inital notification via phone and full report received via email on 9/12. | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Natural Disaster |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/12/2017 12:00:00 AM | Savannah | 9/12/2017 12:00:00 AM |  |  | 1 | Hampstead Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe collapsed from excessive flows during Hurricane Irma | Repaired collapsed section of pipe and installed manhole monitor. Will schedule downstream pipe for repairs. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6584
2017-09-11 | 2017-09-11 | Savannah, City of (President Street WRF) | Chatham |  | 414 Lee Blvd., Savannah, GA | 1475 | Inital notification via phone and full report received via email on 9/12. | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Natural Disaster |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/12/2017 12:00:00 AM | Savannah | 9/12/2017 12:00:00 AM |  |  | 1 | Hampstead Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe collapsed from excessive flows during Hurricane Irma | Repaired collapsed section of pipe and installed manhole monitor. Will schedule downstream pipe for repairs. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6584
2018-02-18 | 2018-02-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 1145 Cleavemark Drive, Clarkston GA 30021 | 5270 | manhole 18-120-s301 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Force Main | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/18/2018 6:54:00 PM | Ocmulgee | 2/18/2018 12:00:00 AM |  |  | 1 | Snapfinger Creek Tributary C | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease | Presure washed main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-05 | 2018-02-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1160 Peachtree Battle Ave. - ATL | 25 | Fax sent 2018-02-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-19 | 2018-01-19 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2183 Hampton Trail | 9000 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System |  | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/19/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Remove Trash and Debris then install bolt down Cover | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-02 | 2018-01-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 821 Celeste Ln. SW - ATL | 2175 | Fax sent 2018-01-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 1/3/2018 12:00:00 AM |  | 1/2/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-16 | 2016-06-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3707 Roswell Road, NE | 1800 | fax received 6/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/17/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and possibly a collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-08 | 2016-02-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 359 Fielding Lane, SW | 500 | fax received 2/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-05 | 2015-09-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 672 Quaker Street, SW | 500 | fax received 9/06/2015. This is a private spill | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/6/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed private lateral |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-30 | 2017-09-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2164 Faulkner Rd. NE - ATL | 5580 | Fax sent 2017-10-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/1/2017 12:00:00 AM |  | 10/1/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a bypass pump to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2017-07-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2705 Harrington Pl. SW - ATL | 2610 | Fax received 2017-07-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/21/2017 12:00:00 AM |  | 7/21/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew made repairs to the mainline to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-02 | 2018-05-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1451 Centra Villa Dr. SW - Atlanta | 60 | Fax sent 2018-05-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/4/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-21 | 2018-04-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 4241 Hendrix Drive, College Park | 6300 | Fax received on 04/21/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 4/21/2018 12:00:00 AM |  |  |  |  | 0 | Poole Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-04-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-05 | 2015-05-05 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  |  | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 64.0 mg/L on 05/05/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-29 | 2016-03-29 |  | Rockdale |  | 2271 Flat Shoals Road | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/29/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Inoperative Pump Station | Return pump station to operatable status | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2017-08-16 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1600 Kissingbower Rd. (#M0106) - Augusta | 1960 | Email received 2017-08-18 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Contractor |  |  | Alys Hannum | Alys Hannum | 8/18/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow was caused by a contractor cleaning sewer gravity mains. When the contractors were attempting to remove a large root ball, a large portion of the root ball fell back into the manhole, flowing down the pipe, creating a blockage. | Utilities C&M was contacted. The sewer gravity main was augered combined with other efforts in order to remove the root ball from the sewer gravity main and manhole. Lime was spread in the affected area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-24 | 2016-03-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4195 Bakers Ferry Road, SW | 4680 | fax received 3/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/25/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-31 | 2017-07-31 | Rome, City of (Rome WRF) | Floyd |  | 420 Feet East of the Georgia Power ROW GPS coordinates 34.24708, -85.29689 | 9400 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 8/1/2017 12:00:00 AM | Coosa |  |  |  | 0 | Beech Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was the result of a blockage due to roots in the sewer main. | The sewer main was thoroughly cleaned. The spill site is being cleaned and the content of the tributary is being pumped into the sewer system as part of the mitigation process. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-06 | 2015-01-06 | Fulton County MS4 | Fulton |  | 910 Oakhaven Drive Roswell 30075 | 8160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/6/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Little River | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. The area impacted by the spill is in the process of being cleaned. Inhibitors were applied to minimize odors. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-07 | 2016-05-07 |  | Cobb |  | 52 Vinings Lake Dr. | 390 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/7/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-01 | 2016-06-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3748 Hollow Oak Lane, Lithonia | 100 | Notification received on June 3, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/2/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | The problem was corrected at 20:22 hours, when a crew cleaned out the grease blockage from the invert and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-05 | 2016-08-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2840 Martin L. King Jr. Drive, SW | 3350 | fax recieved 8/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/6/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-06 | 2018-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3935 Ensign court, Chamblee GA 30341 | 5000 | repaired 4.7.2018 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/7/2018 12:42:00 PM | Ocmulgee | 4/6/2018 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken main | made repair, vactor truck on upstream manhole stopped overflow |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-05 | 2018-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 650 17th St. NW - Atlanta | 2950 | Due to the ransomware attack on City of Atlanta, reports are being handwritten. Some information may be missing or hard to read. Fax sent 2018-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-17 | 2015-03-17 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 32.2 mg/L
2015-05-26 | 2015-05-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3440 Boulder Park Drive | 30625 | Verbal notification received 5/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/27/2015 12:00:00 AM |  |  | 2015-05-27 | 2016-06-17 | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-28 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive, NW | 112000 | fax received 12/24/2015. CTS No. 78623 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-24 | 2016-10-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 4664 Flat Bridge Road, Lithonia | 200 | Notification received on October 25, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/24/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | leaking pipe | The problem was corrected at 9:20 hours when a crew turned off the valve to the pipe, repaired the pipe, and restored normal services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-31 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-18 | 2017-07-18 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Stockbridge | 109 Julie Lane, Stockbridge Manhole - 2195661 | 9600 | Fax received on 07/18/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 7/19/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Big Cotton Indian Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure. | Installed bypass pumps to stop event. Line will be repaired and creek bank re-established with rock to prevent further erosion. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-20 | 0 | 1 | 1 | 0 | 0 | 0
2016-08-08 | 2016-08-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2730 Peyton Springs Circle, SW | 5655 | fax received 8/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 8/9/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed main line | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-17 | 2017-04-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snapfinger Woods Drive, Decatur | 7200 | Notification received on April 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/17/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:45 hours when a crew rodded between manholes 100ft in the 8" sewer main, clearing the blockage at 50ft and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Tifton, City of (New River WPCP) | Tift | Tifton | Manhole located in the abandoned drive on Highland Ave., Tifton, GA 31794 | 370 | Email and phone call received on 01/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch |  | Other |  | Paul Moisan |  | Paul Moisan | 1/25/2016 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to a sewer line that was removed by the land owner. | Hydrated lime was spread to sanitize the affected land. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-01-28 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-02 | 2017-05-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 8304 Union Grove Road, Lithonia | 3420 | Notification received on May 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 5/2/2017 12:00:00 AM |  |  |  |  | 0 | Johnson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor drilling through an 8 inch sewer main and also a debris blockage | The problem was corrected at 11:15 hours when a crew pressure washed the 8" sewer main 277ft clearing the blockage at 275ft, completed the 8" sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-03 | 2016-10-03 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 4237 Napier Ave, Macon MH ID 63884 | 1800 | Email received on 10/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Roots |  |  | Paul Moisan | Paul Moisan | 10/5/2016 12:00:00 AM |  |  |  |  | 1 | Wolf Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots; after the blockage was removed, the line is scheduled to be cleaned and televised. | After the blockage (roots) was removed, the line is scheduled to be cleaned and televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-11 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-03 | 2016-05-03 |  | DeKalb | Atlanta | 1825 Clifton Road, Atlanta | 960 | Notification received on May 6, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 5/3/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing Leaking | The problem was corrected at 14:00 hours, when a crew repaired the sewer main with hydraulic concrete and oakum, stopped the leak and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-21 | 2016-07-21 | Thomaston, City of | Upson | Thomaston | City Hall LIft Station | 5250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary Ave L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was due to a power outage within the service area. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-13 | 2015-11-13 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 1 Knowlton Way | 50 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 11/13/2015 12:00:00 AM | Savannah | 11/13/2015 12:00:00 AM |  |  | 1 | St.Augustine Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | y | 0 | Lift Station force main break | Shut lift station off and contained residual waters from further entering into the storm drainage system. Set up City of Savannah by-pass pumps to pump waters back into City gravity system. City also utilized City vacuum trucks and City contractor to repair force main. All agencies (i.e. Health Department, State EPD, and the City of Savannah Public Information Office (who will issue the Public News Release)) were notified as required by State Guidelines. Notification will be posted on St. Augustine Creek, at spill site and at crosses Crossroads Parkway where ditch crosses. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-11-13 | 1 | 1 | 0 | 0 | 0 | 0
2018-04-27 | 2018-04-27 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 6558 Roswell Road Sandy Springs, 30328 | 1800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Marsh Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The spill has stopped and the manhole has been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-16 | 2017-12-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | EDIT 2/20: THIS IS A PRIVATE SPILL, NOT PUBLIC. 806 Pegg Rd. SW - ATL | 30 | EDIT 2/20: THIS IS A PRIVATE SPILL, NOT PUBLIC. Fax sent 2017-12-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 12/18/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | EDIT 2/20: THIS IS A PRIVATE SPILL, NOT PUBLIC. Unknown | EDIT 2/20: THIS IS A PRIVATE SPILL, NOT PUBLIC. Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1900 Block of East Park Avenue | 55000 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-05-23 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 514 Morris Road | 139766 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Lindsey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, sewer main has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-31 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Hazlehurst, City of (Bully Creek WPCP) | Jeff Davis | Hazlehurst | Cloversett Apartments | 8600 |  | Raw Sewage | Coastal District | GA0036765 | Lift Station | Ground, Storm Drain, Stream | Ditch | Equipment failure |  | Beth Stevenson | Bill Hawthorne | Bill Hawthorne | 4/4/2016 9:00:00 AM | Ocmulgee | 4/2/2016 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The City states that they believe pumps at the Kersey Street Lift station were "tripped-out" by lightning which cause the man-hole at the Cloversett apartments to spill over. | The lift station pumps were reset and placed back into service. | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-04-05 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | King Arthur Lift Station/King Arthur ROW. | 20250 | Initial report only, received on 09/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 9/11/2017 12:00:00 AM | Chattahoochee |  | 2017-09-12 |  | 1 | Pepperell Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Excessive rainfall overwhelmed sewer system/lift station - King Arthur Lift Station | Once rainfall subsides, lift station pumps will recover and surcharge will stop. I/I investigation and corrections will continue. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-13 | 0 | 1 | 0 | 0 | 0 | 0 | David Brown | 706-883-2010 | LaGrange (City of)
2016-02-12 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1825 Clifton Road, Atlanta | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defect in manhole | Berm was built to contain sewer coming from manhole |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-18 | 2015-01-18 | Cobb County MS4 | Cobb |  | 1841 Silver Leaf Ct./Merry Oak Rd. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/18/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 in PVC Main | Spread Lime at spill area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-10 | 2018-08-10 | Cleveland, City of (Cleveland WPCP) | White |  | Manhole at 896 Campbell Street, Cleveland | 500 |  | Raw Sewage | Mountain District - Cartersville | GA0036820 | WWTP |  |  | Equipment failure |  | Matthew Stickney | Kathy Lewis | Katie Meade | 8/13/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rupture and break on the 1 inch check release valve in manhole | Replacement of valve to stop leak. Cleaned up overflow area with lime. | 77dbdd3c-0b48-49c2-b623-a78b1b0170cf | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-15 | 1 | 0 | 0 | 0 | 0 | 0
2015-08-03 | 2015-08-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 896 Harwell Road, NW | 1590 | fax received 8/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/4/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-06 | 2015-05-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2716 Lenox Road, NE | 1470 | fax received 5/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/7/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-16 | 2018-06-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3206 Ward Dr. SW - Atlanta | 240 | Fax sent 2018-06-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/17/2018 12:00:00 AM |  | 6/16/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive NW | 2720 | fax received 11/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-14 | 2018-04-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3763 Ozmer Court Decatur GA 30034 | 1000 | manhole 15-039-s035 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/14/2018 5:23:00 PM | Ocmulgee | 4/14/2018 12:00:00 AM |  |  | 1 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown blockage | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-10 | 2016-02-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3430 Kensington Road, Decatur | 1775 | Notification received on February 12, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/10/2016 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots | The problem was corrected at 19:40 hours, when a crew set up a by-pass pump to contain the spill until the blockage is successfully clear. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-01 | 2018-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 96380000 | This spill is also entered as a violation | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream | Stream | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 8/10/2018 12:00:00 AM |  | 8/1/2018 12:00:00 AM |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | South River Major TSS Spill From midnight August 1 to midnight August 2, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. August 1 TSS - 45 mg/L August 2 TSS - 110 mg/L Permit Limit = 15 mg/L | Seeking additional landfill options for removal of excess solids. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-27 | 2015-11-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 1952 Tanglewood Drive | 3073 | fax received 11/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/17/2015 12:00:00 AM |  |  |  |  | 0 | Watson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Beam break on 10" force main | Repaired force main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-02-25 | 2015-02-26 |  | Lowndes | Valdosta | Cypress Street and Mystic Street | 48000 | Verbal and email notification received 2/26/25015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/25/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The Valdosta area received 2.85 inches of rain in 48 hours. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-10-25 | 2016-10-25 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Near East Baker Hwy between Lakeview Ave & Lupo Lane in Douglas. | 4800 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ditch | Ditch | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/25/2016 4:47:00 PM | Satilla | 10/26/2016 12:00:00 AM |  |  | 1 | un-named tributary of the Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blocked sewer line | Blocked sewer line was cleared. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-27 | 1 | 1 | 1 | 0 | 0 | 0
2016-02-15 | 2016-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 959 E. Confederate Avenue, SE | 1025 | fax received 2/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/16/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-08 | 2016-07-08 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1510 Old Waynesboro Road | 4500 | fax received 7/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/8/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Spirit Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Used jet truck to open sewer segments. Lime was put out. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-01-09 | 2015-01-09 |  | Columbia |  | 4606 Renee Street | 9000 | Fax received on 1/9/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  |  | Sarita Banjade | Sarita Banjade | 1/9/2015 12:00:00 AM |  |  |  |  | 1 | Private Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 'Roots and Grease' | 'Unstopped sewer main with jet machine, cleaned up spill area, aerated pond, took sample, posted signs. Plan follow-up video inspections' |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY WATER UTILITY | 7068636928
2016-06-18 | 2016-06-18 | Lowndes County (South Regional WPCP) | Lowndes | Valdosta | Val Tech Road | 7500 | Verbal notification received 6/20/2016 | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Collection System | Storm Drain |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/20/2016 12:00:00 AM |  |  |  |  | 1 | Drainage ditch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Split in the 16" force main | Flow was bypassed until emergency repairs could be made. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | LOWNDES COUNTY
2017-03-16 | 2017-03-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1955 La Dawn Ln. NW - ATL | 300 | Fax received 2017-03-17. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 3/17/2017 12:00:00 AM |  | 3/16/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-13 | 2015-08-13 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawrenceville | 2330 Highpoint Rd. | 7200 | Fax received on 08/14/2015. ERT notified 8/13/2015, CTS No. 77577. | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System |  |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/14/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-09-07 | 2015-09-07 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | 5400 Altama Avenue at the corner of Carl Gregory Chrysler Dodge. | 1500 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Storm Drain | Stream | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/7/2015 4:10:00 PM | Satilla | 9/7/2015 12:00:00 AM |  |  | 1 | Belle Point Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rains causing I&I to collapse manhole structure. | Vac-Con trucks recover approximately 500 gallons and equalized flow until by-pass pump was installed. A new man hole is to be installed. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-09-11 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2820 Pierce Drive S., Macon MH ID 82002 | 7280 | Phone call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was hydraulic overload due to heavy rains in the MWA service area. According to the National Weather Service, Macon-Bibb County received 5.42 inches of rain on Friday, April 1st. | Debris was removed from the area and the affected area has been disinfected with lime. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 |  | Gwinnett | Buford | 5971 Lake Windsor Pkwy | 100 | fax received 2/18/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Power failure |  |  | Kim Hembree | Kim Hembree | 2/23/2015 12:00:00 AM |  |  |  |  | 1 | Lake Lanier | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage to pump station | Shut down station until power restored |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-02-08 | 2017-02-08 | Rome, City of (Rome WRF) | Floyd |  | 480 feet south of 1929 N. Broad Street | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Tracy Feltman | 2/9/2017 12:00:00 AM | Coosa |  |  |  | 0 | Burwell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots in the sewer main | Sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-18 | 2018-05-18 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8895 London Court | 720 | Fax received on 05/18/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Paul Moisan | 5/18/2018 12:00:00 AM |  |  |  |  | 0 | Flint | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Washed down | Small discharge during maintenance activity. Lift station crew stopped event from occurring and washed down around area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-21 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-02 | 2017-10-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2164 Faulkner Rd. NE - ATL | 5 | Email received 2017-10-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/3/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Damaged bypass hose. | Crew repaired the bypass hose to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-28 | 2016-03-28 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 700 Holcolcomb Bridge Road | 2860 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/28/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Big Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root Intrusion | The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. The area impacted bythe spill has been cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-28 | 2017-02-28 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Alpharetta | 340 Red Bank Rd. - Alpharetta | 350 | Fax received 2017-02-28 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 2/28/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken pipe. | Plugged manhole upstream to stop flow for repairs, clean up lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-27 | 2018-03-27 | Fulton County (Big Creek WPCP) | Fulton | Sandy Spriings | 789 Hammond Drive Sandy Springs 30328 | 1850 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/27/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4427 wesleyan Pointe, Decatur | 317200 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/6/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 08:15 hours on April 6, 2017 when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-13 | 2018-06-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4 Adair Ave. SE - Atlanta | 25 | Fax sent 2018-06-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/14/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-07 | 2018-03-07 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 296 The Plaza | 1495 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 |  | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/8/2018 12:00:00 AM | Oconee |  |  |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | baby wipes and rags | hard-rodded line |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-11 | 2018-05-11 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 158 Paper Mill Rd. - Lawrenceville | 8086 | Fax sent 2018-05-11 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Alys Hannum | 5/11/2018 12:00:00 AM |  | 5/11/2018 12:00:00 AM |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism - Debris. | Removed all deposited solids. Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1761 Hollingsworth Blvd. NW - ATL | 5850 | Fax received 2017-02-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 2/16/2017 12:00:00 AM |  | 2/15/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-07 | 2015-09-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill Street, NW | 175 | fax received 9/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 9/7/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | The crew repaired the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-04 | 2017-04-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1680 Ralph D. Abernathy Blvd - ATL | 18200 | CTS complaint #82680 received 2017-04-04. Fax received 2017-04-04. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/4/2017 12:00:00 AM |  |  | 2017-04-04 | 2018-04-25 | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-05 | 0 | 0 | 0 | 1 | 1 | 0
2017-10-31 | 2017-10-31 | Cobb County Water System | Cobb |  | 595 Riverside Parkway | 370 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 |  | Henry | Stockbridge | 678 Fairhaven Blvd. | 76500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 678 Fairhaven Blvd. Stockbridge, GA 30281 |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-21 | 2015-07-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 637 Briar Hill Ct. | 3000 | REC FAX 7/22/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 7/22/2015 12:00:00 AM | Flint | 7/22/2015 12:00:00 AM |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Cleared Blockage. Blockage was cleared and flow returned to normal. Signs were posted. Televise: Line is scheduled to be televised to determine the cause of the blockage and make repairs if needed. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-07-27 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 770.960.5205
2018-01-08 | 2018-01-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1500 James Jackson Pkwy. NW - ATL | 32100 | Email sent 2018-01-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/9/2018 12:00:00 AM |  | 1/8/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 305 Kelso Drive, SW | 500 | fax received 12/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/23/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-14 | 2016-04-14 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 4279 Duncan Ives Drive | 141 | fax received 4/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Contractor |  |  | Kim Hembree | Kim Hembree | 4/14/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Sherwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Third party damage - Boring |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-03-11 | 2016-03-11 | Cobb County Water System | Cobb |  | 4897 Lake Fjord Pass | 340 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Mansoor Alaeddini | Reginald Williamson | Reginald Williamson | 3/11/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | This overflow occurred as a result of debris in sewer main causing the manhole to overflow into a tributary of Willeo Creek. | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-23 | 2018-02-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Scottdale | 656 Gifford Drive, Scottdale 30079 | 1660 | manhole 18-046-s151 discharging | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/24/2018 10:30:00 AM | Ocmulgee | 2/23/2018 12:00:00 AM |  |  | 1 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | roots and rags | pressure wash main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-19 | 2017-01-26 | Thomaston, City of | Upson | thomaston | 111 Monroe Street | 225 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/19/2017 12:00:00 AM | Flint |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The debris was removed. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2017-07-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3033 Continental Colony Pkwy. SW - ATL | 615 | Fax received 2017-07-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 7/13/2017 12:00:00 AM |  | 7/12/2017 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Not specified. | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-02 | 2017-08-02 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 1176 Lloyd Dr - Forest Park | 4200 | Fax received on 08/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 8/3/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was pipe failure. | Set up by-pass pumps and have tree service remove oak tree. Repair pipe at leaking joint. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-03 | 0 | 1 | 1 | 0 | 0 | 0 | Billy Vonderbush |  | CLAYTON COUNTY WATER AUTHORITY
2015-04-19 | 2015-04-19 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Manhole at Social Circle WWTP | 1100 | Verbal notification and fax received 4/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 4/20/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2018-08-07 | 2018-08-07 | Macon Water Authority (Rocky Creek WPCP) | Macon | Macon | Indian Mounds Lift Station | 9765 |  | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Lift Station | Ditch | Ditch | Equipment failure |  |  | Juan Robles | Juan Robles | 8/8/2018 12:00:00 AM |  | 8/8/2018 12:00:00 AM |  |  | 0 | Walnut Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overload due to rain and lift station failure. | MWA maintenance crews arrived on site and were able to adjust the pumps and the manhole stopped overflowing. Maintenance crews will also be implementing changes to the controls in the station to prevent issues during heavy rainfall. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-08-09 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Atlanta | 6701 Winterbrook Court | 7106 | fax received 2/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/3/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Triburtary of Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-03-23 | 2017-03-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1051 Somerset Dr. NW - ATL | 1540 | Fax received 2017-03-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/24/2017 12:00:00 AM |  | 3/23/2017 12:00:00 AM |  |  | 1 | Long Island | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-25 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2424 Grand Harbor Court, MH 69309 | 1100 | REC EMAIL 2/26/2015. Rec Corrected EMAIL 2/26/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Other | Ditch | Wet weather |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/26/2015 12:00:00 AM | Ocmulgee | 2/26/2015 12:00:00 AM |  |  | 1 | Lake Tobesofkee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was hydraulic overload due to heavy rains in the the MWA service area. Macon-Bibb County experienced a 24 hour rainfall of 1.66 inches according to the National Weather Service. | Debris will be removed and the affected area is being disinfected with lime. CORRECTIVE ACTION TAKEN TO PREVENT FUTURE SPILL: The MWA has developed a project to install a new force main at the Glen Echo Lift Station and is currently in the process of procuring easements. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-27 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2018-01-30 | 2018-01-30 | Marietta (City of)- Sewers | Cobb | Marietta | 848 Powder Springs St. | 750 | Sanitary Sewer Overflow Report is attached. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Marietta Water personnel quickly relieved the blockage thus restoring normal flow. The abandoned sewer service is to be discontinued. The source of concrete debris is unknow but contstruction site is being monitored. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-02 | 2017-06-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1073 South Indian Creek Drive, Stone Mountain | 2600 | Notification received on June 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/2/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:44 hours when the crew pressure an 8" sewer main 169ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 0 | Verbal notification received 2/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-13 | 2016-05-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1615 Johnson Road, NW | 1050 | fax received 5/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 5/14/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, grease, debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-07 | 2016-02-07 |  | Cobb |  | 3587 Candlewood Trail | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 inch clay main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-25 | 2016-03-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4350 Dogwood Farms Drive, Decatur | 2720 | Notification received on March 30, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/25/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 11:37 hours, when a crew pressure washed the 8" sewer main 250ft, clearing the blockage at 83ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-31 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-22 | 2017-05-22 | Cherokee County Water & Sewerage Authority (Fitzgerald Creek WPCP) | Cherokee |  | Manhole between Sixes Road and West Ridge Drive | 12500 | Violation being handled by EECO | Raw Sewage | Mountain District - Cartersville | GA0038555 | WWTP | Stream |  | Contractor |  | Eric Dykes | Kathy Lewis | Eric Dykes | 5/23/2017 12:00:00 AM | Coosa |  |  |  | 0 | Blankets Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor working on piping in lift station due to upgrade. Piping joint came apart disabling pumps | Pipe fixed | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-09 | 2018-01-09 | MACON WATER AUTHORITY - ROCKY CREEK WPCP | Bibb | Macon | 4606 Pine Valley Drive | 12300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/9/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 616 Mitchell Bridge Rd., Athens | 18900 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Oconee | 12/30/2015 12:00:00 AM | 2016-01-02 |  | 1 | Middle Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole overflowed during flood event | Cleaned area. Sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Govenment of Athens-Clarke County | 706-613-3481
2017-09-22 | 2017-09-22 | Dalton Utilities (Riverbend WPCP) | Whitfield |  |  | 6745 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWRF | Stream |  | Equipment failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 9/22/2017 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment malfunction with a portable pump at a Dalton Utilities Underwood lift station during scheduled maintenance at the lift station | Cleanup near the site of the spill is ongoing, but flow to Mill Creek has stopped | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2353 Burroughs Avenue, SE | 66 | The crew used a hydraulic pressure cleaner to contain the spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/16/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-06 | 2015-02-06 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1455 Pleasant Grove Dr. | 1586 |  | Raw Sewage | Mountain District - Cartersville | GA02-056 | WWRF | Stream |  | Contractor |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/9/2015 12:00:00 AM | Coosa |  |  |  | 0 | Logan Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor Damage |  | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-02-11 | 0 | 0 | 0 | 0 | 0 | 0 | Lori McDaniel | 706-529-1032 | Dalton Utiliies
2017-10-21 | 2017-10-21 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1071 Laurel Lane | 480 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/21/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Travers Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ragging and Debris | Removed ragging and debris | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-18 | 2015-11-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Road, NE | 436 | fax received 11-19-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 11/19/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-08 | 2018-05-08 | Cobb County Water System | Cobb | Marietta | 2050 Austell Rd | 2800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Olley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The crew stopped the overflow at 6:20 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-27 | 2016-10-27 | Cobb County Water System | Cobb |  | 2087 Fairport Way | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/27/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-29 | 2016-11-29 |  | DeKalb | Ellenwood | 4280 Newcomb Road, Ellenwood | 1500 | Notification received on December 1, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/29/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole damage | The problem was corrected at 10:40 hours, whena acrew reset hte manhole riser, resealed the joint one the riser with hydraulic cement and stopped the leak. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-02 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-13 | 2018-04-13 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3218 Milledgeville Rd. - Augusta | 650 | Fax sent 2018-04-16 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Roots |  |  | Alys Hannum | Alys Hannum | 4/16/2018 12:00:00 AM |  |  |  |  | 1 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mainline was blocked with roots. | Sawed line 85 ft to open. Flushed and vacuumed storm drain. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-26 | 2015-07-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2364 Lilla Circle, SW | 500 | fax recieved 7/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/26/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-24 | 2016-02-24 | Tifton, City of (New River WPCP) | Tift | Tifton | 181 Brookfield Road, Tifton | 6500 | Telephone call received on 02/24/2016; report received on 02/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/24/2016 12:00:00 AM |  |  |  |  | 1 | New River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | Mitigated by hydrated lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-03 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-18 |  |  | DeKalb |  | 2041 Bramblewood Drive | 15 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-09 | 2017-02-09 |  | Terrell | Dawson | Hwy 82 | 48960 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Brantley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall 7 inches in less than 24 hours on already saturated ground | Area will be clened and limed if necessary. Creek monitoring. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Lift Station at Treatment Plant | 500 | The overflow was primarily waste water fluids with little to no solids; sanitary sewer overflow was onto the vegetated ground and did leave the property and did not enter State waters. | Raw Sewage | Northeast District - Augusta | GA0020893 | Lift Station |  |  | Power failure |  | Delaine Scott | Delaine Scott | Delaine Scott | 10/10/2016 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage occurred at treatment plant from approximately 0600 to 0820 on Oct. 8, 2016 due to storms associated with Hurricane Matthew. The battery in the back up generator located at the treatment plant were inoperable on Oct. 8th resulting in no power at the treatment plant lift station or to power aerators within the treatment plant lagoon. | Reset pump at lift station and returned to service as soon as power was restored after 0820 on Oct. 8, 2016. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-10-12 | 1 | 0 | 0 | 0 | 0 | 0
2017-02-04 | 2017-02-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3714 Casey's Cove, Ellenwood | 6420 | Notification received on February 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/4/2017 12:00:00 AM |  |  |  |  | 0 | Blue Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:19 hours when the crew pressure washed the 8" sewer main 200ft upstream, cleared the grease blockage at 171ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Cobb County MS4 | Cobb |  | 1795 Martin Place | 2900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Buildup in Manhole | Limed Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 4385000 | Verbal notification received 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain event |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-25 | 2018-05-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4340 Tree Haven Dr. NE - Atlanta | 100 | Fax sent 2018-05-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/29/2018 12:00:00 AM |  | 5/25/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-06 | 2015-01-06 | Marietta (City of)- Sewers | Cobb | Marietta | 582 Etowah Dr. | 1200 | Manhole in sidewalk/street in front of property | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/6/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the sewer main caused sewage to escape into nearby storm drain and Creek. | Marietta Water personnel quickly relieved the blockage thus restoring normal service. The street was washed down and deodorized. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-06 | 2015-01-06 | Marietta (City of)- Sewers | Cobb | Marietta | 582 Etowah Dr. | 1200 | Manhole in sidewalk/street in front of property | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/6/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the sewer main caused sewage to escape into nearby storm drain and Creek. | Marietta Water personnel quickly relieved the blockage thus restoring normal service. The street was washed down and deodorized. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-31 | 2015-01-31 | Cobb County MS4 | Cobb |  | 866 Chestnut Lake Drive | 460 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/31/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The crew was able to stop the overflow at 5:50 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-08 | 2017-12-08 | Norman Park (Norman Park WPCP) | Colquitt | Norman Park | Outfall into Reedy Creek. | 0 | All public notice received. | Treated Effluent | Southwest District | GA0033600 | WWTP | Stream | Stream | Other |  | Jay Howell | Jenna Detar | Jenna Detar | 12/8/2017 10:00:00 AM | Suwannee | 12/12/2017 12:00:00 AM | 2017-12-08 |  | 1 | Reedy Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Rising sludge in the clarifier and exiting the plant into the creek. | Improved sludge wasting schedule with assistance from GRWA. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2018-04-10 | 1 | 1 | 1 | 1 | 0 | 0 | Bruce Norton |  | City Norman Park | [8 empty] | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 796 Wesley Drive, NW | 17250 | fax received 12/24/2015. CTS No. 78623 Volume originally entered as 32,100 gal. Volume on final SMP = 17,250 gal. Changed 2017-04-04. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  | 2015-12-24 | 2017-01-13 | 1 | Peachtree Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-08 | 2016-09-08 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit =12, reported = 65.1 TSS, weekly average concentration (mg/L): permit =30, reported = 100 Flow was 0.617 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 10/3/2016 12:00:00 AM | Ogeechee |  |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Immaturity of pretreatment pond at Coastal Processing caused high BOD/TSS loadings to the WPCP | Coastal Processing installed a DAF unit, bypassing pond to allow it to biologically mature |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-625-3166 |  | 65.1 | 100
2017-02-03 | 2017-02-03 |  | Baldwin | Milledgeville | 711 N. Wilkinson Street | 525 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2017 12:00:00 AM | Oconee |  |  |  | 0 | Oliver Hardy Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage spill occurred due to grease in the sewer line. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-02 | 2016-03-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1422 Brookvalley Lane, Atlanta | 4500 | Notification received on March 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/3/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, roots and debris | The problem was corrected at 17:15 hours, when a crew pressure washed the sewer main 600ft, cleared the blockage at 300ft, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-02 | 2018-05-02 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Southeast WPCP | 100000 | EPD contacted DNR Fisheries to investigate the incident. Fisheries submitted a fish kill report indicating that 35 fish had been kill by a slug of chlorinated water released from the WWTP outfall. Public notice not issued nor was major spill sampling conducted as chlorine detoxifies quickly and does not pose a threat to the public. | Chlorinated Effluent | Coastal District | GA0024431 | WWTP | Ditch |  | Operator error |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 5/2/2018 1:00:00 PM | Satilla |  |  |  | 1 | Unnamed | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Operator error resulted in an excessive amount of sodium hypochlorite (50 lbs.) being discharged from the WWTP outfall causing a fish kill. The operator reported 7 dead fish. | A written standard operating procedure has been developed to prevent future releases of chlorine at the WWTP outfall. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-06-06 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Cochran WPCP | Bleckley | Cochran | Several manholes from Ann St. to Peter Street | 15000 | Telephone call received on 02/03/2016, and email received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0032107 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/3/2016 12:00:00 AM | 2016-02-04 |  | 1 | Jordon Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Flash flood rain event coupled with high ground water entered through I/I. | Signs are posted and will be posted until 02/14/2016. Any solids were removed and the area was disinfected with lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-09 | 2016-01-07 | Cobb County MS4 | Cobb |  | 4175 Nance Road | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake AcWorth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Lake Acworth. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-04 | 2015-03-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2964 Ridge Valley Road, NW | 630 | fax recieved 3/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/5/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-13 | 2016-09-13 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 42 Flow was 0.512 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 10/3/2016 12:00:00 AM | Ogeechee |  |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Immaturity of pretreatment pond at Coastal Processing caused high BOD/TSS loadings to the WPCP | Coastal Processing installed a DAF unit, bypassing pond to allow it to biologically mature |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-625-3166 |  | 42
2015-07-24 | 2015-07-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1370 Howell Mill Road, NW | 5 | fax received 7/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-25 | 2015-12-25 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Park Place Lift Station | 17100 | CTS No. 78634 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/26/2015 12:00:00 AM |  |  |  |  | 1 | Little Haynes Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2015-12-30 | 2015-12-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 80 | email received 12/31/2015; fax received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-04 | 2016-04-04 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1805 Slade Drive, Columbus | 950 | Fax received on 04/05/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 4/5/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. | Once the debris was cleared from the main the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-11 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-29 | 2017-03-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 629 Wynbrooke Parkway, Stone Mountain | 3620 | Notification received on March 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/29/2017 12:00:00 AM |  |  |  |  | 0 | Stone Mountain Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 15:33 hours when a crew pressure washed between manholes 120ft, cleared the blockage at 80ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | Tifton, City of (New River WPCP) | Tift | Tifton | Old Ocilla Road | 1500 | REC CALL 2/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Ditch | Debris |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/27/2015 12:00:00 AM | Suwannee | 2/27/2015 12:00:00 AM |  |  | 1 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in pipe | Clear bloackage | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Scott Murphy |  | ESG Operations, Inc. |  | CITY OF TIFTON | 229-391-3937
2015-12-10 | 2015-12-10 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Valley Circle | 1500 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Rags |  |  | Dagny Pariani | Dagny Pariani | 12/11/2015 12:00:00 AM | Oconee | 12/10/2015 12:00:00 AM |  |  | 1 | Tobler Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | sewer line blockage caused by grease and rags | Rodded the 8" sewer line to remove rags. Applied lime to the site. Continuing to monitor. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-11 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2015-12-31 | 2016-01-02 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Central City Park parking lot next to ball fields, Willie Smokey Glover Road, Macon MH #57743 | 460480 | Fax and email received on 01/04/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/4/2016 12:00:00 AM | Upper Ocmulgee | 1/2/2016 12:00:00 AM | 2015-12-31 | 2016-11-28 | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was hydraulic overload. The service area received 12.62 inches of rain for the month of December 2015, and is now the wettest on record for Macon-Bibb. | This manhole is located in a parking lot. The area was washed down, and debris was removed. The MWA will continue its search for inflow and infiltration (I/I) into its sewer system through its CCTV and flow monitoring investigations. The MWA also has projects planned to rehabilitate two large sewer interceptors that feed the Lower Poplar Treatment plant. These projects will help to reduce the I/I into the MWA sewer system. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-05 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2400 Block of Gornto Road | 55800 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Withlacoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-08-20 | 2015-08-20 |  | Henry |  | East of McDonough at the Henry County Water and Sewerage Authority | 57000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 8/20/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lightning damage to the main influent pump station to the Walnut Creek Water Reclamation facility was determined to be the cause. | The site was cleaned, limed and posted with appropriate notification signs. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-16 | 2016-10-16 | Cobb County Water System | Cobb | Marietta | 5000 South Lincoln Trace | 590 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/17/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8 inch Clay main | Spill stopped at 11:20 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-24 | 2015-04-25 |  | DeKalb | Chamblee | 2710 Dresden Drive, Chamblee | 4590 | Notification received on April 28, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/25/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 14:27 hours when a crew pressure washed the 10" sewer main upstream 300ft, cleared the grease blockage, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-13 | 2016-07-13 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 3710 Menloe Way | 5425 | fax received 7/13/2013 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/13/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Jacks Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-03-28 | 2018-03-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 970 Joseph E. Lowery Blvd. NW - ATL | 3075 | Due to the ransomware attack on City of Atlanta, reports are being handwritten. Some information may be missing or hard to read. Fax sent 2018-03-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/28/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Impact State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew installed a by=pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-30 | 2017-04-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2301 Mountain Industrial Boulevard, Tucker | 500 | Notification received on May 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/30/2017 12:00:00 AM |  |  |  |  | 0 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station power failure | The problem was corrected at 15:00 hours when an operator reset the lift station and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-22 | 2017-08-22 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 5885 Glenridge Drive Sandy Springs, GA 30328 | 15290 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/22/2017 12:00:00 AM | Altamaha |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-07 | 2018-05-07 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 213 Cannon Drive - Social Circle | 200 | Email sent 2018-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Roots |  |  | Alys Hannum | Alys Hannum | 5/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root blockage in the sewer main. | Root destroyer applied to sewer line. Signs posted. Lime applied. Public agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-04 | 2018-09-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 2240 Coronado Place Chamblee GA 30341 | 200 | sewer coming out of the bank of the creek | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/5/2018 5:52:00 PM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris of rocks, and tissue. | Pressurewashed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-31 | 2016-12-31 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Harold Rd. @ Coleman Avenue - Augusta | 200 | Fax received 2017-01-01 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 2/1/2017 12:00:00 AM |  |  |  |  | 0 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Line was opened and resumed normal flow. Storm ditch flushed and vacuumed. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-26 | 2016-04-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2226 Gary Court, NW | 1480 | fax received 4/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/27/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-27 | 2015-03-27 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Holly Avenue & Robarts Road (Fairview Trailer Park), Brunswick | 2500 | Spill originated from a private lateral. | Raw Sewage | Coastal District | GA0025313 | Collection System | Ditch | Ditch | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/27/2015 4:00:00 PM | Satilla | 3/27/2015 12:00:00 AM | 2015-03-27 | 2015-03-28 | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Break on a private service lateral. | Lateral repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-04-02 | 1 | 1 | 0 | 0 | 0 | 0
2016-07-15 | 2016-07-15 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 420 West Tyler Street | 1200 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWRF | Stream |  | Debris |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 7/16/2016 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown debris blockage in the sewer main | The blockage was cleared using a high pressure jet. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-23 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2495 Glenbrook Drive, Clumbus | 6577 | Fax sent 5/23/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Paul Moisan | 5/23/2018 12:00:00 AM |  |  |  |  | 0 | Lindsay Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rains | Once the rain subsided and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-16 | 2018-03-16 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Swainsboro WWTP | 23437 | This is an unpermitted discharge, also entered as a violation. Updates are uploaded here. Notification call received 2018-03-16 | Primary Effuent |  | GA0039225 | WWTP | Stream |  | Pipe failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 3/16/2018 12:00:00 AM |  |  |  |  | 1 | Yam Grandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | At 9:45 AM on March 16, effluent discharge line ruptured. Approximately 23,437 gallons of fully treated effluent entered Yam Grandy Creek at a point other than the permitted discharge location, approximately 3.5 miles downstream. | Flow was diverted to the storage pond; repairs completed and flow restored at 10:15 PM. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-01 | 2017-03-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3254 Ward Dr. SE - ATL | 9360 | Fax received 2017-03-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Paul Moisan | 3/2/2017 12:00:00 AM |  | 3/1/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause of the spill is unknown at this time. | Crew set up a by-pass pump to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-21 | 2017-11-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 5342 Peachtree Road Chamblee GA 30341 | 100 | Found evidence of spill, but was not spilling at the time of arrival. Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/22/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Nancy Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sewer main | repaired 8" sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Robert Osburn |  | Dekalb County Department of Watershed Management
2016-10-09 | 2016-10-09 | Savannah, City of (President Street WRF) | Chatham | Savannah | Lift Station #8 - Magnolia Park | 1170 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Storm Drain, Stream | Canal | Natural Disaster |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM | Savannah | 10/9/2016 12:00:00 AM |  |  | 1 | Casey Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage during Hurricane Matthew. Lift station with no generator resulted in manhole overflow. | Brought in portable generator to restore LS power. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-09 | 2016-05-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 939 Epps Bridge Parkway, Athens | 8638 | Initial email 5/10, full report faxed 5/11 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Pipe failure |  |  | Dagny Pariani | Dagny Pariani | 5/10/2016 12:00:00 AM | Oconee | 5/9/2016 12:00:00 AM |  |  | 1 | McNutt Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Section of pipe was damaged due to stream bank erosion | Installed pump diversion until the damaged pipe can be replaced |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | verbal notification from Kris Garcia received 11/02/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a TSS and BOD major outfall spill. The sand filters were bypassed due to hydraulic overload. TSS Permit Limit = 25 mg/L; TSS Reported Value = 405 mg/L. BOD Permit Limit = 25 mg/L; BOD Reported Value = 45 mg/L. Total volume during outfall spill = 116.35 million gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-29 | 2017-03-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4392 Stonington Circle, Dunwoody | 2640 | Notification received on March 31, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Rags |  |  | Hsin Yeh | Hsin Yeh | 3/29/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags blockage | The problem was corrected at 16:56 hours when a crew pressure washed between manholes 410ft, cleared the blockage at 408ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-25 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 5933 Peachtree Industrial Blvd. - Norcross | 7201 | Fax received 2017-04-25 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/26/2017 12:00:00 AM |  | 4/25/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Rocks or Construction Material | Placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-31 | 2017-05-31 | Cobb County Water System | Cobb |  | 2610 Due West Cir | 320 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8" Clay Main | Stopped spill at 1906. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Dalton Utilities (Whitfield Mountain View Acres WPCP) | Whitfield |  | 420 Cattleman Drive | 350 |  | Raw Sewage | Mountain District - Cartersville | GA0047848 | WWTP | Stream |  | Debris |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 5/24/2016 12:00:00 AM | Coosa |  |  |  | 0 | Stone Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris Blockage | The blockage was cleared using a high pressure jet. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-05-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-10 | 2017-10-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1386 Hanover West Dr. NW - ATL | 3 | Fax sent 2017-10-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 10/11/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-12 | 2015-10-12 | Cobb County (Noonday Creek WPCP) | Cobb |  | 102 Ridge Ct. | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 12" Clay Main | Spread Lime at Spill Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-09 | Glennville, City of (Glennville WPCP) | Tattnall | Glennville | The spill occurred at three different lift stations; Continental, Lakeview, and Camelot. These stations were the first to received back up power provided by emergency generators. | 5000 | The affected area included Spring Branch Tributary which is a wet land system that discharges into Beards Creek. | Raw Sewage | Coastal District | GA0037982 | Lift Station | Ground, Stream | N/A | Power failure |  | Hailey Harden | Hailey Harden | Hailey Harden | 10/10/2016 12:00:00 AM | Unknown |  |  |  | 1 | Spring Branch Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to Hurricane Matthew, the City of Glennville experienced high winds of 41-71MPH. This caused trees to fall and cause devastating power outages. In addition, the city received 7.5 inches of rainfall. | the affected area was treated with chlorine and lime to mitigate or reduce the adverse effects of the spill. | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-10-26 | 0 | 0 | 0 | 0 | 0 | 0 | Stan Dansby | 912-654-2476 | City of Glennville
2016-02-25 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 456 | fax received 2/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/26/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-19 | 2016-12-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 5470 Riverdale Road, Riverdale Manhole: 2198472 | 1600 | Fax received on 12/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Vandalism |  |  | Paul Moisan | Paul Moisan | 12/20/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris was in the line from upstream vandalized manhole (2198472) structure. Crews found this problem while conducting downstream inspections as follow up to vandalized manhole repair. | Crews cleared the blockage and flow returned to normal. Manhole upstream of the problem area has been repaired and a bolt down lid installed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-21 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2015-10-03 | 2015-10-03 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Lift Station No. 12 at Hwy. 80 | 1800 | verbal notification received 11/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Lake Luck | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and hydraulic overload | debris cleared | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO
2018-01-21 | 2018-01-21 | Marietta (City of)- Sewers | Cobb | Marietta | 582 Etowah Dr. | 8400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-16 | 2015-02-16 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 144 Moreland Avenue, NE | 2104 | fax received 2/17/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/17/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-08 | 2016-05-08 | Columbus Water Works (South WRF) | Muscogee | Columbus | Building 3105, Leanard Drive, Ft. Benning, Columbus | 584 | Telephone call received on 05/09/2016; fax received on 05/09/2016; email received on 05/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 5/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Opossum Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. | Once debris was cleared from the main the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-04 | 2016-04-04 | Broxton | Coffee | Broxton | West Avenue North | 200 |  | Raw Sewage | Coastal District | GAJ020124 | Pump Station | Ditch | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/20/2016 12:00:00 AM | Satilla | 4/6/2016 12:00:00 AM |  |  | 1 | Unnamed Tributary | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station pump failure. | Pump was repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-04-20 | 1 | 1 | 0 | 0 | 0 | 0
2015-03-15 | 2015-03-15 |  | Gwinnett | Lawrenceville | 870 Cramac Drive | 4800 | fax received 3/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 3/15/2015 12:00:00 AM |  |  |  |  | 1 | Redland Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Flushed the main and restored flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-16 | 2015-01-16 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 |  | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is day two of a major outfall spill. Reported TSS = 37 mg/L. Volume = 68,800,000 |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-07 | 2015-10-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 618 Flamingo Drive, SW | 700 | fax received 10/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-19 | 2018-04-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 601 McDonough Blvd. SE - Atlanta | 2428 | Fax sent 2018-04-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/20/2018 12:00:00 AM |  | 4/19/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1829 Campbellton Road, SW | 1740 | fax received 8/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-12 | 2015-01-12 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Chapel Hill Farms Lift Station, Chapel Hill Farms Court | 9400 | REC CALL 1/13/2015. REC FAX 1/15/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Lift Station | Stream | Stream | Power failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/13/2015 12:00:00 AM | Chattahoochee | 1/13/2015 12:00:00 AM |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical power loss due to failure of a conductor in the power grid sering the area caused power loss to a large section of the county. | Crews discovered spill situation after being notified by SCADA of a power loss in the area and being dispatched to check sites that might be affected. Crews cleaned and disinfected area around the lift station where the spill occurred. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-20 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Douglasville Douglas County Water and Sewer Authority (DDCWSA) | 770.949.7617
2015-09-21 | 2015-09-21 | BASF Corporation (McIntyre) | Wilkinson | McIntyre |  | 4800 | Upstream: pH - 6.2 Turbidity - 15 NTU Downstream: pH - 6.0 Turbidity - 600 NTU | Primary Effuent | Northeast District - Augusta | GA0003131 | N/A | Stream | N/A | Pipe failure |  | Jill Causse | Shea Buettner | Shea Buettner | 9/22/2015 2:00:00 PM | Oconee |  |  |  | 1 | Nelson Branch and Little Commissioner Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 |  |  | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | ec78723e-818a-41f7-abda-40a99625de6f | ec78723e-818a-41f7-abda-40a99625de6f | 2015-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Kolb | 478-946-7593 | BASF
2015-12-29 | 2015-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 777 Valley Brook road, Decatur | 1432 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  |  | Hsin Yeh | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 14:32 hours, when a crew pressure washed sewer main 60' upstream, installed a bypass pump, called in an emergency repair request and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b |  | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | MLK LIft Station | 25000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/14/2016 12:00:00 AM | Suwannee |  |  |  | 0 | Ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | THe backup pump at the lift station had a seal failure and the one pump in the lift station was unable to handle the flow. | A replacement pump was ordered. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-11 | 2018-08-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 771 Lindbergh Dr. NE - Atlanta | 15 | Fax sent 2018-08-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/12/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-24 | 2016-07-24 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 3434 Pinemont Dr, Douglasville Manhole #9683 | 24000 | Fax received on 07/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 7/25/2016 12:00:00 AM | Chattahoochee | 7/25/2016 12:00:00 AM | 2016-07-24 | 2017-08-14 | 1 | Anneewakee Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Clogged line going into well | Mechanics and VacCon crews dispatched to the site and cleared the blockage to stop the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-28 | 0 | 1 | 0 | 1 | 1 | 0 | Lyndsey Sargent | 770-949-2016 | Douglasville Douglas County Water and Sewer Authority (DDCWSA)
2017-01-22 | 2017-01-22 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 13102 Largo Ave., Savannah, GA | 1485 | Initial notification call on 1/23, final report emailed 1/23 | Raw Sewage | Coastal District | GA0020443 | Collection System | Canal | Canal | Wet weather |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 1/23/2017 12:00:00 AM | Savannah |  |  |  | 1 | Coffee Bluff Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather and heavy flows at 3 area lift stations contributed to a manhole overflow | Utilized 3 vac trucks to remove the overflow, reduced pump speed at the 3 area lift stations to slow flow | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-658-6973
2016-02-04 | 2016-02-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 1397 Witham Drive, Dunwoody | 20100 | Notification received on February 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/4/2016 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 17:10 hours, then a crew installed thirty (30) feet of 8" PVC pipe to repair the sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-09 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 4004 Summit Blvd, Brookhaven | 1320 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/29/2015 12:00:00 AM |  |  |  |  | 0 | Perimeter Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:10 hours, when a crew rodded the 8" sewer main upstream 80ft, clearing the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-14 | 2017-01-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall St SE - ATL | 415 | Fax received on 01/15/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/15/2017 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-03-03 | 2015-03-03 | Cobb County MS4 | Cobb |  | 3843 spring Meadow Dr. | 120 |  | Raw Sewage | Wastewater Regulatory Program |  |  | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/3/2015 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Gravel in 8" Ductile Iron Main | cleaned and Limed area | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-01 | 2017-05-01 | Cobb County MS4 | Cobb |  | 1012 Veterans Memorial Hwy | 2450 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-01 | 2017-05-01 | Cobb County MS4 | Cobb |  | 1012 Veterans Memorial Hwy | 2450 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-11 | 2017-01-11 | Cobb County MS4 | Cobb |  | 3185 Brookview Road | 5700 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/18/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rotten Wood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | debris and grease | The crew stopped the overflow at 10:40 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-16 | 2016-02-16 | Fulton County MS4 | Fulton | Roswell | 220 Bunratty Court | 15000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/16/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vabdalism | Remove debris, video inspect and secure ring and covers. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Marietta (City of)- Sewers | Cobb | Marietta | 767 Smithstone Rd. | 1750 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A partial blockage of suspected roots and grease caused sewage to escape a manhole into a nearby creek. | Marietta Water personnel quickly relieved the blockage by hydrojetting the sewer main ths restoring normal service. This line is currently on a replacement list. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-20 | 2016-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 236 Farrington Avenue, SE | 20 | fax received 1/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 1/21/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1794 Alvarado Ter SW - ATL | 1200 | Fax received on 01/22/2017 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  |  | Paul Moisan | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The process to clean and disinfect the site was initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2016-12-14 | 2016-12-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4141 Snapfinger Woods Drive, Decatur | 1350 | Notification received on December 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/14/2016 12:00:00 AM |  |  |  |  | 0 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | The problem was corrected at 15:42 hours, when a crew pressure washed the 8" sewer main 180ft, clearing the grease blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-19 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-12 | 2015-10-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 15 | fax received 10/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 10/13/2015 12:00:00 AM |  |  |  |  | 0 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | The crew made a repair to the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-25 | 2016-01-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 5365 Dividend Drive, Decatur | 1800 | Notification received on January 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/25/2016 12:00:00 AM |  |  |  |  | 0 | Panthers Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:18 hours, when a crew rodded and pressured washed the 8" sewer main 362ft clearing the blockage at 300ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-29 | 2017-06-30 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Chandler Haulk Lift Station Manhole M2 - Loganville | 3600 | Letter received 2017-07-11 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Ground |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/11/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overloading | Cleaned debris from the area, placed lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-14 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-24 | 2016-08-24 | Richmond Hill, City of (Sterling Creek WRF) | Bryan |  | Lift Station #44 located in the Creekside Subdivision. | 200 | The facility could not confirm any raw sewage reached the nearby storm water ditch but opted to follow the Minor Spill provisions in the permit. | Raw Sewage | Coastal District | GA0037648 | Lift Station | Ditch | Ditch | Pipe failure |  | Cliff Swiger | Cliff Swiger | Cliff Swiger | 8/25/2016 8:30:00 AM | Ogeechee | 8/24/2016 12:00:00 AM |  |  | 0 | Sterling Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station was staged with a 6 inch by-pass pump as both permanent submersible pumps were being repaired. An approximate 3/4 inch tear in the bypass-pump line developed allowing raw sewage to spray around the lift station area. | Replaced 6 inch line. | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-08-26 | 1 | 0 | 0 | 0 | 0 | 0
2016-05-19 | 2016-05-19 | Augusta, City of (Spirit Creek WPCP) | Richmond | Augusta | Spirit Creek WWTP | 0 | Verbal notification received 5/19/2016 | Treated Effluent | Wastewater Regulatory Program | GA0047147 | WWTP | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/19/2016 12:00:00 AM |  |  |  |  | 1 | Spirit Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is an major outfall spill due to a TSS violation. TSS Permit Limit = 50 mg/L; TSS Reported Value = 80 mg/L. Total volume = 1,250,000 gallons. The Spirit Creek WWTP was offline for approximately one month. During that time algae developed in the final basin prior to discharge. Due to recent wet weather events, flow was diverted to and discharged from the Spirit Creek WWTP, flushing the buildup of algae into the final discharge. | The discharge from Spirit Creek was stopped. Stream monitoring started. Evaluating options for preventing algae from entering the plant effluent. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-04-06 | 2017-04-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1073 Neal Pl. NW - ATL | 3100 | Fax received 2017-04-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/7/2017 12:00:00 AM |  | 4/6/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-19 | 2015-05-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8139 Attleboro Dr | 1350 | REC FAX 5/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/19/2015 12:00:00 AM | Flint | 5/19/2015 12:00:00 AM |  |  | 1 | Kendrick Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease | Cleared Blockage. Blockage was cleared and flow returned to normal. site was cleaned and work orders generated for additional work to determine cause. Follow-up: Televise. Lines will be televised and root cut and if problem is located it will be repaired | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-21 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1854 Shadydale Avenue, SE | 5820 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive Rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 633-780 Wesley Drive | 3256409 | Verbal notification received 11/02/2015. Total volume has not been determined. 5/11/2017 Note: Spill Volume entered as 325,650 gallons. Final Stream Monitoring Report received December 2016, lists final spill volume as 3,256,409. Spill volume has been updated accordingly. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM |  |  | 2015-11-12 | 2016-11-22 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-22 | 2018-05-22 | Newton County (Yellow River WPCP) | Newton | Covington | Alcovy River - US Hwy 278 & Elks Club Road | 3300 | Email received 2018-05-23 | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream | Stream | 3rd party contractor |  |  | Alys Hannum | Alys Hannum | 5/23/2018 12:00:00 AM |  | 5/23/2018 12:00:00 AM |  |  | 1 | Alcovy River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction crew accidentally punctured pipeline. | NCWSA shut down the pipeline until repair could be made. Caution signs with spill information will be placed downstream in areas of public access. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-04 | 2015-06-04 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 7/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 35.4 mg/L on 06/04/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-04 | 2017-10-04 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3535 Williamson Road, Macon MH ID 51563 | 480 | Fax received on 10/06/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 10/6/2017 12:00:00 AM | Ocmulgee | 10/4/2017 12:00:00 AM |  |  | 1 | Lower Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of the spill was grease. | Debris was removed and the area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Tifton, City of (New River WPCP) | Tift | Tifton | Agrirama, Tifton 31.468429, -83.534252 | 12600 | Email received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Reservoir | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM |  |  | 2016-04-04 | 2017-04-24 | 1 | Agrirama Lake | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rainfall event on April 1-2, 2016 |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 1 | 1 | 0
2015-10-28 | 2015-10-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 1050 | fax received 10/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 10/28/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-14 | 2015-07-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall Street, SE | 1500 | fax received 7/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/15/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | the crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-20 | 2015-11-20 | Paulding County (Coppermine Road WPCP) | Paulding |  | Smith Road | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 11/23/2015 12:00:00 AM | Coosa |  |  |  | 0 | Powder Springs Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station out of commision | Repair station, replaced safety relay that had station down | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey | 770-655-8342 | PAULDING COUNTY - COPPERMINE WRF
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2783 Skyland Drive, Brookhaven | 3200 | Notification received on December 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 12:20 hours, when the rain receded and the manhole returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-29 | 2017-11-29 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Lovejoy | 10690 Day Lily Drive, Lovejoy Manhole - 2203973 | 4500 | Fax received on 11/30/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/30/2017 12:00:00 AM | Flint |  |  |  | 1 | Hurricane Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-30 | 0 | 1 | 1 | 0 | 0 | 0
2015-06-10 | 2015-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1671 James Jackson Parkway, NW | 366 | fax received 6-11-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/11/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-13 | 2016-10-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2210 Holly Hill Drive, Decatur | 2400 | Notification received on October 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 10/13/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | blockage | The problem was corrected at 09:57 hours, when a crew pressure washed the sewer main 315ft, removed the blockage at 293ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-30 | 2015-06-30 |  | Clarke | Athens | 120 Tremont CT | 788 | Lime was applied and the clean up has been completed. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/30/2015 12:00:00 AM | Oconee | 6/30/2015 12:00:00 AM |  |  | 1 | Middle Oconee | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper and Rags Clogged Pipe | Rod Sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-08 | 2018-01-08 | Fulton County (Big Creek WPCP) | Fulton |  | 410 Roswell Hills Place | 2060 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Willeo Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The manhole has been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-17 | 2016-05-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 251 Swan Drive, SE | 289 | fax received 5/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/18/2016 12:00:00 AM |  |  |  |  | 0 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Breach in the mainline | The crew made a point repair to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-02 | 2016-10-02 |  | Cobb |  | 2216 Wakita Dr. | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-19 | 2017-10-19 | Cobb County Water System | Cobb |  | 225 Fontaibe Rd. | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural failure, tree fell on and broke 8" Clay main. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2000 Block of Meadowbrook Drive | 33900 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-11-10 | 2015-11-10 | Columbia County (Crawford Creek WPCP) | Columbia | Evans | 4600 Blanchard Woods Drive | 9000 | fax received 11/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Euchee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2017-03-31 | 2017-03-31 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 4664 Flat Bridge Road, Lithonia | 62150 | Notification received on April 4, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 3/31/2017 12:00:00 AM |  |  |  |  | 1 | South River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Pole Bridge Wastewater Treatment Plant lost power due to the weather which caused a manhole on a 36" sewer main to overflow into the waterway. | The problem was corrected at 09:58 hours when the power was restored and stopped the overflow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-11 | 2016-05-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1615 Johnson Road, NW | 1765 | fax received 5/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/12/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-10 | 2015-07-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1021 Harwell Road, NW | 500 | fax received 7/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/10/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-27 | 2016-01-27 | Cobb County MS4 | Cobb |  | 3812 BerryBridge Way | 30 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/27/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Solids in 8 " Cast Iron | Limed area and stopped flow | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-12 | 2015-05-12 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 400 Patrick Henry Court | 14850 | REC EMAIL 5/13/2015. REC FAX 5/13/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/13/2015 12:00:00 AM | Flint | 5/12/2015 12:00:00 AM | 2015-05-13 | 2016-05-03 | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Roots and Grease | Pumped Out. Blockage required bypass pumping to stop overflow and remove blockage. Line will be televised and any problems will be corrected. Stream sampling will be conducted by the Authority's lab per the requirements of a major spill. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-14 | 0 | 1 | 1 | 1 | 1 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 770-960-5205
2016-03-06 | 2016-03-06 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 4620 Thermal Ct., Douglasville, GA 30135 WSA Manhole 3056 | 8400 | Fax received on 03/07/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/7/2016 12:00:00 AM |  |  |  |  | 1 | Chapel Farms Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in line. | Crews cleaned and disinfected the area around the manhole where the spill occurred. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-10 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-16 | 2017-06-16 | Cobb County Water System | Cobb |  | 2828 Hicks Rd | 310 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 6/16/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-26 | 2018-03-26 | Summerville, City of (Summerville WPCP) | Chattooga |  | West of 470 Red Oak Rd approximately 50 feet off o the right of way on the Industrial Park sewer line | 24000 |  | Raw Sewage | Mountain District - Cartersville | GA0025704 | WWTP | Stream |  | Debris |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 3/28/2018 12:00:00 AM | Coosa |  |  |  | 0 | Chattooga River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Obstruction in sewer line | Sewer crews came out and jetted the line until the obstruction broke free and removed | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-20 | 2015-04-20 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 29.2 mg/L on 04/20/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4510 Mercer Road, Stone Mountain | 4720 | Notification received on January 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/18/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 23:08 hours when the crew pressure washed 100 ft upstream, cleared the grease blockage at 75 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-25 | 2015-11-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1619 High Meadow Court, Stone Mountain | 8760 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/25/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek Tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing Leaking | The problem was corrected at 15:39 hours when the crew built a berm to contain the spill while repairs were made. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-16 | 2017-03-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 4312 Webb Road, Tucker | 4600 | Notification received on March 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/16/2017 12:00:00 AM |  |  |  |  | 0 | Lucky Shoals Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:32 hours when a crew pressure washed the sewer main 180ft, cleared the blockage and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-02 | 2016-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 90 | fax received 8/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-04 | 2016-06-04 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 2525 Atlanta Highway, Athens | 0 | Unknown amount of sewage spilled to dry land. Report received with monthly report on dry land overflows 7/1 | Raw Sewage | Wastewater Regulatory Program | GA0021725 |  | Ground |  |  |  |  | Dagny Pariani | Dagny Pariani | 7/1/2016 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3495
2016-01-15 | 2016-01-15 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5711 Jonesboro Road, Morrow Manhole # 2198706 | 3850 | Fax received on 01/16/2016. | Raw Sewage |  | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/16/2016 12:00:00 AM | Flint |  |  |  | 1 | East Jester's Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. Area was cleaned and work orders generated for additional work to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-19 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 312 2nd Ave., Decatur | 11850 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 22:00 hours, when the heavy rain subsided and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-22 | 2016-03-22 |  | Chatham | Savannah | Outfall 004 | 195000 | pH at the overflow sample point was 10.87. BOD5, TSS and pH were samples were taken up and down stream. They are respectively: BOD5: 40 ppm and 6 ppm; TSS: 221 ppm and 151 ppm; pH: 7.84 and 7.29. The total pounds of BOD5 and TSS and the max pH will be added to and reported on the March DMR Report. | Low Volume Waste | Coastal District |  | Pump Station | Other | N/A | Debris |  | John Kalp | John Kalp | John Kalp | 3/22/2016 1:45:00 PM | Savannah |  |  |  | 1 | Savannah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | NA | 0 | At approx. 0103 hrs on 22Mar16 two simultaneous failures of the Pulp Mill Sump pumps occurred resulting in an overflow from the sump. the total discharge was 23.5 minutes with an estimated total of 195,000 gallons. Preliminary investigation indicates two causes. A 6"x6"x 2' piece of wood became wedged in the suction bell of the East pump mill sump pump breaking the pump's shaft. this caused the middle pulp mill sump pump to cycle on and off to maintain sump level. The constant cycling caused excessive heat on the motor leads and led to the second motor to ground and not run. The remaining West pulp mill sump pump motor could not keep up with 100% of the flow resulting in and overflow until the Middle sump pump could be restored. No environmental effects were seen in the Savannah River, no color change, no dead fish, no foam. |  | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2016-04-04 | 1 | 0 | 0 | 0 | 0 | 0
2015-05-28 | 2015-05-28 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 46.2 mg/L on 05/28/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Rose Lane, Toccoa | 12000 | Spill notice received though email and fax. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 2/5/2018 12:00:00 AM |  |  |  |  | 0 | Eastanollee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Approximately 1.8 inches of heavy rain was received on Sunday morning ia a very short time frame. This caused the two pumps in the station to be unable to keep up with the incoming flow, although both pumps were running at maximum speed. | The cause of the overflow condition was excessive inflow due to heavy rains. The City of Toccoa is continuing its work to find and eliminate sources of rain flowing into the sanitary sewer system. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-06 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-25 | 2018-01-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Sto | 1420 South Hariston Road, Stone Mountain GA 30088 | 2640 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/25/2018 4:43:00 PM | Ocmulgee | 1/25/2018 12:00:00 AM |  |  | 1 | Bashela Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rag blockage caused manhole #16-003-s112 to overflow | Pressure washed 8" line |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-11 | 2017-02-11 | Cobb County Water System | Cobb |  | 54 Vinings Lake Dr. | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/13/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spread Lime in Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3349 17th Ave., Columbus, GA | 35529 | Fax received on 12/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rainfall subsided, flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-20 | 2015-05-20 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to be 27.0 mg/L on 05/20/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 0 | Initial call 2/4, full report received 2/10 | Treated Effluent | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Hydraulic Overload |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 2/4/2016 12:00:00 AM | Ochlockonee | 2/4/2016 12:00:00 AM | 2016-02-04 |  | 1 | Parker's Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Hydraulic overload of the WPCP due to heavy rainfall. During the rain event, flows at the facility increased from 1 MGD to 5 MGD. Flow volume = 20,400 gals. Flow, Weekly Average (MGD): permit = 3.75, reported = 2.65 | No immediate corrective action could be taken due to the nature of the spill. After plant flow returned to normal, debris was cleaned from the outfall area and lime was applied. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-10 | 0 | 1 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025
2017-09-11 | 2017-09-11 | Lowndes County (South Regional WPCP) | Lowndes | Lowndes County Regional | Multiple: 2301 Old Clyattville Road; 5280 Saddle Bags Road; 4109 Quail Hollow Drive; 2880 Touchton Road | 6200 | Email received 2017-09-12. | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Pump Station | Ground |  | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/12/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outages and generator issues caused by Hurricane Irma. | Area cleared of debris and lime spread. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 616 Mitchell Bridge Road, Athens | 12617 | Full report faxed 12/30 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/30/2015 12:00:00 AM | Oconee | 12/24/2015 12:00:00 AM | 2015-12-24 |  | 1 | tributary to Middle Oconee | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Overflow caused by major rain event | Cleaned area of solids. Sewer upgrade is under design |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-30 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2018-01-21 | 2018-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5543 East Mountain Street Stone Mountain GA 30083 | 5400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/22/2018 11:28:00 AM | Ocmulgee | 1/21/2018 12:00:00 AM |  |  | 1 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure wash sewer main manhole 18-089-s113 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-22 | 0 | 0 | 0 | 0 | 0 | 0 | Enard Frett |  | Dekalb Co Dept. Watershed Management
2015-10-19 | 2015-10-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1150 Rankin Street, Stone Mountain | 80 | Notification received on October 26, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/19/2015 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 9:21 hours, when a crew pressure washed the 8" sewer main 205ft, cleared the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Blackshear, City of | Pierce | Blackshear | Manhole on Edgewood Circle. Storm drainage ditch that empties into the Alapaha River. | 7600 | Spill notification form received on September 19th, 2017 from Trey Pearson. Signage is being placed at the discharge point. The local health department and local media are being notified. | Raw Sewage | Coastal District | GAJ020001 | Collection System | Ground, Storm Drain, Stream | Ditch | Natural Disaster |  | Bill Hawthorne | Brett Berry | Brett Berry | 9/21/2017 12:00:00 AM | Satilla |  |  |  | 1 | Alapaha River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive flows due to heavy rains flooding sewer collection system. | N/A | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-21 | 1 | 1 | 0 | 0 | 0 | 0
2015-11-10 | 2015-11-10 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Suwanee | 55 Buford Hwy | 3660 | ERT notified 11/10/2015. CTS No. 78283 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Suwanee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-06-28 | 2016-06-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 2010 | fax received 6/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/30/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-14 | 2016-04-14 | Douglasville, City of (South Central WPCP) | Douglas | Lithia Springs | 3507 Meadowview Dr., Lithia Springs (Meadowview Lift Station) | 500 | Email and fax received on 04/14/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Lift Station | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 4/14/2016 12:00:00 AM |  | 4/14/2016 12:00:00 AM |  |  | 1 | Dry Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease build-up on control floats caused malfunction. Pumps did not turn on properly and alarms malfunctioned. | Spill was discovered by WSA mechanic performing preventative maintenance at the site. He immediately turned the pumps on in hand mode and pumped the wet well down to stop the spill. VacCon Crews were dispatched to the site to clean the grease from the well and clean up any trash and debris at the site of the spill. Crews cleaned and disinfected the area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-29 | 2018-01-29 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Did not enter water | 0 |  | Unknown |  | GA0021725 |  |  |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/2/2018 12:00:00 AM | Oconee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-13 | 2017-06-13 | Darien, City of (Darien WPCP) | McIntosh |  | 112 Florida Street Darien | 200 | affected area was treated with lime | Raw Sewage | Coastal District | GA0033529 | Lift Station |  |  | Debris |  | Hailey Harden | Hailey Harden | Hailey Harden | 6/16/2017 9:31:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | a clog in the sewer line | Vac-Con Truck was dispatched to pressure jet the gravity line before the clog. | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2017-06-28 | 1 | 0 | 0 | 0 | 0 | 0
2015-04-03 | 2015-04-03 | Cobb County MS4 | Cobb |  | 2800 Paces Ferry Rd. | 1410 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/3/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8" Clay Main | Cleaned area and Spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | Two manholes near the Carlton Woods Lift Station, Moultrie | 50000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Lift Station | Stream | Stream | Natural Disaster |  |  | Dagny Pariani | Dagny Pariani | 9/2/2016 12:00:00 AM | Ochlockonee | 9/2/2016 12:00:00 AM | 2016-09-02 |  | 1 | unnamed tributary to Ochlockonee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Tropical Storm Hermine - Spill initiated by a power failure, with spill continuing due to extremely heavy rainfall | Backup power applied. Spill monitored. Cleaned and limed area once the overflow stopped. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc.
2015-10-16 | 2015-10-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 Handley Avenue, SW | 1110 | fax received 10/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/19/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The construction crew made a repair to the mainline |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-30 | 2016-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2214 Wingate Street, SW | 10 | fax received 1/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 1/30/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-30 | 2015-12-30 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Cown Drive Lift Station | 1800 | Unable to locate orginal spill notification. Five Day Follow-up received 1/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/8/2016 12:00:00 AM |  |  |  |  | 1 | Little Haynes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2015-02-15 | 2015-02-15 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 27.6 mg/l
2018-04-04 | 2018-04-04 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | 9508 Highway 92 Woodstock, GA | 4950 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Debris |  | Mick Smith | Kathy Lewis | Eric Dykes | 4/5/2018 12:00:00 AM | Coosa |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown obstruction in the sewer line | Jetted sewer line to clear the obstruction vacuumed ground areas of any debris or sewer, lime ground areas. Scheduled a camera inspection of the sewer line to investigate the obstruction. | 4265e0af-00af-4b96-982e-53f807bc3994 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2017-07-03 | Fulton County (Big Creek WPCP) | Fulton |  | 7219 Peachtree Dunwoody Road | 3200 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Marsh Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spilled stopped and cleaned | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-28 | 2018-08-28 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 4375 Feather Court - Martinez | 900 | Fax sent 2018-08-30 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 8/30/2018 12:00:00 AM |  | 8/28/2018 12:00:00 AM |  |  | 1 | 900 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, flushable wipes, and debris. | Unclogged sewer line with jet machine. Limed overflow area. Posted signs. Planned follow-up video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-22 | 2017-03-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4392 Stonington Circle, Dunwoody | 5720 | Notification received on March 24, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/22/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Yhe problem was corrected at 13:10 hours when a crew pressure washed the 410ft., cleared the blockage at 408ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-28 | 2016-07-28 | Cobb County MS4 | Cobb |  | 2128 Berry Hill Cir. | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/28/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Clay Main | crew members stopped the spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-22 | 2016-12-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2788 Defoors Ferry Rd, NW, ATL | 995 | Fax received on 12/27/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/27/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1440 Sowell Estate, Stone Mountain | 52600 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event /I&I | The problem was corrected at 08:45 hours on April 6, 2017, when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 565 East Weasley Rd, NE - ATL | 2 | Fax received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | 666 Brantley Blvd Lift Station | 6000 |  | Raw Sewage | Coastal District | GA0024431 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/12/2017 8:00:00 AM | Satilla |  |  |  | 1 | Un-named tributary of the Seventeen Mile River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure | Power restored | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-24 | 2015-05-24 | Columbia County (Little River WPCP) | Columbia |  | 875 William Smith Blvd | 8400 | fax received 5/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 5/26/2015 12:00:00 AM |  |  |  |  | 1 | Walton Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism - Someone had put large rocks and limbs in a manhole. | Set up bypass pump, removed debris, plan to bolt down manhole cover |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2018-08-13 | 2018-08-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3330 Northlake Parkway, Atlanta GA 30345 | 47460 | manhole 18-210-p129 a private manhole | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 8/13/2018 9:59:00 PM | Ocmulgee |  |  |  | 1 | North Lake | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | unknown blockage | unsuccessfully pressure washed. Bypassed to stop spill. Point repair will be scheduled |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-05 | 2016-05-05 | Cobb County MS4 | Cobb |  | 2763 Holly Ridge Circle | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/5/2016 12:00:00 AM |  |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of roots in sewer main causing the manhole to overflow into a tributary of Sope Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-06 | 2015-08-06 | Cobb County Water System | Cobb |  | 680 South Cobb Dr. | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the 8 Inch PVC sewer main | Cleaned area and spread lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-10-13 | Jesup, City of (Jesup WPCP) | Wayne | Jesup | East Plum Street Lift Station | 1080 |  | Raw Sewage | Coastal District | GA0026000 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2017 4:44:00 PM | Altamaha |  |  |  | 1 | Penholloway Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure | Power restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2017-07-18 | 2017-07-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5248 Golfcrest Circle, Stone Mountain | 1500 | Notification received on July 19, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/18/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 09:21 hours when a first responder crew cleaned the grease nad rags out of the invert at the manhole and restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-20 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-09 | 2017-08-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1496 Country Squire Drive, Decatur | 49050 | Notification received on August 14, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 8/9/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 11:00 hours when the storm event subsided and the flow return to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-29 | 2017-12-29 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | City of Swainsboro WWTP | 175 | Voicemail left 2017-12-29. Physical letter sent 2017-12-29. | Sludge | Wastewater Regulatory Program | GA0039225 | WWTP | Stream |  | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 12/29/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A guide wire stabilizing the aerator in the aerobic digester broke, and the aerator drifted to the side wall, splashing out liquid phase solids. | Guide wire replaced and aerator put back in service. Liquid phase solids were washed back into primary aeration basin with a high-pressure water hose. Approx. 95% of .the spill was reclaimed. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2322 Carey Drive, SE | 1000 | Fax received 1/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/16/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-25 | 2017-10-25 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 1240 Wildwood Drive - Social Circle | 100 | Scan sent 2017-10-26. Physical letter received | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Swale | Grease |  |  | Alys Hannum | Alys Hannum | 10/26/2017 12:00:00 AM |  | 10/26/2017 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease/roots blockage. | Employees used a jet machine to clear the blockage. Degreaser was applied along with root destroyer. Sign posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-21 | 2017-03-21 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3562 Gardenbrook Dr. - Augusta | 450 | Email received 2017-03-22 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Rags |  |  | Alys Hannum | Alys Hannum | 3/22/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Debris | Technician ran an auger to open the sanitary sewer line and stop the manhole from overflowing. The downstream storm pipe was flushed and vacuumed out. The sanitary sewer will be assessed via SLRAT. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-24 | 2016-10-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, N.E., Atlanta | 230 | Fax received on 10/25/2016. | Raw Sewage |  | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 10/25/2016 12:00:00 AM |  |  |  |  | 0 | Dry Land Spill | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | the crew performed a point repair, cleaned and disinfected the area. Placed on periodic inspection schedule to monitor for upgrading, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-02 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1820 Doug Barnard Pkwy - Augusta | 9107820 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/4/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The wastewater collection system was still recovering from 7-inch rain event earlier in the week. | Projects to remove rainwater from the wastewater collection system are in various stages of design and implementation. Begun monitoring of Butler Creek as requested by the EPD. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 161 Hood Circle, Decatur | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | At time of arrival, manhole had stopped discharging |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 3125 Samples Road - Cumming | 6700 | Call received 2018-01-29. Late report of spill due to miscommunication. | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Pump Station | Stream | Stream | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 1/29/2018 12:00:00 AM |  | 1/29/2018 12:00:00 AM |  |  | 0 | Haw Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Control malfunction at the pump station. | Controls were reset. Lime applied for stabilization. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2017-09-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3889 Chaucer Wood, Atlanta | 3040 | Notification received on September 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 9/20/2017 12:00:00 AM |  |  |  |  | 0 | Perimeter Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and grease blockage. | The problem was corrected at 20:24 hours when the first responder crew rodded the 8-inch sewer main 51-ft, clearing the roots and grease blockage at 48-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-22 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-10 | 2016-01-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5457 Hedgeflower Court, Stone Mountain | 4120 | Notification received on January 11, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Hsin Yeh | 1/10/2016 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage due to vandalism | The problem was corrected at 12:58 hours, when a crew removed the debris out of the manhole, pressure washed the 8" sewer main section that was affected, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-03 | 2016-07-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 4960 | Notification of this spill was not received until 7/20/2016 via the hard-copy follow up. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/20/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure. | The crew replaced a mechanical part on the bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-19 | 2017-04-19 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 475 Forestdale Drive | 4160 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Spilled stopped | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-24 | 2018-04-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4347 Flat Shoals Parkway Decatur GA 30034 | 2000 | manhole 15-070-s050 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/25/2018 11:42:00 AM | Ocmulgee | 4/24/2018 12:00:00 AM |  |  | 1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | Wait for storm to end |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-26 |  | Lowndes | Valdosta | Remerton Lane | 311250 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/25/2015 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-21 | 2017-01-24 | Lyons, City of (Lyons North WPCP) | Toombs |  | Akins Lane and E Toombs Avenue 3 Manholes | 104000 |  | Raw Sewage | Coastal District | GA0033391 | Collection System | Ground, Stream | Stream | Wet weather |  | Sarah Khorramzadeh | Charlotte Nevill | Charlotte Nevill | 1/23/2017 10:00:00 AM | Altamaha | 1/25/2017 12:00:00 AM | 2017-01-24 |  | 1 | Swift Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 |  | 0 | Rain event that occurred over the weekend of January 21. |  | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 2017-01-27 | 1 | 1 | 0 | 0 | 0 | 0
2017-05-11 | 2017-05-11 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville | The digester. | 0 | Investigation indicates that while liquid did overflow the digester, the majority of the flow was accumulated foam on and at base of digester and mixed liquor. The majority of the release flow was confined to berm channels and routed to piping which discharged to the plant effluent channel prior to the composite sampler. | Digester Sludge | Coastal District | GA0047180 | WWTP |  | N/A | Operator error |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 5/11/2017 8:30:00 AM | Ogeechee | 5/12/2017 12:00:00 AM |  |  | 0 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After investigating the situation, it was determined that on 10 May, 2017 the last operator on site failed to turn off the sludge pump which pumps sludge material and mixed liquor from the Sequential Batch Reactor (SBR) basins, which are part of the current Fort Stewart construction project, to the Sludge Digesters. Also, the SCADA system didn’t initiate an alarm for digester volume height even though the alarm set point is set for 20.69 feet. | • Operator will document in facility log book daily and before leaving WPCP that the waste pumps are turned off. • Waste valve repair should be completed NLT 30may17 • Once #2 digester is put on live, schedule to clean the overflow line on Digester #1. | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-05-23 | 1 | 1 | 0 | 0 | 0 | 0
2017-11-24 | 2017-11-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4000 DunWoody Park | 1760 | Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/24/2017 4:41:00 PM | Chattahoochee |  |  |  | 1 | Nancy Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole 18-345-s318 spilling and getting into storm drain | Rodded 8" sewer main, cleared grease blockage at 30'ft, and pressured washed sewer main 33'ft from manhole 18-345-100 to 18-345-s318 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-27 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Dave Ring |  | Dekalb County Department of Watershed Management
2016-10-07 | 2016-10-08 | Southern States Phosphate & Fertilizer Company | Chatham | Savannah |  | 0 |  | Unknown | Coastal District | GA0002437 | N/A | Basin |  | Other |  | Cliff Lewis | Cliff Swiger | Cliff Swiger | 10/10/2016 2:49:00 PM | Savannah |  |  |  | 0 | Savannah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Matthew. Facility reported that Kayton Canal had flooded and the deluge encroached upon the facilities grounds including its discharge system. The outflow was surface water and the facility was not in operation at the time of the flooding. |  | 37abf76e-1c4e-11e1-9fd5-12313b0cb679 | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 33550 | Notification received on January 24, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  |  | Hsin Yeh | 1/23/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 12:35 hours when the heavy rain stopped and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b |  | 2017-01-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-20 | 2017-12-20 | Adairsville, City of (North WPCP) | Bartow |  | Manhole 106 Cass Street | 118080 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream | Stream | Wet weather |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/20/2017 12:00:00 AM | Coosa | 12/26/2017 12:00:00 AM |  |  | 0 | Unnamed tributary to Oothkalooga Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The city received heavy rain fall over a short period of time. This caused the Wastewater Treatment Facility to exceed capacity. As a result the collection system backed up and wastewater overflowed the manhole. | City of Adairsville construction personnel found the overflowing manhole at 9 am. They monitored the creek throughout the day. When it stopped raining the water receded and stopped overflowing from the manhole. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-01-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | First Ave & Grant St. - 1000 gallons, Boys & Girls Club 3836 Johnston, Wylly & Townsend St. - 50 gals, 1890 Townsend St. - 50 gals., 124 Hornet Dr. - 50 gallons, 145 Emanuel Farm Rd.- 50 gallons, 1253 B&W Grade Rd. - 1200 gallons, 133 Cardinal Rd. - 1500 gallons, 2001 Cypress Mill Rd. - 100 gallons, 201 Drayton Circle - 500 gallons1106 Cate Rd. - 100 gallons, 126 Cargo Lane - 25 gallons. | 4700 | Due to Hurricane Irma collection system crews were not able to properly assess all SSOs as priority was given to conduct repair operations to restore both sewer and water systems back to proper operational status. | Raw Sewage | Coastal District | GA0025313 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/19/2017 1:04:00 PM | Satilla | 9/11/2017 12:00:00 AM |  |  | 1 | Academy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Irma caused a hydraulic overload of the sewage collection system. | Crews working to restore proper operational status of wastewater collection system. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-27 | 1 | 1 | 0 | 0 | 0 | 0
2015-09-15 | 2015-09-15 | QUIGG BRANCH WATER POLLUTION CONTROL PLANT | Rockdale |  | 1000 Weatherwood Place | 2080 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/17/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Boar Tusk Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Ragging | Cleared and Cleaned Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-02 | 2017-04-02 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 624 Southbridge Blvd., Savannah, GA | 450 | Initial call and final report received by Michelle Cortes on 4/2, follow up occurred 4/3 and 4/4. | Raw Sewage | Coastal District | GA0038326 | Force Main | Other |  | Equipment failure |  | Michelle Cortes | Dagny Pariani | Dagny Pariani | 4/2/2017 12:00:00 AM | Savannah |  |  |  | 1 | drainage pond | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Air release valve failed on sewer force main. Overflow was into a drainage pond with no exit point. | Shut lift station off to stop overflow and temporarily shut air release valve. Valve to be permanently repaired asap. Vac trucks removed storm/sewage water from pond and sampled for fecal coliform. | db6b2c02-fb34-11e0-9fd5-12313b0cb679 | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-04-04 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2016-01-12 | 2016-01-12 | Dallas West WPCP | Paulding |  | Three Lane Hill | 67000 |  | Raw Sewage | Mountain District - Cartersville | GA0026026 | WWTP | Stream |  | Rags |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 1/12/2016 12:00:00 AM | Coosa |  |  |  | 0 | Griffin Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump went down and bypass was clogged due to rags in valves | Pumped out sewage off ground raked up and disposed of solids and limed infected area | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | Kendall Smith | 770-443-8117 | City of Dallas | 129 E Memorial Dr, Dallas, Georgia, 30132
2016-03-27 | 2016-03-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1957 Glenwood Ave, Atlanta | 2925 | Notification received on March 30, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/27/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | pump failure | The problem was corrected at 22:05 hours, when a crew removed all the rags out of the pump, restarted the pump to stop the spill and restored the sewer flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-31 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-28 | 2018-05-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 210 Pryor St. SW - Atlanta | 1000 | Fax sent 2018-05-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/29/2018 12:00:00 AM |  | 5/28/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-24 | 2015-08-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1132 Collier Road, NW | 510 | Fax received 8/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/26/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-26 | 2015-10-26 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1100 Block of North Lee Street | 600 | call received 10/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Other |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 10/27/2015 12:00:00 AM |  |  |  |  | 1 | Retention Pond to One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Jetted line. Limed area. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2015-07-01 | 2015-07-01 | Trion, Town of (Trion WPCP) | Chattooga |  | Town of Trion WPCP | 13020 |  | Treated Effluent | Mountain District - Cartersville | GA0025607 | WWTP | Stream |  | Hydraulic Overload |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 7/2/2015 12:00:00 AM | Coosa |  |  |  | 0 | Chattooga River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Clarifier #1 was hydraulically overloaded briefly |  | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | Andy Melton | 706-734-7015 | Town of Trion
2016-09-03 | 2016-09-03 | Columbia County (Crawford Creek WPCP) | Columbia | Evans | 899 Fury's Ferry Road | 72000 | Fax received 9/03/2016. Email received 9/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Jones Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Force main ruptured | Replaced broken pipe. Began sampling of creek. posted signs | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-12-23 | 2015-12-23 | Savannah, City of (President Street WRF) | Chatham | Savannah | Pen Waller / Wassaw Road (128 Wassaw Road) | 1220 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Debris |  | Steve Fox | Steve Fox | Steve Fox | 12/23/2015 12:00:00 AM | Savannah | 12/23/2015 12:00:00 AM |  |  | 1 | Betz creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Manhole overflows due to debris (rags) blockage (residential area) | Ditch was contained between Betz Creek and spill site and site was mitigated to further contain and clean overflow site. Containment was placed at Penn Waller Cove / Penn Waller Road. City utilized jet/vacuum trucks to remove water / wastewater mix. Spill notifications will be placed at spill site, at Penn Waller / Betz Creek and Walthour / Betz Creek. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who will send out a news release to the media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-12-28 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-18 | 2017-01-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2926 Judylyn Drive, Decatur | 4420 | Notification received on January 19, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/18/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:30 hours when the crew pressure washed 200 ft upstream, cleared the blockage at 100 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-21 | 2016-03-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Elenwood | 2623 Brittany Park Lane, Ellenwood | 3600 | Notification received on March 22, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/21/2016 12:00:00 AM |  |  |  |  | 0 | Colony Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was correct at 14:01 hours, when a crew pressure washed the sewer main 400ft, clearing the blockage at 250ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-15 | 2015-06-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 473 Park Valley Drive, NW | 615 | fax received 6/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/16/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-04 | 2018-09-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3393 Blackburn Way, Chamblee GA 30341 | 200 | manhole 18-298-s024 spilling | Raw Sewage |  | GA0024147 | Collection System |  |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/4/2018 1:48:00 PM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-26 | 2015-11-26 | Forsyth County (Dick Creek WRF) | Forsyth | Cumming | 3935 Abingdon Place | 2000 | fax received 11/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038563 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/30/2015 12:00:00 AM |  |  | 2015-11-30 | 2016-11-28 | 1 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 |  | blockage removed by jetting line. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-01 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | Forsyth County
2016-10-08 | 2016-10-08 | Jesup, City of (Jesup WPCP) | Wayne | Jesup | Oran Way Lift station | 8100 |  | Raw Sewage | Coastal District | GA0026000 | Lift Station | Bay | Bay | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/10/2016 9:00:00 AM | Altamaha | 10/8/2016 12:00:00 AM |  |  | 1 | Penholloway Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power to the lift station. | A bypass diesel pump was set-up at the lift station until power was restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-26 | 1 | 1 | 1 | 0 | 0 | 0
2017-02-02 | 2017-02-02 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd. | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/2/2017 12:00:00 AM |  |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags | Stopped the spill and removed Rags | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-03 | 2018-03-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2060 Alison Ct. SW - ATL | 8400 | Fax sent 2018-03-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 3/4/2018 12:00:00 AM |  | 3/5/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-11 | 2015-10-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Road, NE | 740 | fax received 10/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/12/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-28 | 2018-01-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1213 Hill St. SE - ATL | 6 | Fax sent 2018-01-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/29/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-03 | 2015-09-03 | Rockdale County (Almand Branch WPCP) | Rockdale |  | 2145 East park Drive NE | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/3/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Roberts Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction Debris and Ragging |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-19 | 2017-09-19 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | South side of Hwy 278 closest cross street is Old Villa Rica Road and Hwy 278. Blockage was .25 miles east of cross street located on sewer outfall line | 6080 |  | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 9/19/2017 12:00:00 AM | Coosa |  |  |  | 1 | Weaver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to 18" x 4" section of PVC pipe put in line, causing rigs to build up on lodged pipe creating a blockage | Removed all spill debris located on ground, cleaned affected areas of impacted creek, limed all affected areas. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-09-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3420 Benjamin E Mays Dr. SW - ATL | 3860 | Fax received 2017-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-19 | 2018-06-19 | Kentucky-Tennessee Clay Company (Sandersville Plant) | Washington |  | Pond near outfall 001; within the constructed spillway of the pond. | 1000 | EPD notified via email on 6/19/2018 | Other | Wastewater Regulatory Program | GA0003387 |  | Stream |  | Operator error |  |  | Sarita Banjade |  | 6/19/2018 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 'Employee did not notice while pumping water from an upper pond that it had a flow rate greater than the lower pond discharge pump'. Operator error. | 'Upper pump will only be operated when there is certainty that the lower pond will contain the full volume of water to be pumped from the upper pond.' New operator trained to prevent the overflow of the pond. |  |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2018-06-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-06 | 2017-11-06 | Marietta (City of)- Sewers | Cobb | Marietta | 710 Walnut Dr. | 3600 |  | Raw Sewage |  |  | Collection System | Stream |  | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 |  | Henry | Stockbridge | 678 Fairhaven Blvd. Stockbridge Ga. | 56250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration from an already saturated ground. Received 4 inches of rain in a 36 hr period. | Cleaned up spill area around manhole, placed spill notification signs around spill area and notified all of the proper agencies. Started stream monitoring program for major spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-30 | 2015-11-30 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Near Meadow Lake Road | 400 | verbal notification received 11/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Ground |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/30/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage caused by fire extinguishers found in the sewer line | fire extinguishers removed | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO | 478-494-4952
2015-03-17 | 2015-03-17 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Memorial Drive & Tucson Avenue at FLETC | 25000 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Ditch | Ditch | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/17/2015 10:00:00 AM | Satilla | 3/17/2015 12:00:00 AM | 2015-03-17 | 2016-03-16 | 1 | Troupe Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Construction debris blocking |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-03-19 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-03 | 2016-05-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4329 Kimball Road, SW | 50 | fax received 5/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/4/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-25 | 2015-12-25 |  | Henry | Stockbridge | Manhole ID 7860 adjacent to Big Cotton Indian Creek | 3000000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/25/2015 12:00:00 AM | Ocmulgee | 12/25/2015 12:00:00 AM |  |  | 0 | Big Cotton Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A force main break due to heavy rains and flooding in the area loosened soil surronding the force main causing it to shift and rupture. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | Patrick Hembree |  | Herny County Water & Sewerage Authority
2015-06-20 | 2015-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1067 Lanier Blvd. NE | 100 | fax received 6/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/21/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-28 | 2015-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2124 Cheshire Bridge Road, NE | 1490 | fax received 11/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/29/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-29 | 2016-02-29 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 1020 Edgewater Trail | 4590 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/29/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The section of the sewer is being inspected. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-22 | 2015-04-22 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2367 Leila Lane, SE | 358 | fax received 4/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/23/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-15 | 2016-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1033 Hollywood Road, NW | 1780 | fax received 2/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/16/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-23 | 2016-02-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 240 Flint River Road, Jonesboro Manhole 2216228 | 7500 | Fax and voice mail received on 02/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/23/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Severe rainfall caused hydraulic surcharge. | Line returned to normal flow as ground water table receded. Lime was spread and site was cleaned. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-29 | 0 | 1 | 1 | 0 | 0 | 0
2015-09-14 | 2015-09-14 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Due south of 300 Richey Lane | 102000 |  | Raw Sewage | Coastal District | GA0024431 | Force Main |  |  | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/15/2015 9:05:00 AM | Satilla | 9/14/2015 12:00:00 AM | 2015-09-15 |  | 1 | Indian Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 8" force main rupture. | Cleaned and limed the spill area and replaced the damage section of piping with ductile iron piping. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-09-17 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3328 Walton Way - Augusta | 8160 | Fax received 2017-01-03, update received 2017-02-03 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and Trash | Line will be CCTV'ed to determine if any structural damage was a factor in the blockage. The line will be cleaned. Lime spread. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-09 | 2016-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1853 Piedmont Avenue, NE | 480 | fax received 2/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/10/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-02 | 2016-03-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 225 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a breach in the mainline. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-25 | 2015-04-25 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1715 Northside Drive, NW | 445 | fax received 4/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/27/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-30 | 2015-06-30 | Douglasville, City of (South Central WPCP) | Douglas | DOUGLASVILLE | 2222 Lee Road | 28500 | REC email 7/1/2015. REC FAX 7/1/2015. REC 5-day written report 7/7/15. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Stream | Vandalism |  | Emily Wingo | Emily Wingo | Emily Wingo | 7/2/2015 2:12:00 PM | Chattahoochee | 7/1/2015 12:00:00 AM | 2015-07-01 | 2016-07-22 | 1 | Tributary B to Lion Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Vandalism-Bricks, large rocks and construction debris were found thrown into a manhole | VacCon Crews were dispatched to the site and a jet tuck was used to clean the line and clear the blockage. Crews cleaned and disinfected the area around the manhole where the spill occurred. WSA personnel are going to weld down the manhole lids in the area to prevent future vandalism | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-07-02 | 0 | 1 | 0 | 1 | 0 | 0 | [8 empty] | Douglasville - Douglas County Water and Sewer Authority | 770-949-7617
2017-02-14 | 2017-02-14 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2257 Old concord Drive | 6125 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/20/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 0 | Snapping Shoals Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-18 | 2017-04-18 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 154 E. Athens Street - Winder | 450 | Email received 2017-04-19 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Other | Beach | Rags |  |  | Alys Hannum | Alys Hannum | 4/19/2017 12:00:00 AM |  | 4/19/2017 12:00:00 AM |  |  | 1 | Fort Yargo Lake | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The blockage was caused by flushable wipes. | Jetted to relieve the blockage. Storm sewer flushed with clean water and the affected area sanitized with powdered lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-20 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | J.B. Messerly Influent Pump Station | 1628000 | Verbal notification received 9/02/2016 - 9/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-399-1238
2015-08-19 | 2015-08-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 360 Englewood Avenue, SE | 20 | fax received 8/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 8/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-15 | 2017-05-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2291 Macon Dr. SW - ATL | 590 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/16/2017 12:00:00 AM |  | 5/15/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1155 Woodland Avenue, NE | 1610 | fax received 3/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/15/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used construction material to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-01 | 2016-04-01 | Tifton, City of (New River WPCP) | Tift | Tifton | 1439 Sutton Circle, Tifton | 16800 | Email received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Storm Drain | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Tributary of New River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall on April 1-2, 2016. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 1 | 0 | 0
2016-07-07 | 2016-07-07 | East Point (City of)- Sewers | Fulton | East Point | 3076 Glendale Court | 6600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the leaking into the Creek was in part to the close proximity of the M.H. to the creek bank, and minor hole / leak for the bottom of the manhole / clay joint resuliting into a discharge in the Camp Creek Basin. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-09 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Lift Station number 12, Albany | 180000 | Telephone call and email received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Lift Station | Unknown |  | Power failure |  |  |  | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Unknown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | the National Weather Service reported 8 - 9 tornadoes plus straight line winds, resulting in power loss to 52 storm and sanitary lift stations. | Full power was restored to al lift stations on 01/14/2017. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2016-09-01 | 2016-09-01 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 451 Creek Ridge | 2000 | fax receive 9/02/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 9/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in manhole | Unstopped manhole with high pressure jet machine. Removed roots from invert. Planned follow up removal of roots and repair of manhole. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2016-12-29 | 2016-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3330 Northlake Parkway, Tucker | 5460 | Notification received on January 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/30/2016 12:00:00 AM |  |  |  |  | 0 | Henderson Mill Creek to North Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 23:20 hours, when a crew pressure washed the 8" sewer main 150ft, clearing the grease blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-18 | 0 | 1 | 0 | 0 | 0 | 0
2018-09-14 | 2018-09-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6591 Tribble Street Litonia GA 30058 | 9495 | manhole 18-121-s008 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/14/2018 6:42:00 PM | Ocmulgee |  |  |  | 1 | Pole bridge Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2017-07-12 | Athens-Clarke County (North Oconee WPCP) | Clarke | athens | 155 Paradise Blvd on ACC Fire Training ROW | 3174 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/12/2017 12:00:00 AM | Oconee |  |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | fire extinguisher and rags clogged sewer | remove extinguisher and rod sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-08 | 2016-03-08 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6029 Creekside Drive, Columbus | 3838 | Telephone call received on 03/08/2016, email received on 03/09/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan |  | Paul Moisan | 3/8/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tributary of Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8-inch main was broken due to creek bank erosion resulting in the pipe leaking. | Once the repair was made to the main, the discharge stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-03-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-22 | 2018-06-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1561 Burnstone Drive Stone Mountain GA 30088 | 1280 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/23/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Polebridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | Rodded manhole |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-30 | 2017-10-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1800 Briarcliff Circle, Atlanta | 2640 | Notification received on November 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/30/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 19:36 hours when the first responder crew pressure washed the sewer main 300-ft, cleared the blockage at 125-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-11-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 165 Meadow Park Lane, SW | 1001 | fax received 1/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-29 | 2016-01-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 606 | fax received 1/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/30/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-31 | 2017-08-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 240 Clarke St. SE - ATL | 200 | Fax sent 2017-09-01; received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/1/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-16 | 2015-09-16 |  | DeKalb | Doraville | 4272 Winters Chapel Road Doraville | 1200 | Notification received on September 18, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/17/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 17:00 hours, when a crew built a soil berm to contain the spill, and repaired the sewer main with 10" pvc pipe to restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3401 17th Ave., Columbus | 730 | Fax, email, and voice mail received on 02/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed. | Once the rain subsided and flow returned to normal, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-21 | 2016-02-21 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1310 C & L Drive Dalton | 24000 | Dalton Utilities is meeting with a private contractor today to establish a plan for permanent repairs | Raw Sewage | Mountain District - Cartersville | GA02-056 | WWRF | Stream |  | Pipe failure |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/22/2016 12:00:00 AM | Coosa |  |  |  | 1 | Mill Creek | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Erosion of stream bank exposed sewer pipe which collapsed | Vacuum trucks pumped out an upstream manhole. After installing an inflatable plug a aportable pump was used to bypass the broken section of sewer main and pumped to a downstream manhole. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-29 | 2015-11-29 | Clayton County Water Authority (Shoal Creek WPCP) | Clayton | Jonesboro | 8095 Flamingo Drive | 1200 | Fax received 11/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038369 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 11/30/2015 12:00:00 AM | Flint |  |  |  | 1 | Kendrick Waters | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-01 | 0 | 1 | 1 | 0 | 0 | 0
2015-12-31 | 2016-01-01 | Griffin, City of (Shoal Creek WPCP) | Spalding | Griffin | 541 South Pine Hill Road, Griffin | 44100 | Notification received on January 5, 2016. | Raw Sewage | Wastewater Regulatory Program | GAJ020036 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The cause was infiltration and inflow due to the excessive rain. The land area was cleaned and limed. Also, samples are being collected and tests are being performed on the affected stream. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 644 Wesley Drive, NW | 61600 | fax received 12/24/2015. CTS No. 78623 Volume originally entered as 32,100 gal. Volume on final SMP = 61,600 gal. Changed 2017-04-04. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  | 2015-12-24 | 2017-01-13 | 0 | Peachtree Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-24 | 2016-11-24 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Buford | I-85 between mile marker 115 and 116 | 7030 | Notification received on November 25, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0026433 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 11/25/2016 12:00:00 AM |  |  |  |  | 0 | Ivy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Raked area and spread lime. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-28 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-18 | 2015-11-18 | Columbus Water Works (South WRF) | Muscogee | Columbus | Manhole at 1826 Slade Drive. | 3824 | Fax received on November 19, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. The basin is Weracoba Creek Basin. | Once the rain subsided, and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-05 | 2018-02-05 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 180 Lake Forest Dr. | 1319 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/6/2018 12:00:00 AM | Oconee |  |  |  | 1 | Middle Oconee River Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags | Hand rodded and flushed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-03 | 2016-04-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 368 | fax received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | The crew repaired the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-02 | 2015-11-02 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Lift Station #2 102 Little Creek Trail | 15780 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 11/2/2015 12:00:00 AM | Chattahoochee | 11/3/2015 12:00:00 AM |  |  | 1 | Little Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall | Area affected by spill has been cleaned up and powdered lime has been applied. The city is going to make sure that the manhole at 206 Sycamore Way will be properly sealed to prevent a spill in the future. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | Justin Allen | 706-754-4216 | City of Clarkesville
2016-11-11 | 2016-11-11 | Blue Ridge, City of (Blue Ridge WPCP) | Fannin |  | Industrial Park Road Pump Station #6 | 100000 |  | Raw Sewage | Mountain District - Cartersville | GA0037583 | WWTP | Stream |  | Power failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 11/14/2016 12:00:00 AM | Tennessee |  |  |  | 0 | Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Failure | Pump station starters were reset and monitoring began | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-14 | 2018-07-14 | Oconee County (Calls Creek WPCP) | Oconee |  |  | 31250 | A spill occured at 1144 Experiment Station Rd on Saturday July 14, 2018. An estimated 31,250 gallons entered a tributary of Calls Creek. | Raw Sewage | Northeast District - Athens | GA0050211 | WWTP |  |  | Other |  | Phoebe Tchoua | Phoebe Tchoua | Phoebe Tchoua | 7/16/2018 12:00:00 AM |  | 7/16/2018 12:00:00 AM | 2018-07-15 |  | 1 | Tributary to Calls Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | "The cause of the spill was determined to be a solids build-up on a flow meter strap that became dislodged in the pipe. The expansion strap is normally placed inside a collection pipe in order to calculate flows as it passes through. The accumulation of solids on the strap caused a blockage to the effluent side of the manhole that resulted in the overflow of the manhole." |  | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 2018-07-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Rd. SW - ATL | 5700 | Fax received 2017-04-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/26/2017 12:00:00 AM |  | 4/25/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-24 | 2015-11-24 | Gainesville, City of (Flat Creek WRF) | Hall | Gainsville | 2641 Old Flowery Branch Road, Gainesville | 2600 | Notification received on November 25, 2015. | Sludge | Wastewater Regulatory Program | GA0021156 | WWTP | Stream |  | Operator error |  |  | Hsin Yeh | Hsin Yeh | 11/24/2015 12:00:00 AM |  |  |  |  | 0 | Flat Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Human error. | Plant personnel discovered the incident. Once discovered, staff immediately turned off the recycle pump. Environmental Compliance staff began the required monitoring protocol early Wednesday morning (November 25, 2015) by posting signs and monitoring the spill site. People from Maintenance, Plant Operations and Environmental Services are actively working to clean up and monitor all affected areas. No negative impact on the receiving stream. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-22 | Hazlehurst, City of (Bully Creek WPCP) | Jeff Davis | Hazlehurst | Conner Street & Plum Street | 1500000 |  | Raw Sewage | Coastal District | GA0036765 | Force Main | Ditch | Ditch | Natural Disaster |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/22/2017 11:30:00 AM | Ocmulgee | 9/22/2017 12:00:00 AM | 2017-09-22 |  | 1 | Bully Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Hurricane Irma - Large trees were blown over by high winds which heavily damaged a 12" aerial sewer main. | Trees removed and aerial sewer main repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2017-11-10 | 2017-11-10 | Cobb County Water System | Cobb |  | 5011 White Blvd | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/24/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spill stop time 1:30 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-17 | 2015-03-17 |  | DeKalb | Stone Mountain | 917 Second Street, Stone Mountain | 2360 | Notification received on March 19, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 3/17/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary to Howell Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and grease blockage | The problem was corrected at 11:41 hours when a crew rodded the 8" sewer main upstream 37ft, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRF | 0 | verbal notification received 2/26/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is an outfall spill from TSS: Reported TSS = 30 mg/L. Estimated flow = ~91.7 MG |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-18 | 2016-01-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1671 James Jackson Parkway, NW | 1575 | fax received 1/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/19/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 530 Reunion Court, SW | 27000 | fax received 2/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  | 2016-02-03 | 2017-02-24 | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-16 | 2016-11-16 | Pilot Travel Center #069 WPCP | Troup | LaGrange | Aeration Basin | 0 | Compliance Office Stephanie Edwards must follow-up to ensure that the solids are removed and documentation is provided to demonstrate acceptance at a permitted solid waste handling facility | Primary/Secondary Effluent | West Central District | GA0032565 | WWTP | Ground | N/A | Equipment failure |  | Scott Henson | Scott Henson | Stephanie Edwards | 11/16/2016 12:00:00 AM |  |  |  |  | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | On Wednesday, November 16, 2016, Mr. Greg Bleigh, Operator, contacted me and said that there was a spill at the facility. He said that a fuse blew at the effluent control panel and it disabled all alarms. He said that the water backed up through the plant and the spill occurred at the aeration basin. He said that the spill was contained inside the fence and did not enter Long Cane Creek. He said that he applied lime to control odors and is getting a bid to have the solids removed and taken to a landfill. I told him to write a letter to the Division, explain what happen to cause the spill and submit receipts demonstrating proper disposal of the solids removed. He said that he would submit the report the week of November 21, 2016. On Thursday, November 17, 2016, I conducted a site visit and verified that the discharge did not enter Long Cane Creek. See attached pictures. Lime had been applied to the spill area to aid in odor control. | Did not impact state waters. | 42d4a71e-eb6e-11e0-b8d8-000c29971acc | 426838fe-eb6e-11e0-b8d8-000c29971acc | 42d4a71e-eb6e-11e0-b8d8-000c29971acc | 2016-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-15 | 2018-01-15 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 1133 Gable Terrace Drive, Jonesboro | 24000 | Fax received on 01/16/2018. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/16/2018 12:00:00 AM |  |  |  |  | 0 | East Jester's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease | Blockage was cleared and flow returned back to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-01-23 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-23 | 2018-01-23 | Wadley, City of (Wadley WPCP) | Jefferson | Wadley | The main truck line that is supported by pillars, running along William Swamp Creek bridge on North Main Street. | 35000 |  | Raw Sewage | Northeast District - Augusta | GA0021024 | Collection System | Stream |  | Pipe failure |  | Glen Treadwell | Adrienne Tabor | Adrienne Tabor | 1/23/2018 6:00:00 PM |  |  | 2018-01-25 | 2019-01-25 | 1 | William Swamp Creek | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | A 12" gravity feed main failed due to one of the pillars holding it up collapsed and broke and caused the other pipes to pull out of the coupling. | Raw sewage is actively bypassed to break by pumping from one manhole above the break to a manhole below, while the pipe is being repaired. Three pillars' integrity was also comprised when the pillar collapsed causing the pipe to roll. These pillars will be stabilized by a tripod system and the couplings will also be upgraded from 6" to 12". The repairs were all completed by January 29, 2018. | 4adb1baa-eb6e-11e0-b8d8-000c29971acc | 52f24d07-1cda-4f35-88c5-340e6bb62008 | 52f24d07-1cda-4f35-88c5-340e6bb62008 | 2018-01-31 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Kyle Edenfield |  | City of Wadley |  | City of Wadley
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 157 Hood Circle, Decatur | 3840 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 13:42 hours when the heavy rain stopped and normal flow was restored. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-03 | 2018-08-03 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Lexington Road | 0 | unknown | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Ground |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/4/2018 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown |  |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-28 | Rome, City of (Rome WRF) | Floyd |  | Behind the Coosa Valley Fairgrounds near a City of Rome Lift Station | 430000 | See spill report dated 2.29.2016 | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream | Stream | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/26/2016 12:00:00 AM | Coosa | 2/28/2016 12:00:00 AM |  |  | 1 | Etowah River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Significant wet weather event | Conducting an investigation | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-24 | 2017-02-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1319 Halter Lane, Lithonia | 4760 | Notification received on February 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/25/2017 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station Failure | The problem was corrected at 19:56 hours when a crew pumped down the spilling manhole, stopped the spill and resumed normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-23 | 2017-05-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3589 Kingsboro Rd. NE - ATL | 3120 | Email received 2017-05-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/24/2017 12:00:00 AM |  | 5/23/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-23 | 2015-10-23 | Washington, City of (Rocky Creek WPCP) | Wilkes | Washington | Off of Garland Avenue | 4000 | Notification received on October 27, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0031101 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/27/2015 12:00:00 AM |  |  |  |  | 0 | Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A tree's root system growing into the sewer pipe causing it to bust. | The leak was fixed on October 23, 2015 by replacing a 15 foot sectionof the damaged pipe. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-19 | 2015-03-19 | Thomaston, City of | Upson | Thomaston | Industrial Lift Station | 3000 | Spill did not reach surface waters. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/19/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred when landscaping personnel was mowing the sewer easement and accidentally struck an air relief valve. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-10 | 2016-02-10 | Cobb County MS4 | Cobb |  | 5229 Sandlewood Court | 280 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/10/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in sewer main causing the manhole to overflow into a tributary of Willeo Creek. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-27 | 2016-03-28 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1800 Block of Remer Lane | 84300 | Email notification received 3/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 3/28/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-05-23 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3220 Bellanca Street | 24260 | fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Lindsey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, sewer main has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-31 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-28 | 2018-06-28 | City of Chattanooga | Catoosa |  | Spring Creek Pump Station Vero Beach Drive | 3750 |  | Raw Sewage | Mountain District - Cartersville | GAU060004 | WWTP | Stream |  | Wet weather |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 6/29/2018 12:00:00 AM | Tennessee |  |  |  | 1 | Spring Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain Event | Turned on diesel backup pump | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-10 | 1 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Rome, City of (Rome WRF) | Floyd |  | Coosa Valley Fairgrounds near a City of Rome Lift Station | 10000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/28/2015 12:00:00 AM | Coosa |  |  |  | 0 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Significant wet weather event causing the Etowah River to rise and overtop manholes both upstream and downstream |  | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2016-04-18 | 2016-04-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2400 Bohler Road, NW | 3140 | fax received 4/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/20/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-12 | 2017-09-13 | Nassau Woods Mobile Home Park | Chatham | Savannah | 1602 Dean Forest Rd., Savannah, GA 31408 | 8500 | Initial notification received from Garden City on 9/13, full report received from operator on 9/17 | Raw Sewage | Coastal District | GAG550101 | Lift Station | Storm Drain |  | Power failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/13/2017 9:45:00 AM | Ogeechee |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station for PID system - pump #1 tripped due to clogging by trash and pump #2 failed to come on because the pump had burnt out. | Pump #1 was cleared of trash and pump #2 was replaced. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Franklin Management
2017-09-12 | 2017-09-13 | Nassau Woods Mobile Home Park | Chatham | Savannah | 1602 Dean Forest Rd., Savannah, GA 31408 | 8500 | Initial notification received from Garden City on 9/13, full report received from operator on 9/17 | Raw Sewage | Coastal District | GAG550101 | Lift Station | Storm Drain |  | Power failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/13/2017 9:45:00 AM | Ogeechee |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station for PID system - pump #1 tripped due to clogging by trash and pump #2 failed to come on because the pump had burnt out. | Pump #1 was cleared of trash and pump #2 was replaced. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Franklin Management
2017-02-16 | 2017-02-16 |  | Clarke | Arhens | 290 Midway Dr. | 473 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/16/2017 12:00:00 AM | Oconee |  |  |  | 0 | cedar creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-18 | 2016-01-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2214 Wingate Street, SW | 60 | fax received 1/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/19/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-17 | 2015-02-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1235 Plaza Avenue, SW | 627 | fax received 2/18/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/18/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-18 | 2016-07-18 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lilburn | 996 Traymore Drive | 1921 | fax received 7/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/19/2016 12:00:00 AM |  |  |  |  | 1 | Tributary of Beaver Ruin Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Washed down impervious can collected run-off. Placed signs at spill and affected waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-03-09 | 2017-03-10 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 4177 Forest Hill Terrace, Macon MH ID 67585 | 17600 | Fax and email received on 03/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  |  | Paul Moisan | 3/13/2017 12:00:00 AM | Upper Ocmulgee | 3/10/2017 12:00:00 AM | 2017-03-13 |  | 1 | Sabbath Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was grease and rags. | Debris was removed and the area was disinfected with lime. Line scheduled to be cleaned with grease emulsifier and televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-03-14 | 1 | 1 | 0 | 1 | 0 | 0 | Heather Veal |  | MACON WATER AUTHORITY
2016-06-13 | 2016-06-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 381 Mount Zion Road, SW | 200 | fax received 6/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/13/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The spill was self contained |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-18 | 2015-09-18 | Athens-Clarke County (North Oconee WPCP) | Clarke |  | 420 King Ave. | 81 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/18/2015 12:00:00 AM | Oconee |  |  |  | 0 | Brooklyn Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | cracked pipe | dug up pipe and replaced broken section | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-30 | 2016-03-30 | Cobb County MS4 | Cobb |  | 2944 Lowe Way | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in sewer main causing the manhole to overflow into a tributary to Noonday Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4666 South Hope Springs Road, Stone Mountain | 3080 | Notification received on January 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/13/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:56 hours when the crew rodded the manhole 81 ft upstream, cleared the blockage at 72 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-22 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Intersection of Spring St. and Russ Circle | 100 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Equipment failure |  | Brian Koehler | Brian Koehler | Brian Koehler | 2/23/2017 3:04:00 PM | Chattahoochee |  |  |  | 1 | Soque River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | collapsed sewer main | replace main and subsequent taps | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 2017-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-17 | 2016-03-17 | Baldwin, City of (Baldwin WPCP) | Baldwin |  | 300 Harrisburg Road | 1200 | Will go back and camera the line | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Roots |  |  | Dagny Pariani |  | 3/18/2016 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Sewer line blocked by roots | Jetted line and removed roots |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2237 Howe Ave., Columbus, GA | 13519 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Chattahoochee River. | Once the rainfall subsided, and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 1 | 0 | 0
2017-01-11 | 2017-01-11 | Fulton County (Johns Creek Environmental Campus) | Fulton |  | 225 Ledgemont Court Sandy Springs | 3300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The area impacted by the spill has been cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Gibson, City of (Gibson WPCP) | Glascock | Gibson | Gibson WPCP-Rocky Comfort Creek section located at the facility. | 30000 |  | Treated Effluent | Northeast District - Augusta | GA0021849 | WWTP | Stream | Stream | Natural Disaster |  | Glen Treadwell | Adrienne Tabor | Adrienne Tabor | 9/21/2017 12:00:00 AM | Ogeechee |  | 2017-09-25 | 2018-09-27 | 1 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | "Due to Hurricane Irma, the high winds made the duck weed in the pond shift causing it to rotten. Therefore, the oxygen level decreased causing a non compliant BOD sample." |  | 4adb1baa-eb6e-11e0-b8d8-000c29971acc | 52f24d07-1cda-4f35-88c5-340e6bb62008 | 52f24d07-1cda-4f35-88c5-340e6bb62008 | 2017-11-08 | 1 | 1 | 1 | 1 | 0 | 0 | Jamie Kitchens |  | CITY OF GIBSON WPCP | [5 empty] | City of Gibson |  |  | 63.9 | 47.4
2016-06-26 | 2016-06-26 | Marietta (City of)- Sewers | Cobb | Marietta | 250 N Forest Ave. | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/26/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-06-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-02-01 | Cobb County MS4 | Cobb |  | 1490 Dansford Court | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-06 | 2017-02-06 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 890 Tower Road - Social Circle | 100 | Email received 2017-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Ditch | Grease |  |  | Alys Hannum | Alys Hannum | 2/7/2017 12:00:00 AM |  | 2/6/2017 12:00:00 AM |  |  | 0 | n/a | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper and grease blockage | Cleared blockage with jet machine. Lime applied to spill site. Sign posted. Proper agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2017-07-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1074 McConnell Drive, Decatur | 1200 | Notification received on July 19, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/17/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:02 hour when a first responder crew pressure washed the 8 inch sewer main 300 feet, removed the debris/grease blockage at 296 feet, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-20 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-23 | Talbotton, City of (Talbotton WPCP) | Tift | Tifton | Tifton WPCP - 80 Old Brookfield Rd W | 9500 | Telephone call and email received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0047805 | WWTP | Stream | Shoreline | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  | 1/23/2017 12:00:00 AM |  |  | 1 | New River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was excessive rainfall over the weekend. | Mitigated with hydrated lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0 | Thomas Corker | 229-391-3904 | TIFTON NEW RIVER WPCP
2017-09-27 | 2017-09-27 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 316 and 337 Commercial Drive, Savannah, GA | 5075 | Initial phone call and full report received 9/27. | Raw Sewage | Coastal District | GA0020443 | Collection System | Canal | Canal | Equipment failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/27/2017 12:00:00 AM | Savannah | 9/27/2017 12:00:00 AM |  |  | 1 | Chippewa Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station failure caused system to surcharge and manhole to overflow | Contained water in canal and removed water/sewage mix (23,000 gallons) from canal with vac truck. Set up bypass pumps, investigated and corrected cause of station control failure. Will continue to mitigate canal and affected area. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6584
2016-02-24 | 2016-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 0 | Verbal notification received 2/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  |  |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-10 | 2015-12-10 | Ashburn, City of (Airport WPCP) | Turner | Ashburn |  | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2015 12:00:00 AM | Ocmulgee | 12/10/2015 12:00:00 AM |  |  | 0 | Ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The Rags plugged the pumps in the station and a fan belt broke on the backup pump. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-13 | 2017-02-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 233 Toni Pl. SE - ATL | 528 | Fax received 2017-02-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 2/15/2017 12:00:00 AM |  | 2/13/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-03 | 2018-01-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 6701 Peachtree Industrial Boulevard, Doraville GA 30360 | 117375 | Lab discovered high fecal count in creek and found problem days later | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/10/2018 1:38:00 PM | Ocmulgee | 1/5/2018 12:00:00 AM | 2018-01-07 |  | 1 | Nancy Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | unknown blockage under Peachtree Ind Blvb. | Rodded sewermain |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-10 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Malcom Benton Tiptopn |  | Dekalb Co Dept. Watershed Management
2018-01-16 | 2018-01-16 | Marietta (City of)- Sewers | Cobb | Marietta | 848 Powder Springs St | 4025 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-09 | 2016-09-10 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 611 Veterans Memorial Drive | 900 | verbal notification received 9/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/12/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Orr Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | gravel and debris in line causing partial blockage | removed gravel and debris | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CUMMING | 404.597.3310
2018-02-19 | 2018-02-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 380 Ardmore Cir. NW - ATL | 80 | Fax sent 2018-02-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-30 | 2015-10-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2717 Hedgewood Drive. NW | 8436 | fax received 10/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/31/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken mainline | The crew replaced a section of the main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-12 | 2017-01-12 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 1095 Colony Trail | 66000 | No fish kill reported. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/12/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Line Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravity sewer main break in an interceptor sewer. | The 16" DIP to 18"RCP connection was reapired by extending the DIP further away from the creek and rip rap was added to deter further erosion. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-07 | 2016-11-07 | Cobb County Water System | Cobb | Marietta | 1024 Ector Chase | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in sewer main causing the manhole to overflow into Noonday Creek. | The Water System was notified at 8:45 a.m. and our crew stopped the overflow at 10:30. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Creekside Subdivision, LaGrange | 5025 | Fax received on 01/22/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/22/2016 12:00:00 AM | Chattahoochee | 1/22/2016 12:00:00 AM |  |  | 1 | Dixie Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was heavy rains inflow/infiltration. | Spill stopped on its own as the D/S liftstation was pumped down. Will be installing bolt-down covers at spill locations and continuing to seek out and correct I/I sources. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-12 | 2017-04-14 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 251 West Laurens School Road - Dublin | 220 | Email received 2017-04-13 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Force Main | Ground | Ditch | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/13/2017 12:00:00 AM |  | 4/12/2017 12:00:00 AM |  |  | 0 | Dry Land | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The 10" PVC main had a small crack on the bottom side of the pipe. | All repairs completed; Vac Truck used to maintain the lift station well and vacuum up the water in the drainage. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-06 | 2015-03-06 | Tifton, City of (New River WPCP) | Tift | Tifton | 1408 Love Avenue | 28000 | REC CALL 3/7/2015 (Sat). REC EMAIL 3/13/2015. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Canal | Canal | Debris |  | Emily Wingo | Emily Wingo | Emily Wingo | 3/7/2015 1:04:00 PM | Suwannee | 3/7/2015 12:00:00 AM | 2015-03-09 |  | 1 | New River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Blockage | Cleared blockage | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-09 | 0 | 1 | 0 | 1 | 1 | 0 | Scott Murphy |  | ESG Operations, Inc. | [5 empty] | CITY OF TIFTON | 229-391-3937
2015-03-19 | 2015-03-19 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | This is a major outfall spill. Reported TSS = 62 mg/l; Reported Volume = 25,650,000 million gallons. | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 3/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Storm related hydraulic overload which clogged the bar screens with influent debris. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-28 | 2018-06-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5473 Mount Vernon Way Dunwoody GA 30338 | 4520 | Manhole 18-375-s257 spilling | Raw Sewage |  | GA0024147 | Collection System |  |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/29/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-13 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 4815 Frontier Dr. - Cumming | 15 | Email sent 2018-03-13 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/13/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer plug in manhole | Vac liquids from manhole; entered manhole to remove plug; nearby pooled water was vac'ed and lime applied. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-02 | 2016-11-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 266 Robin Street, Decatur | 5480 | Notification received on November 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 11/3/2016 12:00:00 AM |  |  |  |  | 0 | Peavine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 19:37 hours, when a crew pressure washed the 8" sewer main 133ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-10 | 2017-02-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 27250 | Fax received Saturday 2017-02-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Paul Moisan | 2/11/2017 12:00:00 AM |  | 2/10/2017 12:00:00 AM | 2017-02-11 | 2018-03-05 | 1 | Utoy Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed mainline. | Crew used a by-pass pump to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-13 | 0 | 0 | 0 | 1 | 1 | 1
2017-04-03 | 2017-04-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Rd. SW - ATL | 966 | Fax received 2017-04-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/4/2017 12:00:00 AM |  | 4/3/2017 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-28 | 2018-01-28 | CITY OF LAGRANGE-LONG CANE CREEK WPCP | Troup | Lagrange | 311 Creekside Dr. | 7350 | Full report is uploaded into GAPDes. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/28/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Dixie Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rains created excessive inflow, overwhelming lift station and allowing sewage to escape through an open clean-out in yard. | Once rains subsided, the lift station returned to normal operation. Ongoing search for I/I sources will continue. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-28 | 2018-01-28 | CITY OF LAGRANGE-LONG CANE CREEK WPCP | Troup | Lagrange | 311 Creekside Dr. | 7350 | Full report is uploaded into GAPDes. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/28/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Dixie Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rains created excessive inflow, overwhelming lift station and allowing sewage to escape through an open clean-out in yard. | Once rains subsided, the lift station returned to normal operation. Ongoing search for I/I sources will continue. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-06 | 2016-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1047 Princeton Park Drive, Lithonia | 2480 | Notification received on April 11, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 4/6/2016 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 11:00 hours, when a crew cleaned out the roots from the downstream pipe and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-04 | 2018-03-04 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 701 North Cherokee Road - Social Circle | 20 | Email sent 2018-03-05 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Swale | Debris |  |  | Alys Hannum | Alys Hannum | 3/5/2018 12:00:00 AM |  | 3/5/2018 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - paper | Jet machine used to clear blockage. Debris cleaned up from site. Sign posted to notify public, lime applied to spill site. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-09 | 2016-03-09 | East Point (City of)- Sewers | Fulton | East Point | 1947 Connelly Drive bewtween Manhole ID U-166-049 and U-166-050. | 6750 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The probable cause of the spill was due to damage by GA Power mowing Crew. | The City's crew jetted and vacuumed out the Main to remove the blockage, and cleaned the affected area as required. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-18 | 2018-07-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 650 Selig Dr. SW - Atlanta | 3000 | Fax sent 2018-07-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/19/2018 12:00:00 AM |  | 7/18/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure | Crew used a bypass pump to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-25 | 2016-01-25 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 1952 Tanglewood Drive | 2049 | fax received 1/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Other |  |  | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM |  |  |  |  | 1 | Watson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structure failure |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-02-20 | 2017-02-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1069 Lookout Ave. NW - ATL | 2150 | Fax received 2017-02-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 2/21/2017 12:00:00 AM |  | 2/20/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-13 | 2015-05-13 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 789 Pinehurst Drive, Fairburn, GA | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2015 12:00:00 AM | Flint |  |  |  | 0 | Unnamed Tributary of Line Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, Grease, and debris | The City jetted the city sewer main. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-22 | 2016-02-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, NW | 2430 | fax received 2/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/23/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-22 | 2017-09-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 2761 Walnut Creek Road, Macon GM ID 19718 | 5700 | Email received on 09/27/2017; phone call received on 09/25/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Other |  |  |  | Paul Moisan | 9/27/2017 12:00:00 AM | Ocmulgee | 9/22/2017 12:00:00 AM |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was tree falling and breaking an exposed sewer main. | The sewer main was repaired; sewage is no longer escaping. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-20 | 2018-01-20 | Cobb County Water System | Cobb |  | 2210 Cumberland Drive | 370 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Bert Adams Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Crew stopped spill at 5:25 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-23 | 2015-09-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 277 Clifton Street, SE | 4890 | fax received 8/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/24/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew made a repair to the line |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-20 | 2018-04-20 | Villa Rica, City of (Tallapoosa West WPCP) | Douglas | Villa Rica | City of Villa Rica's gravity sewer lines. | 2000 | The vollume of flow was estimated to be around 8000 gal with only about 2000 gal reaching the creek which is a tributary to the Town Branch Creek. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 4/20/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Town Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a blockage in the gravity sewer line that caused the flow to back up and spill through a joint in a raised man hole. | The line was jetted and cleared and flow resumed as normal. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1821 Alder Drive | 27000 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2017-09-11 | 2017-09-11 | Blackshear, City of | Pierce | Blackshear | Manhole on North Grady Street in Blackshear. Flows into a storm drainage ditch that empties into the Alapaha river. | 6000 | Spill notification form received on September 19th, 2017 from Trey Pearson.Signage is being placed at the discharge point. The local health department and local media are being notified. | Raw Sewage | Coastal District | GAJ020001 | Collection System | Ground, Storm Drain, Stream | Ditch | Natural Disaster |  | Bill Hawthorne | Brett Berry | Brett Berry | 9/11/2017 12:00:00 AM | Satilla |  |  |  | 1 | Apalaha River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive flows due to heavy rains flooding sewer collection system. | N/A | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-21 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-14 | 2017-04-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 174 Chalmers Dr. NW - ATL | 3320 | Fax received Saturday, 2017-04-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/15/2017 12:00:00 AM |  | 4/14/2017 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-24 | 2015-09-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Road, NE | 1956 | fax receive 9/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/25/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and roots | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-22 | 2015-12-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 111 E Maple Street, Decatur | 840 | Notification received on December 23, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/22/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:17 hours when a crew rodded the 8" sewer main 18ft downstream, clearing the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-11 | 2016-12-11 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1150 Fifth Street - Augusta | 1450 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Ditch |  | Grease |  |  | Alys Hannum | Hsin Yeh | 12/12/2016 12:00:00 AM |  |  |  |  | 0 | Tributary to Mid-City | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Line was opened and resumed normal flow. The storm ditch was flushed and vacuumed out. Will assess the line with CCTV to determine what actions need to be taken to prevent future issues. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-05 | Fulton County (Big Creek WPCP) | Fulton |  | Azalea Drive/Riverside Road Roswell 30075 | 3664473 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/4/2015 12:00:00 AM | Chattahoochee |  | 2015-01-04 |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Heavy rains caused big creek to overflow the banks and inundate the sewer system along the Chattahoochee river and Big Creek. | Ongoing I/I Reduction Program | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-06 | 2018-04-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 650 17th Bishop St. - Atlanta | 450 | Fax sent 2018-04-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/7/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Tifton, City of (New River WPCP) | Tift | Tifton | Agrirama Lift Station, Tifton | 4100 | telephone call received on 12/06/2016; Email received on 12/07/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Lift Station | Stream | Shoreline | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/6/2016 12:00:00 AM |  | 12/6/2016 12:00:00 AM |  |  | 1 | Little River Basin | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was heavy rainfall. | Hydrated lime was spread to mitigate and sanitize the affected area. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-08 | 0 | 1 | 0 | 0 | 0 | 0 | Andrew Marzen |  | ESG Operations, Inc.
2017-07-10 | 2017-07-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 255 Mathews Ave. NE - ATL | 3 | Fax received 2017-07-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/11/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 130 Lawshe St. SW - Atlanta | 540 | Fax sent 2018-03-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 3/14/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-29 | 2016-01-29 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Loganville | 211 Emory Lane | 8202 | fax received 1/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/29/2016 12:00:00 AM |  |  |  |  | 1 | Brushy Fork Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-11-30 | 2017-11-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1353 Montreat Ave. SW - ATL | 1850 | Fax sent 2017-12-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 12/1/2017 12:00:00 AM |  | 11/30/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-02 | 2017-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 532 Ross St. SW - ATL | 890 | Fax received on 02/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/3/2017 12:00:00 AM |  |  |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-09 | 2018-05-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Conley | 1678 Koppers Road, Conley GA 30288 | 1580 | manhole 15-020-s115 spilling | Raw Sewage |  | GA0024147 |  | Storm Drain |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/9/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Blue Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | debris blockage | Pressurewashed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-10 | 2015-09-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1942 East Starmount Way, Decatur | 7650 | Notification received on September 16, 2105. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Natural Disaster |  |  | Hsin Yeh | Hsin Yeh | 9/10/2015 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 22:20 hours, when the heavy rain subsided and the crew rechecked the sewer main for any obstruction, the main was found cleared and regular flow was restored. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-08 | 2016-03-08 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Suwanee | 2700 Crestridge Court | 9494 | fax received 3/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/8/2016 12:00:00 AM |  |  |  |  | 0 | Tributary to Little Suwanee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | verbal notification received 1/19/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain. This is an outfall spill. TSS = 290 mg/L. Total volume 68,560,000 gallons. | Temporary bar screen | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-23 | 2016-02-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 601 McDonough Blvd, SE | 174 | fax received 2/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/24/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-31 | 2018-05-31 | Pembroke, City of (Pembroke WPCP) | Bryan |  | 144 west Ind. blvd | 4000 | issued an NOV | Raw Sewage | Coastal District | GA0038377 | Collection System | Ground, Storm Drain, Stream | Ditch | Wet weather |  | Cate Williams | Steve Wurtz | Steve Wurtz | 6/4/2018 12:00:00 AM | Upper Ocmulgee | 6/3/2018 12:00:00 AM | 2018-06-04 | 2018-09-03 | 0 | tributary of ogeechee Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | I&I problem large amounts of rain | removal of solids, notification of public and new outlets, will replace lift station pump to get more flow to WWTP | 48f7be6a-9e6f-4367-8d25-df303c0058c0 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-06-06 | 1 | 1 | 1 | 0 | 0 | 0
2017-10-23 | 2017-10-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 968 Stallings Ave. SE - ATL | 100 | Fax sent 2017-10-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 10/24/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debirs | Spill contained. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-09 | 2016-12-09 | Cobb County Water System | Cobb | Marietta | 240 The Bluffs | 510 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in Main Line | Flushed and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2017-07-07 | Gwinnett County (F. Wayne Hill WRC) |  | Duluth | 2670 N Berkeley Lake Rd. - Duluth | 2600 | Fax received 2017-07-07 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 7/7/2017 12:00:00 AM |  | 7/7/2017 12:00:00 AM |  |  | 1 | Bromolow Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots; Debris - wipes, paper, and other products. | Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-28 | 2015-01-30 |  | Stephens | Toccoa | Hillcrest Street, Toccoa | 100 | Notification received on January 29, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  |  | Hsin Yeh | 1/29/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary to Eastanollee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The blockage was removed and the flow quickly returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b |  | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-24 | 2015-08-24 | Dallas West WPCP | Paulding |  | Plant Outfall | 289500 | See Report dated August 26, 2015 | Other | Mountain District - Cartersville | GA0026026 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 8/24/2015 12:00:00 AM | Coosa |  |  |  | 0 | Weaver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment Failure | Failed components replaced with new components | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | Brian Bourque | 770-443-8118 | City of Dallas
2018-01-22 | 2018-01-22 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | 112 Park Lane | 1800 | Full report uploaded. | Raw Sewage | Wastewater Regulatory Program | GA0020079 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2018 12:00:00 AM | Flint |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | The crews cleared the blockage at 6:02 pm. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-11 | 2017-04-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 115 Biscayne Dr. NW - ATL | 7125 | Fax received 2017-04-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/12/2017 12:00:00 AM |  | 4/11/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 7850 Old Covington Hwy, Lithlnia | 646250 | Notification received on December 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/25/2015 12:00:00 AM |  |  |  |  | 0 | Pine Mountain Creek to Yellow River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected on December 25, 2015, at 15:00 hours, when the rain subsided and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4828 A Miller Road, Columbus | 14262 | Voice mail received on 02/03/2016; fax and email received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Cooper Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Cooper Creek. | Once the rain subsided and flow returned to normal and the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-09 | 2015-09-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 886 Granite Springs Land, Stone Mountain | 5280 | Notification received on September 16, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/9/2015 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots | The problem was corrected at 20:26 hours, when the clean up crew, pressure washed the 8" sewer main 120ft upstream, cleared the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-23 | 2015-03-23 | Cobb County MS4 | Cobb |  | 1049 Triad Ct. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/23/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" PVC Main | Cleaned and Limed Area | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-15 | 2016-12-16 | Flowery Branch, City of (Flowery Branch WPCP) | Hall | Flowery Branch | Oakwood Industrial Park South | 9000 | Notification letter received on December 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0031933 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 12/16/2016 12:00:00 AM |  |  |  |  | 0 | Mud Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer line corridor leaking | Contained the spill and repair the damaged section. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-09 | 2016-12-09 | SOUTH COBB WATER RECLAMATION FACILITY | Cobb |  | 240 The Bluffs NW | 510 |  | Raw Sewage | Wastewater Regulatory Program | 000012035 | Collection System | Stream | Stream | Contractor |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflo occurred as a result of grease causing it to overflow into a tributary of the Chattahoochee River. | The Cobb County crew stopped the overflow at 8:15 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-04 | 2018-07-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2489 Baxter Rd. SW - Atlanta | 30 | Fax sent 2018-07-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 7/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Spill was self contained, Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-13 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | Walmart Lift-Station Force Main | 2940 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/20/2018 12:00:00 AM | Flint |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Pipe | Repairs were made and the station was brough back on line at 3:40 pm. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-22 | 2015-01-22 | Douglasville, City of (Sweetwater Creek WPCP) | Douglas | Douglasville | 6264 Malone Rd | 4300 | REC EMAIL 1/26/2015. REC FAX 1/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0047201 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/26/2015 12:00:00 AM | Chattahoochee | 1/23/2015 12:00:00 AM |  |  | 1 | Huey Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and solids | Clean the line and clear the blockage | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-28 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Douglasville Douglas County Water and Sewer Authority (DDCWSA) | 770.949.7617
2016-03-01 | 2016-03-02 | Hogansville, City of (Hogansville WPCP) | Troup | Hogansville | West off of Hwy 29N | 126000 | Notification received on March 2, 2016. | Raw Sewage | Wastewater Regulatory Program | GAJ020019 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 3/2/2016 12:00:00 AM |  |  |  |  | 0 | Yellow Jacket Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Erosion from heavy rains, causing the entire manhole to fall into the branch, breaking the line. | Crew members repaired the lines. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-03 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-11 | 2016-11-11 |  | Gwinnett | Snellville | 1956 Tanglewood Drive, Snellville | 289 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/12/2016 12:00:00 AM |  |  |  |  | 0 | Watson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure - Cracked | Washed down impervious and collected run-off |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-06 | 2018-07-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1376 Church Street Decatur GA 30030 | 920 | manhole 18-007-s201 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/6/2018 7:54:00 PM | Ocmulgee |  |  |  | 1 | Church Street Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | rodded sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-30 | 2018-08-30 | Columbus Water Works (South WRF) | Muscogee | Columbus | 927 Forbes Drive | 349 |  | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Pipe failure |  |  | Juan Robles | Juan Robles | 8/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" pipe broke that resulted in a discharge into a unnamed tributary of the Chattahoochee River. | Section of broken pipe was repaired. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 103 Country Oaks Drive, Macon MH ID - 62635 | 1400 | Fax received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  |  |  |  | 1 | Upper Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and roots. | Debris was removed. This line is scheduled to be cleaned with grease emulsifier and televised. It will also be treated for root control. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1280 Oakland Dr. SW - ATL | 3105 | Fax received 2017-04-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/26/2017 12:00:00 AM |  | 4/26/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-29 | 2018-04-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2362 Dellwood Dr. NW - Atlanta | 100 | Spill originally reported as creek spill on 2018-04-30. Updated to dry land on 2018-05-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/2/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-26 | 2017-03-26 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 2330 Highpoint Rd. - Snellville | 4108 | Fax received 2017-03-26 Correction received 2017-03-28 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/26/2017 12:00:00 AM |  |  |  |  | 1 | Jacks Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and Other Products; Grease | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | DeKalb | Atlanta | 1320 Memorial Dr. SE - ATL | 2625 | Fax received on 01/18/2017 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  | Paul Moisan | Alys Hannum | Paul Moisan | 1/18/2017 12:00:00 AM |  | 1/17/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed machine. | Steps taken to prevent reoccurence. Placed on periodic inspection schedule. Need for upgrading, etc. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-29 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 357 Hall Street, Macon MH ID 66166 | 1600 | Fax and email received 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Upper Ocmulgee | 12/29/2015 12:00:00 AM |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was grease. There are commercial sources of grease upstream from this location and residential grease is not regulated. | The manhole was located down the street. Any remaining sewage was washed back into the manhole and the street was washed down. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-06-05 | 2015-06-05 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 408 Patrick Henry Ct. | 9000 | REC FAX 6/5/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 6/5/2015 9:49:00 AM | Flint | 6/5/2015 12:00:00 AM |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared Blockage. Blockage was cleared and flow returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Lines will be televised and grease cleaned and i problem is located it will be repaired. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-10 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 770-960-5205
2015-12-06 | 2015-12-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Road, SW | 7500 | fax received 12/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-21 | 2016-11-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Sanpfinger Woods Drive, Decatur | 36420 | Notification received on November 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/22/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease blockage | The problem was corrected at 09:00 hours on November 22, 2016, when a crew rodded the 8" sewer main 150ft, clearing the grease and debris blockage which restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-28 | 0 | 1 | 0 | 1 | 1 | 0
2015-01-04 | 2015-01-04 |  | DeKalb | Decatur | 1615 Melanie Court, Decatur | 47575 | Notification received on January 6, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/5/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | Service was restored at 09:07 hours when the heavy rain receded, in addition a crew inspected the manholes up and down stream and observed the flow has restored to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-23 | 2015-07-23 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 501 East Walton Street | 600 | verbal notification received 7/23/2015. CTS No. 77401 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 7/23/2015 12:00:00 AM |  |  |  |  | 1 | Tanyard Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Used root cutter on pipe, limed area, and plan to watch stream for fish kill and pipe for root control |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-23 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2018-02-20 | 2018-02-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 215 West Wieuca Rd. NW - ATL | 1960 | EDIT 2/20 - THIS IS A PRIVATE SPILL, NOT PUBLIC. Fax sent 2018-02-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/21/2018 12:00:00 AM |  | 2/21/2018 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | EDIT 2/20 - THIS IS A PRIVATE SPILL, NOT PUBLIC. Debris in the mainline | EDIT 2/20 - THIS IS A PRIVATE SPILL, NOT PUBLIC. Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-08 | 2018-08-08 | Pine Mountain, Town of (Pine Mountain WPCP) | Harris |  |  | 500 |  | Raw Sewage | West Central District | GA0025691 | Lift Station | Stream | Stream | Equipment failure |  |  |  | Stephanie Edwards | 8/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 426838fe-eb6e-11e0-b8d8-000c29971acc |  | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 240 Flint River Road, Jonesboro | 384000 | Telephone call received on 12/30/2015. Fax received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Severe rain event caused a hydraulic overload on the system | Sampling, and lines upstream of the spill event to be inspected to determine the sources of the I/I. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-24 | 2017-04-24 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn |  | Harry Driggers Boulevard | 3000 |  | Raw Sewage | Coastal District | GA0025313 | Force Main | Canal | Canal | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/24/2017 12:05:00 PM | Satilla | 4/24/2017 12:00:00 AM |  |  | 1 | Altamaha Canal | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken force main | Force main repaired, notification signs posted along storm drains and Altamaha Canal, Vac-con truck utilized to stop spill until forced sewer main was repaired. Remedial actions: applied potable water via fire hydrants to increase dissolved oxygen and dilute affected areas to minimize impact. Additionally an air pump was used to raise DO. A fish kill of 62 fish consisting of Catfish, Brim & Minnows occurred as a result of this spill. Wildlife Resources Division Representative was also on site to evaluate the spill impact. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-05-15 | 1 | 1 | 0 | 0 | 0 | 0
2018-08-14 | 2018-08-14 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 1010 Honeysuckle Road - Dublin | 2500 | Phone call rec'd 2018-08-14 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Pump Station | Other |  | Power failure |  |  |  | Alys Hannum | 8/14/2018 12:00:00 AM |  |  |  |  | 0 | Private Retention Pond | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at the lift station. | Power company (EMC) was called to repair. Wet well was pumped down. Health Dept. and Newspaper notified. Low-lying area will be monitored over the next 10 days in case of rainfall or other situations which could cause adverse impacts. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-08-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-23 | 2015-11-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1327 Fairview Road, NE | 40 | fax received 11/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  | Kim Hembree |  | Kim Hembree | 11/24/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 |  | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-01 | 2017-02-01 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 5655 Spalding Dr. - Norcross | 5506 | Fax received 2017-02-01 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/1/2017 12:00:00 AM |  | 2/1/2017 12:00:00 AM |  |  | 0 | Unnamed Tributary of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - rocks or construction material - and wipes, paper, and other products. | Washed down impervious surface and collected runoff, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-16 | 2016-01-16 | Tifton, City of (New River WPCP) | Tift | Tifton | Intersection of Hwy. 82 and I-75 (Exit 62) in the southwest intersection off ramp heading south. | 1000 | Email received on 01/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/19/2016 12:00:00 AM |  | 1/16/2016 12:00:00 AM |  |  | 1 | Cowhouse River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to a grease blockage. | Hydrated lime was spread to mitigate and sanitize the affected area. The blockage was removed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-29 | 2016-12-05 | Cobb County Water System | Cobb |  | 3111 Port Cobb Dr. | 1310 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/5/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical failure (Pump) 12" DI main | Stopped spill at 1240 hrs. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2150 Joesph E Boone Blvd, NW | 3820 | fax received 2/27/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/27/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew installed a bypass pump to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-04 | 2016-10-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 2311 Dunwoody Crossing, Dunwoody | 242 | Notification received on October 10, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/5/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Leak coming form a creek crossing | The problem was corrected on October 4, 2016 at 13:30 hours when the contractor set up a by-pass pump to contain the leak, and completed the repair of the creek crossing which restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-11 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 |  | Lowndes | Valdosta | Hwy 133 | 22000 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Withlacoochee | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-12-19 | 2017-12-19 | Cobb County Water System | Cobb | Marietta | 1075 Amberton LN / Lost MT RD | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Florance Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in County 8" PVC Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-12 | 2017-02-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1173 Smith St. SW - ATL | 1125 | Fax received 2017-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 2/13/2017 12:00:00 AM |  | 2/12/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-28 | 2017-02-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 340 Armour Dr. NE - ATL | 150 | Fax received 2017-03-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Paul Moisan | 3/1/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-06 | 2017-12-06 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2727 Cardigan Ct. - Augusta | 4500 | Email sent 2017-12-07 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Alys Hannum | 12/7/2017 12:00:00 AM |  | 12/6/2017 12:00:00 AM |  |  | 1 | Butler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sanitary Sewer Overflow was caused by vandalism, which led to a buildup of grease in the upstream side of the manhole invert. Debris (rocks) from the hillside were found in the manhole. | A large rock had to be removed from the invert before the sewer gravity main could be augered. The sanitary sewer main was augered to break up the grease in the line. The area around the manhole was cleaned up and lime was spread in the area. Notifications were placed downstream of the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-03 | 2016-05-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3841 Kensington Road, Decatur | 6120 | Notification received on May 6, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/3/2016 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 9:30 hours, when a crew pressure washed the 8" sewer main 300ft, cleared the blockage at 80ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 188 Wadley Street, NW | 415 | fax received 5/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/24/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-04 | 2016-04-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1697 Line Street, Decatur | 2300 | Notification received on April 11, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/5/2016 12:00:00 AM |  |  |  |  | 0 | Shoals Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 20:42 hours, when a crew pressure washed the 8" sewer main 150ft, clearing the blockage at 60ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-01 | 2015-12-01 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lilburn | 4629 Charcoal Lane | 3680 | fax received 12/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/2/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8" main break | Repaired main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-11-13 | 2015-11-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 4000 | ERT notified 11/14/2015. CTS No. 78303. Verbal notification received 11/16/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 11/14/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The plug in Outfall No. 3 dislodged |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-24 | 2016-02-01 | Cobb County MS4 | Cobb |  | 2871 Torreya Way | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson |  | 2/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-22 | 2017-03-24 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 142 & 144 Hartwood Drive | 1000 | Notice of Noncompliance letters were sent to the two property owners at 142 Hartwood Drive, and 144 Hartwood Drive, in Woodstock, GA 30189. 142 - Mr. Jeffrey Willis 144 - Mr. Richard Selby Stream Monitoring conducted by CCW&SA. | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream | Stream | Other |  | Ebony Johnson | Kathy Lewis | Mick Smith | 3/23/2017 12:00:00 AM | Coosa | 3/23/2017 12:00:00 AM |  |  | 0 | Posey Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fell and broke sewer lines due to storm | Customers had plumbers fix lines | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 4265e0af-00af-4b96-982e-53f807bc3994 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-31 | 2015-12-31 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 615 Riverhill Dr., Athens | 12580 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Oconee | 12/31/2015 12:00:00 AM | 2016-01-02 |  | 1 | Middle Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole overflowed during flood event | Cleaned area. Sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-11-18 | 2017-11-18 | Trion, Town of (Trion WPCP) | Chattooga |  | Plant by pass line into Chappel Creek (relief valve) | 96000 |  | Raw Sewage | Mountain District - Cartersville | GA0025607 | WWTP | Stream | Stream | Equipment failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 11/18/2017 12:00:00 AM | Coosa |  |  |  | 0 | Chappel Creek and Chattooga RIver | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Widespread 3-4 hour power outage and plant's back up generator failed to start because of starter solenoid | Replace starter, solenoid and batteries on existing generator Get quotes to replace existing generator | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-11-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-20 | 2018-01-20 | Chatham County | Chatham | Savannah | 2 Elizabeth Circle, Savannah, GA 31406 | 124000 | Initial phone call received through CTS, complaint id #85117, on 1/20/18. Full report received via email on 1/24/18. | Raw Sewage | Coastal District | GAU060099 | Force Main | Storm Drain, Stream | Ditch | Pipe failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 1/20/2018 5:00:00 PM |  | 1/22/2018 12:00:00 AM | 2018-01-20 |  | 1 | Vernon River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 570000 | 0 | Section of pipe on 16" force main failed. Overflow into drainage ditch along Sallie Mood Dr. - Casey Canal - Hayner's Creek - Vernon River. | Main was excavated and broken section replaced. Vac truck was used to remove ~40,000 gallons from ditch, area was cleaned and limed. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-01-25 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CHATHAM COUNTY | 912-721-5580
2017-12-14 | 2017-12-14 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Atlanta | 155 Meadowbrook Drive - Lawrenceville | 6616 | Fax sent 2017-12-14 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/14/2017 12:00:00 AM |  | 12/14/2017 12:00:00 AM |  |  | 1 | Pew Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and other products | Raked area and spread lime, placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-25 | 2016-10-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1038 South Hairston Road, Stone Mountain | 2400 | Notification received on November 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/25/2016 12:00:00 AM |  |  |  |  | 0 | Barbarshela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 15:45 hours, when a crew pressure washed the 8" sewer main 300ft, cleared the blockage at 200ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-01 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-05 | 2016-10-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall Street, SE | 1640 | fax received 10/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 10/6/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-02 | 2015-03-02 |  | Richmond | Augusta | 2611 Crosscreek Road | 6000 | fax received 3/02/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/2/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-09-25 | 2017-09-25 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 518 Towler Shoals View - Loganville | 1260 | Email received 2017-09-27 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/27/2017 12:00:00 AM |  | 9/26/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary to Little Haynes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unspecified blockage in the gravity sewer main. | Jetted and flushed the sewer main to clear the obstruction. Signs posted. Sampling started. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 240 Flint River, Jonesboro MH# 2216228 | 135000 | Fax received on 01/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/23/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Capacity | Lines will be inspected for source for source of inflow and infiltration to solve capacity issue. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 1 | 1 | 1 | 0 | 0 | 0
2017-06-01 | 2017-06-01 | Cobb County Water System | Cobb |  | 3173 Laramie Dr | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-30 | 2016-10-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 630 Aline Dr., NW, Atlanta | 370 | Fax received on 10/31/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 10/31/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the main line. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-8466 | ATLANTA, CITY OF
2015-09-06 | 2015-09-12 | Rochelle, City of (Southeast WPCP) | Wilcox | Rochelle | City of Rochelle Southeast WPCP. | 10000 | Weekly BOD and TSS concentration and loading violations during 09/06/2015 - 09/12/2015 period. Through plant major spill as defined. | Treated Effluent | Southwest District | GA0024236 | WWTP | Stream | Stream | Debris |  |  | Linda Stevens | Jay Howell | 10/20/2015 12:00:00 AM | Suwannee | 10/28/2015 12:00:00 AM | 2015-10-21 | 2016-11-11 | 1 | Unnamed Creek Tributary to Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | There were blockages in the effluent lines during the sampling period of 09/06/2015 - 09/12/2015. | The blockages have been cleared. All PNs performed and completed on 10/31/2015. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-05-24 | 0 | 1 | 0 | 1 | 1 | 0
2018-07-10 | 2018-07-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 810 W. Wesley Rd. NW - Atlanta | 925 | Fax sent 2018-07-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/12/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Leaking mainline | Crew performed a point repair to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-09 | 2017-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1540 Marietta Blvd. NW - ATL | 4425 | Fax sent 2017-10-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/10/2017 12:00:00 AM |  | 10/9/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-25 | 2016-05-25 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3627 Bermuda Circle | 1800 | fax received 5/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/26/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The sewer gravity main was opened with the jet truck. The line will be cleaned, smoked, and inspected via CCTV to assess for structural defects. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-09-20 | 2015-09-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1576 Nantahalla Court Atlanta | 4180 | Notification received on September 21, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/20/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 14:20 hours, when a crew plugged the opening end of the line to stop the leak, set up the vactor truck to vacuum the flow preventing any other manholes' from spilling over, made a request for the repair and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-24 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift Station in Eastman, GA. | 15000 |  | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 1/27/2017 10:00:00 AM | Ocmulgee | 1/24/2017 12:00:00 AM | 2017-01-24 | 2018-01-24 | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Lift Station overflow resulting from 4" rainfall within short timeframe. | Emergency action requirements for major spill initiated on 1/24/2017 by facility personnel. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-01-30 | 1 | 1 | 0 | 1 | 1 | 0
2016-01-25 | 2016-01-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 90 Abington Court, NW | 10 | fax received 1/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-06 | 2017-07-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 37 Delmoor Ct. NW - ATL | 130 | Fax received 2017-07-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/7/2017 12:00:00 AM |  | 7/6/2017 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Creekside Subdivision, Lagrange, GA | 133000 | Fax received on 12/25/2015. Received a second fax on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream | Shoreline | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/25/2015 12:00:00 AM | Chattahoochee | 12/25/2015 12:00:00 AM | 2015-12-25 |  | 1 | Dixie Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Lift station downstream flooded due to heavy rainfall. Water got into the electrical panel and generator causing the lift station to shut down. | Water receded, electrical system dried and fuses were replaced. Electricity was restored, allowing the lift station to once again become functional. Once flooding subsidede and repairs were made to the flood-damaged lift station, flows recovered to normal conditions. I/I investigations will also continue in this area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 1 | 1 | 0 | 0 | 0
2015-11-28 | 2015-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1354 Memorial Drive, SE | 13305 | fax received 11/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  | Kim Hembree |  | Kim Hembree | 11/29/2015 12:00:00 AM |  |  | 2015-11-29 | 2016-12-20 | 0 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 |  | 2015-11-30 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-17 | 2017-01-17 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawrenceville | 180 Gwinnett Dr. and Stone Mountain St. - Lawrenceville | 5422 | Fax received 2017-01-17 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/17/2017 12:00:00 AM |  | 1/17/2017 12:00:00 AM |  |  | 1 | Pew Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products - as well as grease. | Washed down the impervious surface and collected run-off. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-16 | 2016-08-16 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12. Lab results indicated 25.2 mg/L BOD with a flow of 1.09 MGD. | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 25.2
2017-07-28 | 2017-07-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3714 Roswell Rd. NE | 40 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/29/2017 12:00:00 AM |  | 7/28/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 1376000 | Verbal notification received 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain event |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-17 | 2016-05-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 241 Scott Street, NW | 2460 | fax received 5/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/18/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-16 | 2018-04-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3099 Panther Trl. - Atlanta | 300 | Fax sent 2018-04-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/17/2018 12:00:00 AM |  | 4/16/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 1267 | fax recieved 11/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and possible collapsed mainline | Bypass pump put in place |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-16 | 2017-05-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4010 Moffat Court, Decatur | 20 | Notification received on May 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/16/2017 12:00:00 AM |  |  |  |  | 0 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | The problem was corrected at 10:45 hours when a crew pressure washed the 12" sewer main 300ft upstream, cleared the blockage at 150ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-18 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-19 | 2017-07-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 1176 Lloyd Dr., Forest Park Manhole - 2198151 | 2600 | Fax received on 07/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 7/20/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-20 | 0 | 1 | 1 | 0 | 0 | 0
2016-07-20 | 2016-07-20 | Rome, City of (Rome WRF) | Floyd |  | Armuchee Community on Lindsey Road approx 800 feet west of Martha Berry Highway and 3471 Martha Berry Highway | 8000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream | Stream | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 7/21/2016 12:00:00 AM | Coosa |  |  |  | 0 | Big Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to root mass in the sewer main | Dislodged the root mass. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-07-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-21 | 2017-07-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 4306 North Peachtree Road, Chamblee | 40 | Notification received on July 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 7/21/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 6-inch cleanout spilling into a storm drain due to a defective lateral. | The problem was corrected at 18:32 hours when a first responder crew repaired the 6-inch right-of-way cleanout to stop the spill and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-09 | 2017-01-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall St., SE, ATL | 430 | Fax received on 01/10/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/10/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-08-25 | 2015-08-25 | Cobb County (RL Sutton WRF) | Cobb |  | 5329 Whitehaven Park Lane | 3000 |  | Raw Sewage | Wastewater Regulatory Program | GA0026140 | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/25/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of structural damage in sewer main causing the manhole to overflow into a tributary of Nickajack Creek. | The Water System was notified at 2:45 and our crew stopped the overflow at 3:45 P.M. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-02 | 2015-04-02 |  | DeKalb | Stone Mountain | 924 Belle Glade Drive, Stone Mountain | 50 | Notification received on April 6, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/2/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken main | The problem was corrected at 16:40 hours when the contractor's crew stopped pressure washing the creek crossing main line, TV the main to find the problem and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-06 | 2016-04-06 | Newnan Utilities (Mineral Springs WPCP) |  | Coweta | 107 Southfeild Dr. on an out fall trunk line. | 7820 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/6/2016 12:00:00 AM | Flint |  |  |  | 0 | White Oak Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-30 | 2016-08-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 55 | fax received 8/31/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/31/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-18 | 2016-07-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2020 Highview Road, SW | 760 | fax received 7/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/19/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-23 | 2018-05-23 | Columbus Water Works (South WRF) | Muscogee | Columbus | 5330 Burbank Street, Columbus | 16337 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Mill Branch Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Once the rain subsided and flow returned to normal the overflow stopped. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-21 | 2017-03-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 92 Piedmont Ave. SE - ATL | 320 | Fax received 2017-03-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/22/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Kingsland, City of (Kingsland WPCP) | Camden | Kingsland | Two manholes located adjacent to Clarks Bluff lift station, two manholes located adjacent to Gross Road lift station, fifth manhole located at Underwood Subdivision. | 0 |  | Raw Sewage | Coastal District | GA0037800 | Collection System | Stream | Stream | Natural Disaster |  | Denali Trimble | Denali Trimble | Brett Berry | 9/18/2017 12:00:00 AM | Saint Mary's | 9/19/2017 12:00:00 AM | 2017-09-19 | 2018-09-18 | 1 | St. Marys | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 |  | 1 | Hurricane Irma. | N/A | e688d4d4-470a-4ee6-aee6-8057ba640fec | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | e688d4d4-470a-4ee6-aee6-8057ba640fec | 2017-09-18 | 1 | 1 | 0 | 0 | 0 | 0
2017-11-08 | 2017-11-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 815 Alpine Way, Forest Park Manhole: 2217067 | 3375 | Fax received on 11/09/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 11/9/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Veteran Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage, and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-13 | 0 | 1 | 1 | 0 | 0 | 0
2015-07-24 | 2015-07-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 360 Englewood Avenue | 200 | fax received 7/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment Failure |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-06 | 2018-09-06 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 4720 Odum Lake - Cumming | 2 | Email received 2018-09-07 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/7/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage, gravel | Jetted lateral, placed lime around cleanout. Camera, gravel was found. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2017-06-23 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1669 Spring Street | 620 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/23/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Silt | Repair Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-30 | 2015-06-30 | Athens-Clarke County (Cedar Creek WPCP) |  | Clarke | 120 Tremont CT | 788 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/1/2015 12:00:00 AM | Oconee |  |  |  | 0 | un-named tributary to Middle Oconee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper and Rags Clogged Pipe | Rod Sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-19 | 2018-03-20 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 100 Renee Drive Tallapoosa | 5600 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/20/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Unnamed tributary to Tallapoosa River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Outage extreme weather | Power was restored | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-22 | 2015-01-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 2820 Pierce Drive S, MH 82002 | 320 | REC FAX 1/22/2015. REC EMAIL 1/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/22/2015 2:45:00 PM | Ocmulgee | 1/22/2015 12:00:00 AM |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. There are no commercial sources of grease upstream from this location and residential grease is not regulated. | Debris will be removed and the affected area is being disinfected with lime. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2016-10-29 | 2016-10-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 978 Grand Ave, NW, Atlanta | 1650 | Fax received on 10/30/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Pump Station | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/30/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction | The crew repaired by-pass pump to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (West Area CSO) | Fulton | Atlanta | West Area WQCF | 2030000 | EPD received verbal notification from Kris Garcia on 11/02/2015 at 10:45am | Primary Effuent | Wastewater Regulatory Program | GA0038644 | WWRF | Stream |  | Unknown |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm induced hydraulic overload |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-07 | 2015-07-07 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Between West Charlton and West Hancock | 10001 | ERT contacted 7/07/2015. CTS No. 77252 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/7/2015 12:00:00 AM | Oconee |  | 2015-07-07 | 2016-06-08 | 1 | Fishing Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Erosion of dirt under the pipe | Dirt mounded under the pipe. Pipe patched until new pipe can be installed. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-09 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2016-03-07 | 2016-03-07 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 510 East Montgomery St | 2250 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Roots |  |  | Dagny Pariani | Dagny Pariani | 3/8/2016 12:00:00 AM | Oconee | 3/8/2016 12:00:00 AM |  |  | 1 | Tanyard Branch stream | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer line caused the pipe to break | Rodded the sewer line, cut the roots, and treated the line with copper sulfate. Raked the soil around the spill and applied lime. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2016-11-23 | 2016-11-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4033 Stovall Ter., NE, ATL | 1220 | Fax receoved on 11/26/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/26/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. DRY LAND SPILL> | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-28 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 3100 Block of Falling Leaf | 7380 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-05-11 | 2018-05-11 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 250 Orton Street, Tallapoosa | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Katie Meade | 5/11/2018 12:00:00 AM | Tallapoosa |  |  |  | 1 | Greene Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in a gravity sewer line caused multiple manholes to overflow | Blockage was removed and flow restored. Fast reaction time reduced environmental effects and contained most of the overflow. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-21 | 1 | 0 | 0 | 0 | 0 | 0
2017-04-11 | 2017-04-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1557 Habershal Dr. NW - ATL | 50 | Fax Sent 2017-04-12; Fax not received. Delivered 2017-05-08. | Raw Sewage |  | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/8/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-22 | 2017-04-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3360 Mountain Drive, Decatur | 750 | Notification received on April 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/26/2017 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:00 hours when a crew pressure washed the 12 inch sewer main between manholes 523ft, clearing the blockage at 272ft and restoring steady flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-27 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-02 | 2018-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1269 E Rock Springs Rd. NE - Atlanta | 128 | Fax sent 2018-08-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/3/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-08 | 2015-02-09 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | WWTP effluent to unnamed ditch to the Seventeen Mile River to the Satilla River Basin. | 4400000 |  | Secondary Effluent | Coastal District | GA0024431 | WWTP | Ditch | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/16/2015 9:00:00 AM | Satilla | 2/16/2015 12:00:00 AM | 2015-02-16 |  | 1 | Seventeen Mile River to the Satilla River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | BOD results for the 2/8/2015 sample: 26 mg/L - classified as a major spill for the 24 hour flow period. The sample was properly preserved and the 5-day test was started on 2/11/2015 with the results posting on 2/16/2015. The cause of the spill was caused by a faulty check valve that was stuck open between the gravity thickener and the effluent wet well of the sand filter. | The check valve has been repaired and an air gap will be installed at the gravity thickener end of the force main to prevent a re-occurrence of this issue. Up and down stream sampling began on 2/16/2015 as per spill protocols and will be reported over the next year. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-02-23 | 1 | 1 | 1 | 0 | 0 | 0
2018-03-24 | 2018-03-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3899 Misty Lake, Ellenwood GA 30294 | 1920 | manhole 15-043-s159 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/26/2018 10:14:00 AM | Ocmulgee | 3/24/2018 12:00:00 AM |  |  | 1 | Blue Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks and asphalt | pressure washed manhole |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-17 | 2015-08-17 | Winder, City of (Marburg Creek WPCP) | Barrow | Winder |  | 9432 | Received fax on 08/18/2015. | Raw Sewage | Wastewater Regulatory Program | GA0023191 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/18/2015 12:00:00 AM |  | 8/18/2015 12:00:00 AM |  |  | 1 | Tributary to Beech Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A split in the sewer force main from the Clay Howard Sewer Pump Station. When the pump at Clay Howard Sewer Pump Station cycled on the increased pressure in the sewer force main caused sewer to leak out of the split in the pipe. | Immediately turned off the sewer pump station pumps. Used a vacuum truck to pump out the lift station wet well and transport the sewer to a point in the sewer collection system where it could be dumped into a manhole and gravity Cedar Creek Wastewater Treatment Plant. Dug down on the sewer force main and replaced the section of pipe that was split. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER
2018-05-15 | 2018-05-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2301 Mountain Industrial Boulevard, Tucker GA 30084 | 2750 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Other |  |  |  | Dillon Rodenbaugh | 5/16/2018 11:28:00 AM | Ocmulgee | 5/15/2018 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flow monitor device blocked sewer to downstream invert | Vacuum manhole and removed the flow monitor device |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 |  | 2018-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-28 | 2018-08-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Fowler St. NW - Atlanta | 456 | Fax sent 2018-08-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | 3rd party contractor |  |  |  | Alys Hannum | 8/29/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Private contractor damaged mainline while digging |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-27 | 2017-11-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4714 Edwina Ln. SW - ATL | 100 | Email sent 2017-11-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/28/2017 12:00:00 AM |  | 11/27/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-10 | 2015-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way, S.W. | 665 | Fax received on 08/11/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/11/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Hydraulic pressure cleaner was used to contain spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-04 | 2018-09-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4300 Northside Dr. NW - Atlanta | 1112 | Fax sent 2018-09-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 |  | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-21 | 2016-09-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2746 Clairmont Road Atlanta | 5700 | Notification received on September 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/21/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected on September 21, 2016 at 17:20 hours when a crew rodded and pressure washed the 8" sewer main, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-27 |  | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 249 Farlow Drive | 5050 | ERT contactd 7/27/2016. CTS No. 80402 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/27/2016 12:00:00 AM |  |  |  |  | 1 | Storm Drain to Cedar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken pipe main |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER
2017-04-11 | 2017-04-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1560 Habershal Dr. NW - ATL | 1300 | Fax received 2017-04-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/12/2017 12:00:00 AM |  | 4/11/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-07 | 2016-12-07 | Cobb County Water System | Cobb |  | 2315 Dallas Hwy | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-04 | 2018-03-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 601 Hemlock Cir. SE - ATL | 100 | Fax sent 2018-03-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a by=pass pump to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Gum Swamp Lift Station in McRae-Helena | 9000 | Isolated spill. | Raw Sewage | Southwest District | GA0048674 | Lift Station |  |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma and generator failure. | Dirt embankment created to control spill and hold in place. Generator was repaired Wednesday, September 13. Spill was contained in area and cleaned. Lime was applied liberally. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2017-03-29 | 2017-03-29 | Gwinnett County (Yellow River WPCP) | Gwinnett | Liliburn | 596 Johns Way - Liliburn | 1650 | Fax received 2017-03-29 | Raw Sewage | Wastewater Regulatory Program | GA0047911 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/29/2017 12:00:00 AM |  | 3/29/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Beaver Ruin Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper and other products; Grease | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-07 | 2016-10-08 | Southern States Phosphate & Fertilizer Company | Chatham | Savannah |  | 0 |  | Unknown | Coastal District | GA0002437 | N/A | Basin |  | Other |  | Cliff Lewis | Cliff Swiger | Cliff Swiger | 10/10/2016 2:49:00 PM | Savannah |  |  |  | 0 | Savannah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Matthew. Facility reported that Kayton Canal had flooded and the deluge encroached upon the facilities grounds including its discharge system. The outflow was surface water and the facility was not in operation at the time of the flooding. |  | 37abf76e-1c4e-11e1-9fd5-12313b0cb679 | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4706 Wieuca Rd. NE - Atlanta | 700 | Fax sent 2018-03-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/14/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-08 | 2018-01-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3803 Gothic Elm Court Decatur GA 30034 | 325 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/8/2018 4:39:00 PM | Ocmulgee | 1/8/2018 12:00:00 AM |  |  | 1 | Shoal Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4" DI lateral leaking | Replaced damaged ternco |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Darro Patterson |  | Dekalb Co Dept. Watershed Management
2018-02-26 | 2018-02-26 | Savannah Pines Mobile Home Park | Chatham | Garden City | 1518 Dean Forest Road, Garden City, GA | 13000 | Initial email and full report received 3/1/2018. | Raw Sewage | Coastal District | GAG550127 | Lift Station | Canal | Canal | Equipment failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 3/1/2018 12:00:00 AM | Ogeechee | 3/1/2018 12:00:00 AM |  |  | 1 | Horshoe Canal to Salt Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Lift station onsite at the WWTP had both pumps fail causing the station to overflow into the canal. | Repaired one pump and ordered a replacement for the other. Pumped out the lift station and cleaned it of debris. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-03-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Franklin Management | 912-661-1139
2018-02-27 | 2018-02-27 | Clayton County (Northeast WPCP) | Clayton | Forest Park | 688 Brook Wood Drive, Forest Park | 2680 | Fax sent 2018-02-28 | Raw Sewage | Wastewater Regulatory Program | GA0020575 | WWTP | Stream |  | Debris |  |  | Hsin Yeh |  | 2/28/2018 12:00:00 AM |  |  |  |  | 1 | Jester Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generate for additional work to determine cause. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-07 | 2017-12-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 40 Perimeter Center East Atlanta GA 30346 | 123495 | Letter states 123495 gallon spill. SSO report says 123475 gallons | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/7/2017 7:08:00 PM | Ocmulgee | 12/7/2017 12:00:00 AM | 2017-12-14 |  | 1 | North Fork Nancy Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | creek crossing 12" pipe broke into creek | Repair crew on site making necc |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-11 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Cody Dallas |  | DEKALB CO-SNAPFINGER CR WPCP
2017-11-10 | 2017-11-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 532 Cleveland Av. SW - ATL | 860 | Fax sent 2017-11-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 11/11/2017 12:00:00 AM |  | 11/10/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-08 | 2017-12-10 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 20 Arbacoochee Street, Oak Village Lift Station | 63000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/11/2017 12:00:00 AM | Tallapoosa |  |  |  | 0 | Goose Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Extreme weather power outage that shut down our city, with emergency or back up power preventable | Power restored, treated area with hydrated lime and clean up persistent | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2940 East Lindsay Dr., Columbus, GA | 6784 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Lindsay Creek. | Once the rainfall subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn | St. Simons Island | 514 Delegal Street, St. Simons Island | 10000 |  | Raw Sewage | Coastal District | GA0021521 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2016 9:00:00 AM | Satilla | 10/27/2016 12:00:00 AM | 2016-10-27 |  | 1 | St. Simons Sound | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Lift Station (#2009) power failure due to Hurricane Matthew. | Removed trees from lift station, restored power and restarted pumps, control flow with vaccon trucks until wet well was restored back to normal. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-31 | 1 | 1 | 0 | 0 | 0 | 0
2015-02-04 | 2015-02-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3700 Roswell Road, NE | 300 | fax received 2/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/5/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-07 | 2017-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1455 Fairmont Ave. NW | 700 | Fax sent 2017-11-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/8/2017 12:00:00 AM |  | 11/7/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-07 | 2016-09-07 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 3579 Everson Road | 11054 | fax received 9/07/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/7/2016 12:00:00 AM |  |  | 2016-09-08 |  | 1 | Unnamed Tributary of Jacks Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Wipes, paper, and other products | raked area and spread lime. placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-09 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-11-07 | 2016-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2636 Martin L. King Jr., Dr., SW, Atlanta | 5180 | Fax received on 11/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/8/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the main line. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Banks |  | ATLANTA, CITY OF
2015-12-15 | 2015-12-15 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Hwy 1 Norths | 300 | Voice message left on 12/16/2015. Haven't confirmed information yet. | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Ditch |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/16/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Drainage Ditch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease and debris | Cleaned out with sewer jetter | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO
2018-01-09 |  | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant. | 70000 | The local health department was notified on 1/19/18; spill signage posted at the effluent on 1/19/18; public notification was posted at City hall on 1/19/18; and public notification was also published in The True Citizen on 1/24/18. Spill superseded by second spill notification provided to EPD on 1/30/18. Stream monitoring initiated under 1/16/18 spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/18/2018 12:00:00 AM | Savannah | 1/19/2018 12:00:00 AM |  |  | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Inadequately treated wastewater was discharged at the wastewater treatment plant effluent due to new mixers (as part of the treatment plant upgrades) installed within the aeration basin malfunctioned. The facility discharged water with a BOD concentration greater than 50% of the weekly average. This was discovered as a result of the BOD composite sample collected between Jan 9-10, 2018. | Signage will be placed at the location of the spill into State waters at the effluent discharge point of the WWTP. The local health department and local media are being notified. Upstream and downstream monitoring is being initiated to determine in there are any immediate or lasting harmful effects from the discharge in the stream. Monitoring is to be implemented for 1 year. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2018-02-23 | 1 | 1 | 1 | 0 | 0 | 0
2017-02-20 | 2017-02-20 | Pooler, City of (Bloomingdale Regional WPCP) |  |  | 800 Winskie Rd., Pooler, GA, 31322 | 1300 | Initial call to Coutney Huggins on 2/20/17, full report emailed 2/23/17. | Other | Coastal District | GA0047066 | WWTP | Canal |  | Equipment failure |  |  | Dagny Pariani | Dagny Pariani | 2/20/2017 12:00:00 AM | Savannah | 2/20/2017 12:00:00 AM |  |  | 1 | Hardin Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A faulty solenoid in an air valve allowed MLSS to taint treated effluent with traces of mixed liquor. | Replaced the solenoid. Used a vac truck to remove ~1000 gallons from the canal. Recirculated the effluent tank through the headworks until clean effluent was achieved. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Carrollton, City of | Carroll | Carrollton | Carrollton Greenbelt/Cottage Hill 136 Manor Way - Carrollton | 3000 | Telephone call received on 01/23/2017; letter received on 02/01/2017. | Raw Sewage | Wastewater Regulatory Program | GAJ020126 | Collection System | Ground |  | Unknown |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown | The crew raked, and applied lime and hay to the affected areas. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2237 Lake Haven Drive, (MH 69387, 69389, 69392). | 19400 | Fax received on 12/23/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Basin |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/23/2015 12:00:00 AM | Upper Ocmulgee |  | 2015-12-26 | 2016-11-29 | 1 | Lake Tobesofkee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause was hydraulic overload and high lake levels. The service area received 3.18 inches of rainfall on December 21 and 22. | Debris was removed from the area and the affected area was disinfected with lime. The MWA has placed a by-pass line for the force main to be used during heavy rainfall events. Also a project to install a new force main for the Glen Echo Lift station has begun. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2015-02-09 | 2015-02-09 |  | Richmond | Augusta | 1113 River Ridge | 8790 | fax received 2/10/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 2/10/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Rock Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2016-05-25 | 2016-05-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 675 Metropolitan Parkway, SW | 84 | fax received 5/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/26/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-16 | 2015-09-16 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/14/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 25.4 mg/L on 09/16/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-28 | 2017-07-28 | Cobb County Water System | Cobb |  | 1451 Bolingbrook Rd | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/28/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-28 | 2018-06-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 1516 Summerset drive, Dunwoody GA 30338 | 4360 | manhole 18-375-s257 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/3/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Pressurewashed from manhole 18-375-s257 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | Manhole near the Carlton Woods lift station | 36000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | WWTP | Stream |  | Power failure |  |  | Hsin Yeh | Hsin Yeh | 1/23/2017 12:00:00 AM |  |  |  |  | 0 | Ochlocknee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage at lift station caused by a major thunderstorm |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-27 | 2017-06-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1266 Plaza Ave SW - ATL | 4140 | Fax received 2017-06-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/29/2017 12:00:00 AM |  | 6/27/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 161 Hood Circle, Decatur | 3846 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 13:42 hours when the heavy rain stopped and normal flow was restored. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2780 Fairlane Drive, SE | 575 | fax received 1/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-04 | 2015-05-04 |  | DeKalb | Clarkston | 3954 Memorial College Ave., Clarkston | 1600 | Notification received on May 6, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/4/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek Tributary "D" | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:30 hours when a crew rodded the 8" sewer main 150ft upstream, clearing the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-05-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-28 | 2017-11-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2892 Eastwyck Circle, Decatur, GA 30032 | 2600 | Four notices of spill placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/28/2017 2:21:00 PM | Ocmulgee |  |  |  | 1 | Shoal Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole 15-138-s059 spilling into Shoal Creek due to grease blockage | Pressure washed the 8" line upstream a total of 100ft from m/h #15-136-s058, hit and cleared grease blockage at 38 ft to restore flow |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-29 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Lamonica Brown |  | Dekalb County Department of Watershed Management
2018-05-28 | 2018-05-28 | Gray, City of (Wolf Creek WPCP) | Jones | Gray | Stone Brook Sd | 1500 |  | Raw Sewage | West Central District | GA0026085 | Lift Station | Ground | N/A | Power failure |  | Jody Sapp | Jody Sapp | Jody Sapp | 5/29/2018 12:00:00 AM | Oconee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | tripping of breaker (electrical) | electrician checked lift station to ensure proper operation | 43bc988a-eb6e-11e0-b8d8-000c29971acc | 43bc988a-eb6e-11e0-b8d8-000c29971acc | 43bc988a-eb6e-11e0-b8d8-000c29971acc | 2018-06-20 | 1 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 2017-07-18 | Covington, City of (Covington WRF) | Newton | Covington | Blackwell St. Sewer Crossing - Covington | 4900 | Email received 2017-07-18 | Raw Sewage | Wastewater Regulatory Program | GAJ020055 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/18/2017 12:00:00 AM |  |  |  |  | 1 | Dried Indian Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fell across elevated sewer line. | Repaired broken line. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-13 | 2016-01-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4024 Blanton Avenue, SW | 19530 | fax received 1/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/14/2016 12:00:00 AM |  |  | 2016-01-14 | 2017-02-03 | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 |  | The crew installed a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-23 | 2015-01-24 |  | Lowndes | Valdosta | 1834 Remer Lane | 171000 | Verbal notification from John Waite w/ the City of Valdosta received 3:00pm on 1/23/2015. Email follow-up from City sent 1/24/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/23/2015 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-13 | 2017-01-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1206 Oak Knoll court, Lithonia | 1420 | Notification received on January 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/13/2017 12:00:00 AM |  |  |  |  | 0 | Swift Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 15:20 hours when the crew pressure washed the sewer main 110 ft downstream, cleared the blockage at 100 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Manhole at Lee street Lift Station | 4200 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cornelia Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Overflow due to Heavy Rains |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-12 | 2015-02-12 |  | Gwinnett | Norcross | 1635 Pirkle Road | 3300 | fax received 2/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/12/2015 12:00:00 AM |  |  |  |  | 1 | Sweetwater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 8" pipe | Repaired 8" pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-05-22 | 2018-05-22 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Manhole #8907-6264 Malone Rd, Douglasville GA 30134 | 6000 |  | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Stream | Debris |  |  | Juan Robles | Juan Robles | 5/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Huey Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to roots, bricks, and construction debris in the line. | -Vac Trucks crews were dispatched to the site and were able to clear the blockage. -Crews cleaned and disinfected the area around the manhole where the pill occurred. -Signs were posted in the area to notify residents and the public of the spill. -Notification given to EPD, the Health Department, and local media. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-11 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-02 | 2018-01-02 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 6711 Church St - Riverdale | 2200 | Fax sent 2018-01-03 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Paul Moisan | 1/3/2018 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-02 | 2018-01-02 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 353 Stevens Drive | 2500 | Phone call received 2018-01-02 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Stream |  | Pipe failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 1/2/2018 12:00:00 AM |  |  |  |  | 1 | Local Waterways - Did not reach State? | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ruptured force main | Damaged line was repaired and powdered lime was applied. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-13 | 2016-04-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 359 West Lake Avenue, NW | 58 | fax received 4/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/14/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-29 | 2016-07-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1765 Pryor Road, SW | 623 | fax received 8/01/2016. This is a spill from a private lateral. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/1/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This is a spill from a private lateral. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-02 | 2017-01-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 824 Fulton Ave., Columbus | 32555 | Telephone call and fax received on 01/03/2017 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Double Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Double Branch Creek. Columbus received 2.19 inches of rain on 01/01/2017, and 4.59 inches of rain on 01/02/2017. | Once the rain subsided and flow returned to normal, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2016-07-05 | 2016-07-05 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 240 Flint River Road, Jonesboro Manhole 2216239 | 750 | Fax received on 07/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 7/5/2016 12:00:00 AM | Flint |  |  |  | 1 | Kendrick Waters | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots. | Blockage was cleared and flow was returned back to normal. Lines will be televised and root cut and problems repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-07 | 0 | 1 | 1 | 0 | 0 | 0
2017-03-08 | 2017-03-08 | Cobb County Water System | Cobb |  | 1940 County Services Parkway | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8 inch Clay Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-11 | 2017-01-11 | Fulton County MS4 | Fulton |  | 225 Ledgemont Court | 3300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-19 | 2018-05-19 | Adairsville, City of (North WPCP) | Bartow |  | Manhole in street at 127 Martin Luther King Jr. Drive | 2880 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Wet weather |  | Eric Dykes | Kathy Lewis | Katie Meade | 5/22/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed Tributary to Oothkalooga Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line backed up and spilled from manhole after heavy rain event. We suspect major inflow and infiltration contributed to a capacity overload in the collection system. | City of Adairsville construction personnel found the overflowing manhole at 4 am on 5/19/18. When it stopped raining, the water receded and stopped overflowing from the clean out. City sewer crews will investigate the lines through camera inspection throughout the week. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-23 | 1 | 0 | 0 | 0 | 0 | 0
2017-08-11 | 2017-08-11 | Marietta (City of)- Sewers | Cobb | Marietta | 960 Sourwood Cir | 2100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/14/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Marietta Wate rpersonnel quickly set up a pump around to stop leakage and allow for a repair of the failing pipe segment. The crew will conitnue to monitor sewereasements so that issues such as this are found and repaired quickly. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Tifton, City of (New River WPCP) | Tift | Tifton | Southside lift station on golden road, and the manhole u pstream at 61 TC Gordon Road. | 250000 | A telephone call and email were received on 09/12/2017. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Lift Station | Stream | Shoreline | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/12/2017 12:00:00 AM | Suwannee | 9/12/2017 12:00:00 AM | 2017-09-12 |  | 1 | Cow House Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | The cause was due to an electrical failure at the lift station due to Hurricane Irma. | Once power was restored (after 8 hours), flow in the lift station returned to normal. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-13 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-24 | 2017-03-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 99 Johnson Rd. NW - ATL | 50 | Fax received Saturday 2017-03-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 3/25/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown at this time. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-03 | 2016-06-03 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Country Club Drive, Douglasville | 880 | Email received on 06/03/2016; fax received on 06/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Vandalism |  |  | Paul Moisan | Paul Moisan | 6/3/2016 12:00:00 AM |  | 6/3/2016 12:00:00 AM |  |  | 1 | Tributary A to Tiger Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism - Golf course bunker rake found in manhole. | VacCon crews were dispatched to the site and a jet truck was used to clean the line and clear the blockage. Crews cleaned and disinfected the area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-14 | 2018-03-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 33 Edgewood Ave. SE - Atlanta | 579 | Fax sent 2018-03-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/15/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and a collapsed mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-14 | 2016-11-14 | Newnan Utilities (Wahoo Creek WPCP) | Coweta | Newnan | Corner of Third St. and Hollis Hights | 250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/14/2016 12:00:00 AM | Flint |  |  |  | 0 | Mountain Creek Drainage basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 6in servicetap that feeds a small apartment building was broken where it crossed a torm sewer pipe. | The facility dug up the broken section of pipe and replace it. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-07 | 2015-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2920 ML King, Jr. Drive, SW | 5150 | FAX received 6/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-09 | 2018-06-09 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Peachtree Corners | 3280 Green Pointe Pkwy - Peachtree Corners | 8270 | Fax sent 2018-06-10 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 6/10/2018 12:00:00 AM |  | 6/9/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris - wipes, paper, and other products | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-07 | 2016-08-07 | Lowndes County (South Regional WPCP) | Lowndes |  | Blue Lake Pump Station | 25000 | Verbal notification received 8/08/2016. This is an overflow to a private pond. | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Collection System | Other |  | Equipment failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/8/2016 12:00:00 AM |  |  |  |  | 0 | Private Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical failure. "Heater" breaker tripped. | Bypass installed and repair made to electrical "heater." | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | LOWNDES COUNTY
2017-05-13 | 2017-05-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3440 Boulder Park Dr. SW - ATL | 1460 | Email received 2017-05-15 CORRECTION to spill volume received 2017-10-31: previous volume 1245 gallons | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/15/2017 12:00:00 AM |  | 5/13/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris and grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-10 | 2017-11-10 | Cobb County Water System | Cobb |  | 5011 White Blvd. | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clay Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System stopped spill at 2:20 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-25 | 2018-06-25 | Cobb County Water System | Cobb |  | 3040 Wayward Dr. NE | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/25/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morgan Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1300 Block of North Ashley Street | 114750 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-08-14 | 2015-08-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 337 Elizabeth Street, NE | 1028 | Fax received on 08/15/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Hydraulic pressure cleaner was used to contain spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-20 | 2017-12-20 | Cobb County Water System | Cobb | marietta | 2001 Old Concord Road | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Reginald Williamson | Reginald Williamson | 12/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-20 | 2017-12-20 | Cobb County Water System | Cobb | Marietta | 2001 Old Concord Road | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Reginald Williamson | Reginald Williamson | 12/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-30 | 2017-09-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3724 Eagles Beek Circle, Lithonia | 100 | Notification received on October 4, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 9/30/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor was in the process of replacing a 48" by-pass sewer main. | The problem was corrected at 10:15 hours when the contractor completed the removal of the 48" by-pass sewer main and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-05 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-20 | 2016-06-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 3575 Howell Ferry Road | 3639 | fax received 6/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/20/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris (rags and other flushables) | Raked area, placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-08 | 2015-01-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | 1/09/2015: Voicemail to EPD by Kris Garcia stating a TSS violation had occurred. Telephone and email confirmation on 1/12/2015. | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Unknown |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This is a major outfall spill due to an exceedence of TSS. The TSS limit is 22.5 mg/L and the reported value during the major spill was 69 mg/L. Volume = 78,700,000 gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-03 | 2016-02-03 | Tifton, City of (New River WPCP) | Tift | Tifton | manhole located at 1392 Whiddon Mill Road, Tifton, GA | 670 | Voice mail received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Reservoir | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | Agrirama Lake | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | mitigated by hydrated lime). | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-05 | 2017-09-05 | Cobb County Water System | Cobb |  | 4050 Jordan Lake Dr. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in Manhole | stopped spill and spread lime around the manhole | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-08 | 2016-09-08 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 200 Zatella Ln., Athens | 653 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Oconee | 9/8/2016 12:00:00 AM |  |  | 1 | Trail Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags, grease, and roots clogged the sewer line resulting in a manhole overflow | Cleared the clog, rodded the line, cleaned and limed the area. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Govenment of Athens-Clarke County | 706-613-3481 x237
2015-02-11 | 2015-02-11 |  | Cobb |  | 886 Banford Court N.E. | 530 | No known adverse environmental effects occurred as a result of this spill. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/11/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cobb County Water System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The Water System was notified at 7:01 a.m. and the crew stopped the overflow at 8:30 a.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-07 | 2018-05-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 7134 Maddox Rd, Lithonia 30058 | 484089 | List Station 8 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Power failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/8/2018 6:08:00 PM | Ocmulgee | 5/10/2018 12:00:00 AM |  |  | 1 | Swift Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Power went down at lift Station 8 | Robert Carthage turned power on manually to stop spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-05 | 2017-01-05 | Cobb County Water System | Cobb |  | 2352 Goodwood Drive | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-09 | 2017-01-09 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | 900 West Water Street | 10 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Equipment failure |  | Brian Koehler | Kathy Lewis | Brian Koehler | 1/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Soque | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station Malfunction | Midway Electric worked on the controls and got things running | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-07 | 2016-10-07 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 2748 Porter Drive | 6738 | fax received 10/07/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/7/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Sweetwater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage from paper products | Raked area and spread lime. Placed signs at spill and affected waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-05-19 | 2018-05-19 | Adairsville, City of (North WPCP) | Bartow |  | 105 Holcomb Drive, Adairsville | 1440 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Wet weather |  | Eric Dykes | Kathy Lewis | Katie Meade | 5/22/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed Tributary to Oothkalooga Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line backed up and spilled from clean out after heavy rain event. We suspect major inflow and infiltration contributed to a capacity overload in the collection system. | City of Adairsville construction personnel found the overflowing manhole at 11:30 am on 5.19.18. When it stopped raining, the water receded and stopped overflowing from the clean out. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-23 | 1 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2650 Laurens Circle, SW | 6510 | fax received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disjointed pipe | pipe repaired temporarily |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-21 | 2017-02-21 | Cobb County Water System | Cobb |  | 1918 Martin Rd. | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Ollie Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8" Clay Main | Spread Lime in Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-06 | 2017-12-06 | Cobb County Water System | Cobb |  | 154 Silver Mine Trail | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spill stopped at 10:17 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1300 Block of Brookwood and North Lee | 45000 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-07-27 | 2015-07-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3806 Dedee Court, Tucker. | 920 | Notification received on July 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 7/29/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary of Peachtree Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage. | The problem was corrected at 13:30 hours when the crew rodded the line to restore flow followed by pressure washing 400 feet of line. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-07-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-29 | 2018-06-29 | BASF Corporation (McIntyre) | Wilkinson |  |  | 30000 | Chip explained that the spill was from a recycled process water pipe that consist of approximately 1.5% solids. Chip stated the spill travelled south a short distance on Leverette Road and through a culvert passed under and headed east through a heavily wooded area. I took photos of the culvert and small area of where the spill had travelled through the woods. I saw no white kaolin deposits so did not travel further into woods there. I asked Chip if he could generate an aerial view that shows the path the spill took to enter Bluff Creek and he stated he would do so and send to me. We then went to the upstream sample point on Bluff Creek (Lat 32deg 59min 08.50sec & Long 83deg 01min 51.26sec) the water there was naturally turbid and turbidity data on it has been provided in the 7.4.18 5-day follow-up email from Chip to EPD. | Primary Effuent |  | GA0003131 |  |  |  | Pipe failure |  |  | Shea Buettner |  | 6/29/2018 12:00:00 AM |  | 7/10/2018 12:00:00 AM | 2018-06-29 | 2018-07-02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0910 I received a text from the SWP and confirmed receipt at 0911. I spoke with Chip Brooks (BASF; chip.brooks@basf.com) who stated a ruptured pipe released an unknown amount of processed water/Kaolin mixture, impacting a nearby tributary. Contractors are being secured for remediation. No stressed aquatic life observed at this time. 1015 Chip stated, in house contractors and Clean Harbors are on site developing a remediation strategy including pH sampling, tributary inspections and removal of free product via vac truck. | Process Operations have been shut down, contractors are on site and the damaged pipe has been repaired. The product migrated approximately a quarter of a mile down stream near Fall Line Freeway. The release has been naturally contained by naturally occurring berms downstream. 1050 I called Tim Stuckey (BASF; 478-233-7881) for additional details and left a voice mail. Mr. Stuckey states four vac trucks are enroute for free product recovery. Two trucks will be actively pumping areas of highest concentration, while the other two offload the contaminated water back into the facilities processing system. 1545 Mr. Stuckey stated, approximately 30,000g (liquid) and 2,500 lbs (Kaolin) slurry mix was released from the ruptured pipeline. The spill has migrated to about a half mile downstream. Mr. Stuckey states ER contractors will continue recovery efforts, pH and stream monitoring throughout the weekend. Report being transferred to the East Central District. |  |  | ec78723e-818a-41f7-abda-40a99625de6f | 2018-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-20 | 2017-07-20 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Under sidewalk across from 2449 Towne Lake Parkway across the street from the Towne Lake Square shopping center. | 19500 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/21/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary of Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 Inch split on top of 12 inch force main line | Construction put on a 8 inch force main until construction replaced the section of line | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | 91 Pebble Creek Drive, Toccoa | 2000 | Notification received on February 8, 2018 via fax. | Raw Sewage | Wastewater Regulatory Program | GA0021814 |  |  |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 2/8/2018 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | City remove the blockage. The overflow was stopped at approximately 2:30 PM. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-08 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-07 | 2018-05-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 155 10th St. NE - Atlanta | 5 | Fax sent 2018-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/8/2018 12:00:00 AM |  | 5/7/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | RM Clayton Water Reclamation Facility - ATL | 48970000 | Written Report received 2017-06-28 | Primary Effuent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/28/2017 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | RM Clayton WRC had a passive bypass of the sand filters that resulted in a major spill of TSS to the Chattachoochee River. During the spill event, the facility was experiencing an ongoing hydraulic overload due to a severe storm event. Based on analytical results, the concentrations of TSS in the composite samples was 119 mg/L for June 20th and 38 mg/L for June 21st, both of which exceed the 25 mg/L limit specified in the permit. | Flows diverted to onsite storage, however there was insufficient supplemental storage to rapidly treat and discharge influent flows. The event ended when influent flow rates substantially declined. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-26 | 2017-03-26 | Rockdale County (Quigg Branch WPCP) | Rockdale | Conyers | 918 Jackie Court | 900 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/28/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ragging | Clean Pipe | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 199 Camden Road, NE | 1905 | fax received 10/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/11/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew made repairs to the mainline |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-18 | 2015-09-18 | Augusta, City of (J.B. Messerly WPCP) | Richmond | August/Fort Gordon | Fort Gordon, Back Hall, Dinning Facility #8 | 1000 | email and verbal notification received 9/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Ditch |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/29/2015 12:00:00 AM |  |  |  |  | 1 | Storm water drainage ditch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Unstopped sanitary sewer with water jet | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-828-7151
2018-06-04 | 2018-06-04 | Thomasville, City of (Oquina Creek WPCP) | Thomas | City of Thomasville | 1600 block of East Jackson Street | 15000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024082 | Collection System | Stream |  | Rags |  |  | Juan Robles | Juan Robles | 6/4/2018 12:00:00 AM | Ochlockonee |  | 2018-06-05 | 2019-06-05 | 0 | Good Water Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Gravity line partially blocked with rags. | Line cleared, flow returned to normal. Immediate area disinfected. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-22 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 406 Kemp Drive | 2400 | fax received 12/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/23/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-12-09 | 2015-12-09 | Americus, City of (Mill Creek WPCP) | Sumter | Americus | In the area of Willet's Brook, approximately 370 feet from the creek. | 9999 | Telephone call on 12/09/2015. Email received on 12/15/2015. | Raw Sewage | Wastewater Regulatory Program | GA0047767 | Collection System | Stream | Shoreline | Rags |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/9/2015 12:00:00 AM |  | 12/15/2015 12:00:00 AM | 2015-12-15 | 2016-12-26 | 1 | Willets Brook | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | It was determined that the spill was a result of a blockage in a 12" gravity sewer line. The line was found to be blocked with an accumulation of what appeared to be some type of tape and assorted industrial cloths. | A crew was dispatched to the manhole (adjacent to Willet's Brook). Upon arrival to the site, the discharge had stopped. A high pressure rodding machine was brought in to clear the line. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-23 | 0 | 1 | 0 | 1 | 1 | 0
2016-08-15 | 2016-08-15 | Columbia County (Crawford Creek WPCP) | Columbia | Grovetown | 712 Gallaway Lane | 4500 | Fax received 8/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/16/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Euchee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | "Unstopped sewer main with high pressure jet machine. Cleaned up the overflow. Posted sign. Follow up sewer main cleaning and CCTV inspection" |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2017-01-02 | 2017-01-03 | Columbia County (Little River WPCP) | Columbia | Evans | 4600 Blanchard Woods Drive - Evans | 10001 |  | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/5/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM |  |  | 1 | Euchee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Surcharge from excessive rainfall | Monitored area, searched area for inflow, posted signs, spread lime, follow up inspections, begin sampling. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-26 | 2018-05-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4893 Memorial Drive Stone Mountain GA 30083 | 200 | manhole 18-043-s305 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/29/2018 7:54:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek Tributary C | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Pressurewashed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-09 | 2015-11-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 243 Hemphill School Road, NW | 1200 | fax received 11/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-25 | 2018-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1620 Derry Ave. SW - Atlanta | 1200 | Original fax sent 2018-04-28 (late, missing information.) Update sent 2018-05-03. Final update sent 2018-06. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/28/2018 12:00:00 AM |  | 4/25/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | By-pass pump set up to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Cobb County Water System | Cobb |  | 6850 Mableton Parkway | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/10/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Unknown Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-16 | 2015-04-16 |  | DeKalb | Atlanta | 1635 Sugar Downs Court, Atlanta | 4980 | Notification received on April 28, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/16/2015 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 19:43 hours when a crew rodded the 8" sewer main, cleared the grease blockage ta t144ft, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 5699 Salem Road, Lithonia | 2920 | Notification received on February 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 2/15/2017 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy roots blockage | The problem was corrected at 13:08 hours when a crew root-cut the 8" sewer main 263ft upstream, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-20 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1025 Edgewood Avenue, NE | 6000 | fax received 12/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/29/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain induced spill |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-10 | 2017-04-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3006 Durban Court, Decatur | 2460 | Notification received on April 14, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/10/2017 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:30 hours when a crew rodded the 8" sewer main 3ft, clearing the blockage at 1ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-29 | 2017-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1965 Niskey Lake Trl. SW - ATL | 50 | Fax sent 2017-12-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 12/30/2017 12:00:00 AM |  | 12/29/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pumping system malfunction | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-22 | 2015-05-22 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Latitude 34.522064 Longitude 83.523575 | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Debris |  | Cindy Nix | Kathy Lewis | Cindy Nix | 5/22/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cornelia Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage overflowed the manhole as a result of a blockage in the sewer line | The overflow was stopped and the affected area leading to the Cornelia Branch was treated with hydrated calcium carbonate. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-22 | 2016-03-25 |  | Berrien | Nashville | Approximately 500 ft from the corner of Sycamore Drive and Pine Road off of Hwy 129 in the Northview Heights Subdivision | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Vandalism |  |  | Dagny Pariani |  | 3/23/2016 12:00:00 AM | Suwannee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowed due to debris (a fence post and tree limbs) being thrown into it, more than likely by kids. | Bypassed the sewage to the next manhole until the water level was pumped down enough to retrieve the debris. Limed the area and are installing a gate to try to minimize foot traffic through the area. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-31 | 2016-03-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1731 South Gordon Street, SW | 3400 | Fax received 4/01/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/1/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-02 | 2016-12-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1351 Cartecay Drive, Brookhaven | 1860 | Notification received on December 6, 2016 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/3/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | The problem was corrected at 13:33 hours, when a crew rodded the manhole 75ft downstream, cleared the grease blockage at 45ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1833 Slade @ Cherokee | 27707 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rain subsided, and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2017-06-29 | 2017-06-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1965 Lewis Rd. SE - ATL | 1975 | Fax received 2017-06-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/30/2017 12:00:00 AM |  | 6/29/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-11 | 2016-07-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 1729 | fax received 7/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/12/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-09 | 2018-03-09 | Cobb County Water System | Cobb |  | 1750 Bertram Lane | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/9/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Olley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped the overflow at 4:02 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2017-06-23 | Cobb County Water System | Cobb |  | 2195 Cobb Parkway | 710 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/29/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Poplar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | The cobb crew stopped the spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-19 | 2016-10-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1542 Alder CT., SE, Atlanta | 3 | Fax received on 10/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System |  |  | Debris |  |  | Paul Moisan | Paul Moisan | 10/21/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used hydraulic pressure to contain the spill. This area has been placed on periodic inspection schedule to determine the need for upgrade, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-02 | 2017-06-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2769 Mornington Dr. NW - ATL | 10 | ** This is not a city problem. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/3/2017 12:00:00 AM |  | 6/2/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the service lateral. | ** This is not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Baldwin, City of (Baldwin WPCP) | Baldwin |  | Fishing Creek Lat 33.0373111 degrees N Long 83.235544 degrees | 925 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/18/2017 12:00:00 AM | Oconee |  |  |  | 0 | Fishing Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Damaged line was plugged and Bypass Pumping was set up. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 101 Green Street, Decatur | 30750 | Notification received on November 4, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/3/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 18:30 hours when a crew waited until the storm event passed, the water receded, the manhole stopped spilling and resumed to regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-16 | 2016-07-17 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | J. B. Messerly WPCP Influent Pump Station | 2800000 | ERT notified 7/17/2016. CTS No. 80317 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  | Michelle Cortes | Kim Hembree | Kim Hembree | 7/17/2016 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Spill at head works to J.B. Messerly due to 3" rain event. |  | db6b2c02-fb34-11e0-9fd5-12313b0cb679 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-399-1238
2018-01-03 | 2018-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2839 Cornelia Drive - Augusta | 2800 | Email sent 2018-01-04 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/4/2018 12:00:00 AM |  |  |  |  | 1 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sand and other debris were in the line. | Used the Jetter truck to open the line. At 80’ a blockage was opened. The road was washed down and debris vacuumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-02 | 2015-01-02 | Cobb County MS4 | Cobb |  | 664 Ashley Circle | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/8/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Chattahoochee River. | The Water System crew stopped the overflow at 3:30 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-06 | 2017-02-06 | Summerville, City of (Summerville WPCP) | Chattooga |  | Urgent Care Medical Facility | 2500 |  | Raw Sewage | Mountain District - Cartersville | GA0025704 | WWTP |  |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 2/6/2017 12:00:00 AM | Coosa |  |  |  | 0 | Henry Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A gravity fed line had fallen over time and worked a coupling loose letting the sewage seep out | The city's crew immediate began replacing the defective sewer line and it was fixed by the close of business that day. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-08 | 2017-03-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) |  | Atlanta | 1461 Sylvan Rd. SW - ATL | 530 | Fax received 2017-03-09. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Paul Moisan | 3/9/2017 12:00:00 AM |  | 3/8/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Lyons, City of (Lyons North WPCP) | Toombs | Lyons | Manhole located at the end of N. Washington St. Lyons, GA, 30436. | 5000 | 5 day spill notice letter received on September 18th, 2017 from Mr. Jason Hall. No downstream water suppliers located within 20 miles of the spill. | Raw Sewage | Coastal District | GA0033391 | Collection System | Unnamed Drain |  | Natural Disaster |  | Beth Stevenson | Brett Berry | Brett Berry | 9/12/2017 12:00:00 AM | Altamaha |  |  |  | 1 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole located at the end of N. Washington St. was overflowing. This was determined that when flows exceeded the flow capacity of a section of the line. | N/A | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-20 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 85250 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 19:00 hours when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-13 | 2015-08-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6403 Port-A-Prince | 675 | Fax received 08/14/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Emily Wingo | 8/14/2015 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Cleared blockage. Blockage was cleared and flow was returned to normal. Site will be cleaned and work orders generated for additional work to determine cause. Televise. Lines will be televised and root cut and if problem is located it will be repaired. |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY | 770-960-5205
2016-10-08 | 2016-10-08 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | 1253 B&W Grade Road, Brunswick | 10000 |  | Raw Sewage | Coastal District | GA0025313 | Lift Station | Canal | Canal | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2016 9:00:00 AM | Satilla | 10/27/2016 12:00:00 AM | 2016-10-27 |  | 1 | Brunswick-Altamaha Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Lift Station (#4036) power failure due to Hurricane Matthew. | Power generator was connected to restore temporary power until permanent power was restored days later. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-31 | 1 | 1 | 0 | 0 | 0 | 0
2016-10-20 | 2016-10-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2145 Candler Road, Decatur | 2960 | Notification received on October 24, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/20/2016 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 10:28 hours, when a crew pressure washed the sewer main 484ft downstream, cleared the blockage at 450ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-23 | 2016-08-23 | Savannah, City of (President Street WRF) | Chatham | Savannah | 106 Okatee Drive, Savannah, GA | 177 |  | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain | Ditch | Pipe failure |  | David Lyle | David Lyle | Hailey Harden | 8/23/2016 3:41:00 PM | Savannah | 8/23/2016 12:00:00 AM |  |  | 1 | Betz Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defective Sanitary Sewer Main inside Storm Water Manhole | Defect in gravity sewer main being repaired immediately. Storm drainage system was mitigated to minimize contamination of State Waters. Notifications were posted at spill site, Betz Creek at Penn Waller Road and Betz Creek at Walthour Road. All agencies (i.e. Health Department, State EPD, and the City of Savannah Public Information Office (who will issue the Public News Release)) were notified as required by State Guidelines. | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | 2016-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-25 | 2018-08-25 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 2235 Academy Extension | 50 | Complaint received 2018-09-04 Email received 2018-09-05 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/4/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waterways | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "The City's repair crew was called in to inspect and they found that sewer was leaking inside a force main concrete vault..... a crack was located next to the 2" tap, on the 10" C-900 PVC, for the air release valve. " | "A repair clamp was installed and the leak was slowed to a slow drip and instructions left for the repair crew to continue monitoring and pumping down, as needed, to maintain for final repair. The City crew also used the vac truck to vacuum up, approximately 20 feet in length, the bottom of the drainage ditch where the sewer had ran and settled. The City will control the pump station and use two, 2,500 gallon septic tank trucks, to maintain the pump station during repair. 10" ductile iron piping will be replaced through the prefab concrete vault, grouted to seal the vault, and a new tap with a new air release valve, will be installed. The contractor will excavate the right-of-way, bring in new fill dirt with top soil and re-grass. Since Saturday, August 25th, the City has responded for inspection of the sewer vault and has vacuumed the vault 5 times, to maintain control of the sewer weeping in the vault." |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-08 | 2017-12-11 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 100 Renee Drive Tallapoosa | 14400 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream | Ditch | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/11/2017 12:00:00 AM | Tallapoosa |  |  |  | 0 | Unnamed tributary to Tallapoosa River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Extreme weather power outage that shut down our city, with emergency or back up power preventable | Power restored, treated area with hydrated lime and clean up persistent | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-18 | 2017-01-18 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville | Victory Division Drive | 10 | See "Documents" section below for a more detailed description of the event. | Raw Sewage | Coastal District | GA0047180 | WWTP | Stream | Stream | Grease |  | John Kalp | John Kalp | John Kalp | 1/18/2017 1:50:00 PM |  | 1/18/2017 12:00:00 AM |  |  | 1 | Tributary of Taylor's Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Yes | 0 | A grease blockage in the sanitary collection system caused a backup and a sanitary manhole overflowed (no solids released). The total over flow was estimated at 12400 gallons with only 10 gallons entering a storm water curb inlet that discharged into State Waters. | A berm was constructed preventing further discharge and a Jet Truck was used to clear the grease blockage. A pumper truck was used to remove any puddles. Agricultural lime was applied around the surrounding vegetation for disinfection. The area, located in a old demolished housing area, was marked off with caution tape and signs posted warning the public of the sanitary spill. All the proper agencies and media were notified. | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2017-01-19 | 1 | 1 | 0 | 0 | 0 | 0
2018-05-16 | 2018-05-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 294 pine Tree Circle, Decatur GA 30032 | 7200 | manhole 15-250-s020 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/17/2018 8:41:00 AM | Ocmulgee |  |  |  | 1 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Rodded main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-12 | 2018-02-12 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2260 Wrightsboro Rd - Augusta | 2000 | Email sent 2018-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Rags |  |  | Alys Hannum | Alys Hannum | 2/13/2018 12:00:00 AM |  |  |  |  | 1 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The main was blocked with rags and debris. | Used the rodder truck to open the blockage at 241’. The street was washed down and the curb and gutter and storm drain was flushed and vacuumed out. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 187 Vine Circle (WWTP Outfall) - Social Circle | 602890 | Fax received 2017-01-04 | Treated Effluent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/4/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Little River Stream | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Excessive flow due to rainfall (3.5'' in 2 days) | Started diesel pimp. Shut down some motors in basin. Adjusted telescoping valves in clarifiers. Adjusted splitter box. After flow subsided, returned to normal operation. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-22 | 2018-01-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 509 North McDonough Street Decatur GA 30030 | 50 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain | Stream |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/22/2018 2:25:00 PM | Ocmulgee |  |  |  | 1 | Pevine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | roots | Rodded privite 4" cleanout and removed root blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-22 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Phillips Davis |  | Dekalb Co Dept. Watershed Management
2016-11-18 | 2016-11-18 | Cumming, City of (Lanier Beach South WWTP) | Forsyth | Cumming | 1045 Pilgrim Mill Road Cumming, Georgia 30041 | 1000 |  | Raw Sewage | Wastewater Regulatory Program | GA0031674 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/18/2016 12:00:00 AM |  |  |  |  | 0 | Baldridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | breaker failure | The area that was affected by the spill has been cleaned up lime has been applied, and signage has also been posted along the stream, and the Forsyth County Health Department has been notified. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-28 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-21 | 2015-03-21 | Cobb County MS4 | Cobb |  | 2429 Justin Dr | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/21/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud and Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots in 8" Clay | Cleaned and Limed Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-08 | 2015-05-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1761 Hollingsworth Blvd, NW | 1372 | fax received 5/08/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/8/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-14 | 2017-08-14 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 1000 Lake Regency, Riverdale | 9600 | Fax received on 08/15/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 8/15/2017 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-18 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2015-09-08 | 2015-09-08 | Marietta (City of)- Sewers | Cobb | Marietta | 131 Herbert Dr. | 1350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 9/10/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A root blockage caused a sewer main to back up and discharge from a manhole into a nearby creek. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-08 | 2017-04-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 300 Speer Road, Jonesboro MH #2196674 | 40425 | Fax received on 04/08/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Lift Station | Stream | Shoreline | Power failure |  |  | Paul Moisan | Paul Moisan | 4/8/2017 12:00:00 AM | Upper Ocmulgee |  | 2017-04-09 |  | 1 | Cotton Indian Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The lift station lost power resulting in a surcharge and overflow. Station was brought on line stopping the event from occurring. | The area around the discharge was cleaned. Lift station operation will be reviewed by Clayton County Water Authority staff to prevent this event from re-occurring. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-11 | 0 | 1 | 1 | 1 | 0 | 0 | Charles Ecton |  | Clayton Co Water Authority
2017-07-03 | 2017-07-05 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 700 Sanders Road Pump Station - Cumming | 500 | Fax received 2017-07-03 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Pump Station | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/3/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was a result of a control panel failure. | Spill contained in a low-lying area inside the pump station site. The area affected has been cleaned up and the Forsyth County Health Department has been notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-22 | 2017-07-22 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville |  | 650 | It is estimated the discharge was 50 gallons per minute (GPM) over a thirteen (13) minute period of time for a total discharge estimate of 650 gallons. No evidence was observed that would indicate this discharge entered states waters. | Low Volume Waste | Coastal District | GA0047180 | WWTP |  |  | Equipment failure |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 7/24/2017 6:30:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewage release at approximately 0926 on Saturday July 22, 2017 at the Taylor Creek lift station. | The on-call Maintenance Technician was notified by the Maintenance Manager concerning a “High Wet Well” alarm at the Taylor Creek lift station. The on-call technician arrived about 0935 and observed water coming out of the station wet well. The pumps were restarted a 0945 and the discharge ceased at about 0948. | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-07-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-07 | 2017-03-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 1628 Crescent Centre Boulevard, Tucker | 4320 | Notification received on March 10, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/7/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:50 hours when a crew pressure washed the 8 inch sewer main between manholes 415ft, removed the blockage at 400ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2940 Clairmont Road Atlanta | 4880 | manhole 18-196-s055 | Raw Sewage |  | GA0024147 |  | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/15/2018 7:40:00 AM | Ocmulgee | 2/15/2018 12:00:00 AM |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Pressure washed line |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-03 | 2017-02-03 |  | DeKalb | Stone Mountain | 4886 Wedgewood Way, Stone Mountain | 2280 | Notification received on February 7, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/3/2017 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 20:50 hours when the crew pressure washed the 8" sewer main 300ft between manholes, cleared the grease blockage at 260ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-27 | 2017-08-01 | Duramatic Products | Tattnall |  |  | 800 |  | Raw Sewage | Coastal District | GAP050051 | Collection System |  |  | Pipe failure |  | Hailey Harden | Hailey Harden | Hailey Harden | 7/28/2017 10:35:00 AM |  |  |  |  | 0 | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | During a paving project in between Duramatic Products and Rotary Corporation, a high hoe ruptured our waste water line at approximately 3:45 PM, 7/27/17. This line contained waste from our Heat Treat and Finishing Processes. Both departments were shut down until the line could be fixed. | Our team, consisting of multiple departments, sprang into action and immediately began pumping the water into totes. We also used our emergency spill kit to try and soak up and items that may have been on the surface. The water was contained in a hole that was being filled with crush and run. Thus, the water did not reach the ditch. We pumped approximately 800 gallons of water into totes, PH of 3.75. Once the pipe was fixed, we scooped out the surrounding dirt and placed it into a holding tank under a shelter for containment. The water and the dirt will be treated. The overall process was completed by 5:45 PM. This was a team effort and I am really proud of our | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2017-08-01 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-17 | 2016-02-17 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 400 Block of Seymour Street | 3700 | Verbal notification received 2/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/17/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-12-12 | 2016-12-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1450 Woodbine Ave SE - ATL | 1000 | Fax received on 12/13/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/13/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-16 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-01-07 | 2015-01-07 |  | Fulton | East Point | 2548 Lumpkin Street | 385 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/7/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Utoy Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The probable cause of the spill was due to debris in the main resulting into a discharge into the Utoy Creek Basin. | The City's crew jetted and vacuumed out the main to remove the blockage, and cleaned the affected area as required. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-27 | 2016-05-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3901 Campbellton Road, SW | 725 | fax received 5/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/28/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-28 | 2016-07-28 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Corbin Lift Station to Riverside Lift Station Easment, Macon MH ID 66879 | 5285 | Email received on 08/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Lift Station | Stream | Shoreline | Contractor |  |  | Paul Moisan | Paul Moisan | 8/1/2016 12:00:00 AM | Upper Ocmulgee | 7/28/2016 12:00:00 AM |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A contractor was setting up by-pass pumps in order to complete the replacement of a section of sewer main. During the set-up, the discharge hose became disconnected causing the sewage to back up and overflow from a manhole. | Debris was removed form the area, and the hose was reconnected. Area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-08-01 | 0 | 1 | 0 | 0 | 0 | 0 | Heather Veal | 478-464-5669 | MWA
2017-03-27 | 2017-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3242 W. Roxboro Rd. NE - ATL | 390 | Fax received 2017-03-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/28/2017 12:00:00 AM |  | 3/27/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-15 | 2016-03-16 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | In the Area of 210 Pinehill Lane | 39600 | Water sampling of Noonday Creek up and down stream of the effected outfall location has been implemented. | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 3/15/2016 12:00:00 AM | Coosa |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Obstruction in line (tree limb and asphalt piece) caused an accumulation of debris to back up the line and overflowed the manhole. | Removed the obstructions from the line, jetted line, vacuumed and spread lime to the effected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | Hwy 94 Lift Station | 1300 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Withlacoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-21 | 2017-01-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3528 Misty Valley Road, Decatur | 174000 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 17:30 hours on January 22, 2017 when the heavy rain stopped and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 500 Dairy Pak Rd., Athens | 3000 | Initial call 11/3, full report faxed 11/4 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Oconee | 11/2/2015 12:00:00 AM |  |  | 1 | wetland tributary to North Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | overflow caused by flooding during major rain event | vac truck removed flow |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2018-02-24 | 2018-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 818 Joseph E. Lowery Blvd NW - ATL | 350 | Fax sent 2018-02-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 2/25/2018 12:00:00 AM |  | 2/24/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-19 | 2017-01-19 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | Behind 6019 Mark Trail - Norcross | 6686 |  | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 1/19/2017 12:00:00 AM |  | 1/19/2017 12:00:00 AM |  |  | 1 | Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked area and spread lime, as well as placed signs at the spill site and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-30 | 2016-03-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2819 Browntown Road, NW | 4200 | fax received 3/31/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/31/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-03 | 2018-03-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1767 Church St. NW - ATL | 92 | Fax sent 2018-03-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum |  | 3/4/2018 12:00:00 AM |  | 3/4/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-21 | 2018-02-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1354 Elizabeth Ave. SW - ATL | 530 | Fax sent 2018-02-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 2/22/2018 12:00:00 AM |  | 2/21/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-04 | 2017-01-04 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3008 West Floyd Avenue - Augusta | 4500 | Fax received 2017-01-08 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 1/8/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the sewer gravity main. | Jet-washed to clear blockage. Standing water in the affected area was removed by Vac truck. Lime spread in the affected area. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-27 | 2016-10-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1292 Euclid Ave., N.E., Atlanta | 595 | Fax received on 10/28/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  |  |  |  | Paul Moisan | Paul Moisan | 10/28/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the main line. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-01 | 0 | 0 | 0 | 0 | 0 | 0 | Donnie Morris |  | CITY OF ATLANTA
2016-06-07 | 2016-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 120 Claire Drive, SW | 1500 | fax received 6/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/8/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-08 | 2018-05-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2362 Dellwood Dr. NW - Atlanta | 100 | Fax sent 2018-05-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/9/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-18 | 2016-03-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3215 Lovell Drive, SW | 3420 | fax received 3/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/19/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-07 | 2016-10-15 | United States Army Hunter Army Airfield WWTP | Chatham | Savannah | Wilshire Plant effluent for the City of Savannah | 4730000 | See the "Documents" Section | Primary/Secondary Effluent | Coastal District | GA0027588 | WWTP | Other | Shoreline | Natural Disaster |  | John Kalp | John Kalp | John Kalp | 10/10/2016 12:00:00 AM | Savannah | 10/14/2016 12:00:00 AM | 2016-10-10 |  | 1 | City of Savannah's effluent to Savannah River | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Yes | 0 | Hurricane Matthew caused flooding at the WWTP and major damage to pumps, electrical equipment, and infrastructure at the facility causing partially treated wastewater to discharge to the Savannah WPCP effluent pipe and then to the Savannah River. The spill occurred over a period of nine (9) days and an estimated 4.73 MG was discharged. Entire spill has been entered into the "Documents" section | The facility has been brought back on line to be able to treat 100% of Hunter's daily flow. However, the facility is not at full capacity. A CAP is being authored to address future issues. The facility is currently doing the "Major Spill Protocol" monitoring | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2016-10-25 | 1 | 1 | 0 | 0 | 0 | 1
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive, NW | 8550 | fax received 1/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/15/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-02 | 2016-05-02 | Columbus Water Works (South WRF) | Muscogee | Columbus | 14 Benning Dell Drive, Columbus | 372 | Telephone call received on 05/02/2016; fax received on 05/03/2016; email received on 05/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 5/2/2016 12:00:00 AM | Chattahoochee | 5/3/2016 12:00:00 AM |  |  | 1 | Tributary of Upatoi Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A brick manhole was seeping from the mortar between the bricks. | Once repairs were made the seeping stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-23 | 2017-09-28 | Hazlehurst, City of (Bully Creek WPCP) | Jeff Davis | Hazlehurst | Near Pine Street in Hazlehurst, GA | 350000 |  | Raw Sewage | Coastal District | GA0036765 | Collection System | Stream | Ditch | Natural Disaster |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/27/2017 10:45:00 AM | Ocmulgee | 10/27/2017 12:00:00 AM | 2017-09-27 |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Large trees fell on a 12" aerial sewer main due to Hurricane Irma. | Sewer main repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2015-07-31 | 2015-07-31 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 564 Gwinnett Drive | 9600 | fax received 7/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/31/2015 12:00:00 AM |  |  |  |  | 1 | Fairground Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 425 Fielding Lane, SW | 790 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-30 | 2015-07-30 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1535 Benning Drive | 750 | REC EMAIL 7/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 7/31/2015 12:00:00 AM | Chattahoochee | 7/31/2015 12:00:00 AM |  |  | 1 | Tributary of Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 18" pipe was leaking from a split and entered a tributary of Bull Creek. | The pipe was plugged and a pump around was installed until permanent repairs can be made. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2015-06-04 | 2015-06-04 | Dallas North WPCP | Paulding |  | Behind City Barn | 9000 |  | Raw Sewage | Mountain District - Cartersville | GA0026034 | WWTP | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 6/5/2015 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | Jetted and cleaned line, cleaned up debris, Limed infected area | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | Kendall Smith | 770-443-8110 | City of Dallas - North WPCP
2017-08-03 | 2017-08-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1020 Peachtree Battle Ave. NW - ATL | 233 | Fax received 2017*08*04, in mailbox 2017-08-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 8/4/2017 12:00:00 AM |  | 8/3/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew repaired a segment of the mainline |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-08 | 2015-01-08 |  | DeKalb | Chamblee | 2739 Shallowford Road, Chamblee | 1600 | Notification received on January 12, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/8/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris blockage in an 8" sewer main | The problem was corrected at 09:32 hours when a crew rodded the 8" sewer main 50ft upstream, and restores normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-12 | 2017-04-12 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 1975 Deerwood Place, Macon MH ID 18630 | 3000 | Fax received on 04/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 4/13/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that the cause of this spill was a broken sewer main. | Debris was removed and the area was disinfected with lime. Sewer was repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-26 | 2017-07-26 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 3988 Braddock Street - Martinez | 3150 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/26/2017 12:00:00 AM |  |  | 1 | Tributary to Crane Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rainfall | Monitored Area. Follow up inspection of area. Continue to look for points of inflow. Posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-28 | 2015-06-28 | Cobb County MS4 | Cobb |  | 3865 Westmoreland Drive | 920 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/1/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease in the sewer main causing the manhole to overflow into a tributary of Noonday Creek. | The Water System was notified at 10:30 a.m. and the crew stopped the overflow at 1:03 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-25 |  | Gwinnett | Sugar Hill | 4710 Allison Drive | 520 | fax received 2/26/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 4" force main | Repaired force main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-02-04 |  |  | DeKalb |  | 161 Hood Circle | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flow had already been restored so crew cleaned up debris in area |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-13 | 2016-07-13 | Cobb County MS4 | Cobb |  | 2839 Pine Meadow Dr. | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/13/2016 12:00:00 AM |  |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in manhole |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1100 Block of Joeree Street | 29250 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-03-17 | 2017-03-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 555 8th St. NW - ATL | 20 | Received in letter. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 4/3/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-23 | 2015-07-23 |  | Fulton | East Point | 2812 Pine Valley Circle | 224640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/21/2015 12:00:00 AM | Chattahoochee | 7/21/2015 12:00:00 AM | 2015-07-21 |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Vacuumed and jetted out upstream sanitary sewer main to elimate blockage and cleaned and spread lime over the affected area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1959 Crescent Ln., Athens | 572 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Private Lateral | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/3/2016 12:00:00 AM | Oconee | 9/2/2016 12:00:00 AM |  |  | 1 | tributary to Brooklyn Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Homeowner cut sewer line during a private excavation | Fixed pipe, cleaned and limed area |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-08 | 2017-02-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 2765 Keystone Ave, Lithonia | 245 | Notification received on February 10, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/8/2017 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:00 hours when the crew pressure washed the 8" sewer main 102ft between manholes, cleared the grease blockage at 90ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-31 | 2018-05-31 | Rome, City of (Rome WRF) | Floyd |  | At the intersection of Coosawattee Avenue @ Ridge Drive where the sewer main crosses the creek. | 6500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP |  |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 5/31/2018 12:00:00 AM | Coosa |  |  |  | 1 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The bottom of the ductile iron had deteriorated to the point of failure | A dam was built to channel the sewage to the manhole. The damaged pipe was removed to allow the sewage to flow into the manhole. New ductile iron pipe installed to the manhole | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-06-05 | 1 | 0 | 0 | 0 | 0 | 0
2015-08-12 | 2015-08-12 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 2484 River Ridge Road | 660 | verbal notification received from Amanda Akins, City of Milledgeville, on 8/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/12/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Tobler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Removed grease, rodded line, limed area | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2016-02-03 | 2016-02-04 | Cordele, City of (Gum Creek WPCP) | Crisp | Cordele | 801 Perimeter Road, Cordele At fence, just east of the WWTP. | 1000000 | Email received on 02/05/2016. Health Department not notified, no one would answer and no room on message recorder. Health Dept notified on 02/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024503 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 2/5/2016 12:00:00 AM | Flint | 2/8/2016 12:00:00 AM | 2016-02-04 |  | 1 | Gum Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Excessive rainfall on saturated ground. | Contacted Southeast Pipe Co. to cap the abandoned line and manhole. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-09 | 0 | 0 | 0 | 1 | 0 | 0
2016-02-04 | 2016-02-05 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Douglas Southeast WPCP | 6800000 |  | Secondary Effluent | Coastal District | GA0024431 | WWTP | Stream | Stream | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/4/2016 11:30:00 AM | Satilla | 2/5/2016 12:00:00 AM | 2016-02-05 |  | 1 | Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Heavy rainfall event causing hydraulic overload that exceeded the WPCP capacity. | Continue I&I investigations to reduce flow to the WPCP during heavy rain events. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-02-16 | 1 | 1 | 0 | 0 | 0 | 1
2017-04-27 | 2017-04-27 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Athens Country Club, 2700 Jefferson Road | 3501 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2017 12:00:00 AM | Oconee |  |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Erosion of creek bank damaged existing sewer line. | Replace pipe and stablized creek bank to prevent future erosion. 2-8" Pipes were damaged. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-25 | 2017-05-25 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Central Avenue @ Meigs Street | 5300 | Email received 2017-05-25 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Other |  |  |  | Alys Hannum | 5/26/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Mid City | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vehicle Accident | Bypass pumping was set up. Repairs to the sewer gravity main are underway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | 406 Greenville St., Lagrange | 7677 | Fax received on 04/15/2017. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 2/15/2017 12:00:00 AM | Chattahoochee | 2/15/2017 12:00:00 AM |  |  | 1 | Tanyard Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease mixed with sanitary wipes. | High pressure jetting truck used to clear the choke - will follow-up with camera inspection and disconnect abandoned service line from main. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-16 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-21 | 2015-09-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2228 Snapfinger Road, Decatur | 2160 | Notification received on September 23, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/21/2015 12:00:00 AM |  |  |  |  | 0 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:19 hours, when a crew rodded the sewer main 200ft upstream, also pressure washed the line 300ft for additional cleaning and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-12 | 2015-10-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 77 | fax received 10/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 10/13/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-11 | 2016-11-11 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3210 11th Div. Road, Fort Benning | 1897 | Fax received on 11/11/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Force Main | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/11/2016 12:00:00 AM |  |  |  |  | 1 | Upatoi Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. | Once the debris was cleared from the main, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2016-03-22 | 2016-03-22 | Paulding County (Pumpkinvine Creek WRF) | Paulding |  | Longwood Crossing Acworth | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0039021 | WWRF | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 3/24/2016 12:00:00 AM | Coosa |  |  |  | 0 | Branch of Pickets Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks, sticks down in manhole blocking it | Pump manhole out and removed all rocks and debris from bottom of manhole | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-18 | 2017-04-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 781 Needle Rock Drive, Stone Mountain | 1960 | Notification received on April 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 4/18/2017 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage | The problem was corrected at 11:25 hours when a crew pressure washed between manholes 50ft, clearing the blockage at 15ft and restored steady flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-20 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-02 | 2018-07-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 26720000 | Call received 2018-07-05 | Primary Effuent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 7/5/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | From midnight July 2 to midnight July 3, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. TSS - 31 mg/L. (Limit - 15 mg/L) This spill is also entered as a violation. | Excess biosolids to be removed from the facility | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-03 | 2017-05-03 | Gainesville, City of (Linwood WPCP) | Hall | Gainesville | Old Oakwood Road, NE | 35000 | Notification and overflow check list received on May 4, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0020168 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 5/3/2017 12:00:00 AM |  |  |  |  | 0 | Balus Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown obstruction in sewerline | A city crew responded to the discharging manhole, removed the blockage, restored flow, removed wastewater via a pump truck and applied lime to the area. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-01 | 2015-06-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 600 Newtown Circle, SE | 690 | fax received 6/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/2/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-01 | 2017-09-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4 Adair Ave. SE - ATL | 430 | Fax sent 2017-09-02; received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/2/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-01 | 2015-04-01 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility. Effluent TSS reported at 26.8 mg/L on April 1, 2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-30 | 2015-07-30 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | 401 Creekside Drive | 500 | REC FAX 7/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Ground |  | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 7/31/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease adhered to wet well level control bulbs not allowing pumps to come on. | Bulbs cleaned off and pumps reactivated. Residual sewage cleaned up from street. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LAGRANGE | 706.883.2118
2015-01-29 | 2015-01-29 |  | DeKalb | Decatur | 335 Ponce DeLeon Place, Decatur | 1960 | Notification received on January 30, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Other |  |  | Hsin Yeh | Hsin Yeh | 1/30/2015 12:00:00 AM |  |  |  |  | 0 | Lamont Drive Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks blockage | The problem was corrected at 13:53 hours when a crew rodded the sewer main 12ft upstream, clered the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-03 | 2015-01-03 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1176 Garibaldi Street, SW | 5 | fax received 1/06/2014 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/6/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-19 | 2016-04-19 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 111 Clarion Road | 4136 | fax received 4/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/20/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Little Suwanee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-11-29 | 2017-11-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3994 Blanton Ave. SW - ATL | 1125 | Fax sent 2017-11-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/30/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-16 | 2015-12-16 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | Belhaven/Turnbury Pump Station, 3876 Ancroft Circle | 74755 | fax received 12/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Operator error |  |  | Kim Hembree | Kim Hembree | 12/17/2015 12:00:00 AM |  |  | 2015-12-16 | 2016-12-27 | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Operator error | Put pumps in manual and pumped the well out. Ensured pump float was free from grease. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | GWINNETT COUNTY
2018-02-15 | 2018-02-15 | Marietta (City of)- Sewers | Cobb | Marietta | 2420 Delk Rd. | 3300 | Report attached | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/15/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage / Rocks | Marietta Water personnel relieved the blockage thus restoring normal service. Our crews continue working to remove all rocks and debris and repair the damage manholes. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-26 | 2015-01-26 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 26.8 mg/l
2015-04-28 | 2015-04-28 |  | Gwinnett | Norcross | 3201 Sunrise Village Lane | 1740 | fax received 4-29-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/29/2015 12:00:00 AM |  |  |  |  | 1 | Jackson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-02-15 | 2016-02-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5449 Bunky Way, Dunwoody | 4380 | Notification received on February 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/15/2016 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 11:15 hours, when a crew pressure washed the sewer main 125ft, ckearing the blocakge at 83ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-16 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Savannah, City of (President Street WRF) | Chatham | Savannah | 101 Bobstay Ct., Savannah, GA | 40 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Storm Drain | Ditch | Power failure |  | Azarina Carmical | David Lyle | Hailey Harden | 10/11/2016 12:00:00 AM | Savannah | 10/11/2016 12:00:00 AM |  |  | 0 | Richardson Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  | 0 | Hurricane Matthew cause power outages at lift station 27 | repaired generator and cleaned up area with City of Savannah Vehicles and Staff. Spill notification markers were placed at the spill site and at a ditch near Captain Butlers - 115 Penrose Drive Whitemarsh Island. | 94d448a2-8813-11e1-9b1d-12313d2b7a91 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | 2016-10-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-14 | 2015-09-14 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton |  | 6853 Red Maple Drive, Rex, Georgia; Manhole # 2200533 | 7200 | Fax was received on 09/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 9/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots. | Cleared blockage. Blockage was cleared and flow was returned to normal. Site will be cleaned and work orders generated for additional work to determine the cause. Lines will be televised and root cut and if a problem is located it will be repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-09-15 | 1 | 1 | 1 | 0 | 0 | 0
2017-01-22 | 2017-02-24 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Joe Coleman Road - Augusta | 29400 | Facility did not have record of the end date for the spill on Jan 22, so they combined it with the spill on Jan 24 to avoid under-reporting. Records for both spills are in Documents. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County Area. | Will assess system via flow monitoring and CCTV to determine any areas with inflow and infliltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-05 | 2015-03-05 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | 855 N. Center Street, Thomaston, Georgia | 35000 |  | Raw Sewage | Wastewater Regulatory Program | GA0020079 | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/5/2015 12:00:00 AM |  |  | 2015-03-05 |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The spill occurred due to a broken force main. | The force main was repaired and the affected areas were treated with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-06-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-05 | 2016-08-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 3540 Buford Hwy NE, Brookhaven | 23280 | Notification received on August 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 8/5/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Outside Contractor/Utility | The problem was corrected at 20:00 hours, when a County crew assisted the contractor using the vactor truck to detain the spill, while the contractor repaired the 8" sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-09 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 106 Greenbrier Ct., Savannah, GA | 600 |  | Raw Sewage | Coastal District | GA0020443 | Lift Station | Storm Drain, Stream | Stream | Natural Disaster |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM |  | 10/9/2016 12:00:00 AM |  |  | 1 | Vernon River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage at lift station during Hurricane Matthew. LS has no generator onsite. | Sand bagged area and cleaned with vac truck. Will pump and haul and/or install portable generator as needed. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-01 | 2018-07-01 | Rome, City of (Rome WRF) | Floyd |  | Intersection of Lee Avenue @ E. 7th Street | 1500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/2/2018 12:00:00 AM | Coosa |  |  |  | 1 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer main, excessive rain | The sewer main is flowing at this time however, there are indications of an issue downstream. We are attempting to identify the location and make repairs | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-10 | 1 | 0 | 0 | 0 | 0 | 0
2016-08-18 | 2016-08-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2684 Santa Barbara Drive, NW | 1 | fax received 8/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/18/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-19 | 2015-04-19 |  | Henry | Stockbridge | 678 Fairhaven Blvd. Stockbridge, GA | 7000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/19/2015 12:00:00 AM | Ocmulgee | 4/19/2015 12:00:00 AM |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration from an already saturated ground, 9.2 inches of rain so far this month, 1.3 inches came in on the 19th in just a couple of hours which caused the system to be overwhelmed. | Cleaned up spill area around manhole, and placed spill notification signs around spill area and notified all of the proper agencies. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-22 | 2015-01-22 |  | DeKalb | Decatur | 3403 Glenwood Road, Decatur | 10 | Notification received on January 23, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 1/23/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek crossing joint leaking | The problem was corrected at 10:10 hours when a crew sealed pipe and built a brick collar around the repair line and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | 303 Creekside Drive. | 2088 | Fax received at EPD office on November 2, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Dixie Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Heavy rainfall creating excessive I/I, overwhelmed the system, allowing sewage to escape around locked manhole lid. | Once rain subsided, system returned to normal flow. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-22 | 2016-02-25 | Rome, City of (Rome WRF) | Floyd |  | Behind 2631 Callier Springs Road | 9200 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream | Stream | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/26/2016 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer main | The main was excavated and repaired. The spill site is being cleaned and the contaminated soil removed. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2367 Leila Ln. SE - ATL | 1620 | Fax received 2017-04-26. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/27/2017 12:00:00 AM |  | 4/25/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Metter, City of (Metter WPCP) | Candler | metter |  | 123750 |  | Raw Sewage | Coastal District | GAJ020185 | Collection System | Basin | Ditch | Power failure |  | Cliff Swiger | Cliff Swiger | Cliff Swiger | 10/10/2016 1:47:00 PM | Ogeechee | 10/10/2016 12:00:00 AM | 2016-10-10 |  | 0 | Caney Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Matthew |  | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-17 | 2016-09-17 | Hartwell, City of (Hartwell WPCP) | Hart | Hartwell | Hartwell LAS, 402 Hodges Mill Rd, Hartwell | 60000 | Operator left voicemail Saturday, 9/17. Follow up call on Tuesday, 9/20. | Undisinfected Primary Effluent | Wastewater Regulatory Program | GAJ020114 | WWTP | Stream | Stream | Operator error |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/17/2016 12:00:00 AM | Savannah | 9/17/2016 12:00:00 AM | 2016-09-19 |  | 1 | Little Cooter Branch | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Aeration Basin #1 had been offline for repairs. When the facility placed the process back online, a valve was mistakenly left shut allowing the process water to spill. | Aeration Basin #1 was properly placed online. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Hartwell | 706-856-3212
2017-09-03 | 2017-09-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 230 East Lake Blvd. SE - ATL | 3750 | Fax sent 2017-09-03; received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/4/2017 12:00:00 AM |  | 9/3/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-29 | 2017-08-29 | Cobb County Water System | Cobb |  | 5860 Dunn Rd | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/29/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | pine creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | stopped spill and spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 500 Block of Rouse Road | 3060 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2018-06-14 | 2018-06-14 | Rome, City of (Rome WRF) | Floyd |  | Back side of Redmond Regional Hospital site near John Maddox Drive | 100 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Contractor |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 6/14/2018 12:00:00 AM | Coosa |  |  |  | 1 | Little Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction contractor was digging up tree stumps and broke sewer main. Contractor was cautioned the previous day by City of Rome personnel about the sewer main running through his dig site. | Approximately 100 gallons of sewage made it to the private storm drain system inside hospital property but did not leave the property. City work crew is in the process of making repairs to the sewer main. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-06-18 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-12 | 2017-01-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 348 Armour Dr NE - ATL | 13450 | Fax received on 01/13/2017. Another fax received on 01/14/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/13/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is debris in the mainline. | The crew is setting up a by-pass pump (work in progress) to contain spill (rate approximately 50 GPM). Spill was contained on 01/13/2017 at 18:50 using a by-pass pump. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-06-05 | 2017-06-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 118 Roseclair Dr. SE - ATL | 1590 | Email received 2017-06-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/6/2017 12:00:00 AM |  | 6/5/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-07 | 2017-11-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3763 Wake Forest Road Decatur GA 30034 | 1180 | manhole 15-036-s048 surcharging | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/7/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root blockage | pressured washed 8" main for 100ft |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Jimmy Veal |  | Dekalb County Department of Watershed Management
2018-01-09 | 2018-01-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 479 Park Valley Dr. NW - ATL | 555 | Fax sent 2018-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Swale | Grease |  |  | Alys Hannum | Alys Hannum | 1/10/2018 12:00:00 AM |  | 1/9/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-06 | 2015-04-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 595 Brownwood Avenue, SE | 18 | fax received 4/06/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/6/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-23 | 2015-12-26 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 153 Covington Court, Macon, GA (MH #63699) | 156600 | Fax and email received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/24/2015 12:00:00 AM | 2015-12-26 | 2016-11-30 | 1 | Wolf Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was hydraulic overload. The MWA service area received 5.75 inches of rain from December 21-24. | Debris was removed from the area, and the affected area was disinfected with lime. The MWA will continue its search for I/I into its sewer system through CCTV and flow monitoring investigations and will develop rehabilitation projects based on this information and contractor conducted sewer evaluations. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0
2016-11-18 | 2016-11-18 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1469 Pitts Place, Macon MH ID 59830 | 4830 | Email received on 11/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 11/21/2016 12:00:00 AM | Ocmulgee | 11/21/2016 12:00:00 AM |  |  | 1 | Unnamed tributary feeding Ocmulgee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Debris was removed from the area and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-21 | 0 | 1 | 0 | 0 | 0 | 0 | Heather Veal | 478-464-5669 | MACON WATER AUTHORITY
2018-06-16 | 2018-06-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1814 Peachtree St. NW - Atlanta | 60 | Fax sent 2018-06-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 6/17/2018 12:00:00 AM |  | 6/16/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-24 | Glennville, City of (Glennville WPCP) | Tattnall | Glennville | 600 Pecan Road Glennville, GA | 0 | Outfall spill caused by high BOD | Treated Effluent | Coastal District | GA0037982 | WWTP | Stream | Stream | Other |  | Jonathan Dance | Jonathan Dance | Jonathan Dance | 5/31/2018 12:00:00 AM | Altamaha | 5/24/2018 12:00:00 AM |  |  | 1 | Brickyard Branch Tribuatary | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Facility undergoing maintenance and experienced heavy rainfall that led to a shortened detention time and an algae bloom. | Maintenance completed to bring the facility back to full capacity. | 3c961d94-0dba-4b14-af92-55314e79f9da | 3c961d94-0dba-4b14-af92-55314e79f9da | 3c961d94-0dba-4b14-af92-55314e79f9da | 2018-06-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-09 | 2017-06-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4001 Lake Forrest Dr. NW - ATL | 8730 | Email received 2017-06-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 6/12/2017 12:00:00 AM |  | 6/9/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew set up a by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-03 | 2017-11-03 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 196 Old Mill Trail | 180 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/3/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Almand Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-18 | 2016-02-18 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | 120 McGhee St., LaGrange | 8030 | Initial and Follow-up spill reports faxed on 02/18/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/18/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tanyard Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease mixed with sanitary wipes created a choke in the main. | Used high-pressure jetting truck to clear choke/will follow-up with camera inspection and take any additional actions needed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-19 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 33 Rivermoor Ct., Savannah, GA | 310 | Initial notification via phone and full report via email on 9/12 | Raw Sewage | Coastal District | GA0038326 | Collection System | Stream | Stream | Natural Disaster |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/12/2017 12:00:00 AM | Savannah | 9/12/2017 12:00:00 AM |  |  | 1 | St. Augustine Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive flow caused by Hurricane Irma | Pumped system down with vac truck until flow subsided | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6584
2016-08-05 | 2016-08-05 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lilburn | 996 Traymore Drive | 5084 | fax received 8/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/5/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Beaver Ruin Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-02-03 | 2016-02-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1551 West Nancy Creek Drive, Brookhaven | 9000 | Notification received on February 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/3/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:30 hours, when a crew pressure washed the 10" sewer main 300ft, clearing the blockage at a 180ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-21 | 2016-07-26 | Thomaston, City of | Upson | Thomaston | Martha Mills Lift Station | 7050 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was hydraulic overload due to heavy rains in the COT service area. | Debris has been removed from the surronding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-16 | 2018-05-16 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Manholes #7636 adjacent to South Central Influent LS | 18000 | Email received on 5/17/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038709 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Paul Moisan | 5/17/2018 12:00:00 AM |  |  |  |  | 0 | Little Bear Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Heavy rains | Mechanics were dispatched to the site to monitor and ensure pumps were running correctly. Crews cleaned and disinfected area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-28 | 2015-01-28 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3342 Kilby Place, NW | 20 | fax received 1/29/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/29/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-12 | 2017-12-12 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 3530 Highway 81 South - Loganville | 14400 | Email sent 2017-12-12 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 12/12/2017 12:00:00 AM |  | 1/12/2018 12:00:00 AM |  |  | 1 | Unknown Trib. to Big Flat Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Broken 8' Sewer Force Main | Sewer force main repaired. Signs posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-20 | 2017-03-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3242 West Roxboro Rd. NE - ATL | 442 | Fax received 2017-03-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/22/2017 12:00:00 AM |  | 3/20/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew made repairs to the mainline to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-06 | 2015-02-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 626 Lynn Valley Road, SW | 415 | email received 2/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/9/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-28 | 2017-01-28 | Cobb County Water System | Cobb |  | 1260 Timberland Dr | 160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/28/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solid Build up |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-24 | 2016-11-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way, SW, ATL | 164 | Fax received on 11/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/25/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-28 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-1328 | ATLANTA, CITY OF
2017-10-25 | 2017-10-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 712 W. Paces Ferry Rd. NW - ATL | 200 | Fax sent 2017-10-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 10/26/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | Countryside Lift Station, Moultrie | 5400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Lift Station | Stream | Stream | Natural Disaster |  |  | Dagny Pariani | Dagny Pariani | 9/2/2016 12:00:00 AM | Ochlockonee | 9/2/2016 12:00:00 AM |  |  | 1 | unnamed tributary to Ochlockonee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tropical Storm Hermine - tree fell on power lines cutting off power to the LS | Power was restored once the tree was removed from the power lines. Area was cleaned and limed. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc.
2017-06-20 | 2017-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2479 Sharondale Dr. NE | 25 | Email received 2017-06-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-09 | 2018-02-09 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Henderson Falls Park | 500 | Spill report received on February 9, 2018. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 2/9/2018 12:00:00 AM |  |  |  |  | 0 | Toccoa Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Remove the blockage |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-12 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-14 | 2016-06-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 Handley Avenue, SW | 4600 | fax received 6/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/15/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-02 | 2015-11-03 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | City of Social Circle Little River WPCP | 586585 | Verbal notification recieved 11/03/2015 | Primary Effuent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload. Approx. 3.5" of rain. Facility personnel had to turn off motors in the aeration basin and allow partially treated water to flow through the treatment facility. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2015-03-24 | 2015-03-24 | Grovetown, City of | Columbia |  | manhole adjacent to Euchee Creek north of Harlem-Grovetown Road | 4000 | Written notification was received on March 27, 2014. Department of Health was notified. Monitoring of receiving stream was conducted on March 25, 2015 as instructed; and the results provided to EPD. The monitoring results revealed that water quality violations had not occurred; therefore the incident will be treated as a spill with the appropriate notifications per the permit to be implemented, but no additional stream monitoring will be required. | Raw Sewage | Northeast District - Augusta | GA02-222 | N/A | Ground, Stream |  | Debris |  | Delaine Scott | Delaine Scott | Delaine Scott | 3/24/2015 12:00:00 AM | Savannah |  | 2015-03-25 | 2015-03-25 | 1 | Euchee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the sewer system resulted in a raw sewage spill at a manhole ajacent to Euchee Creek. | Obstruction was cleared using a Jetta machine; manholes and pipe were cleaned and flushed; and lime was placed around the manhole and receiving stream to neutralize sewage at the spill location. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2015-04-23 | 1 | 1 | 0 | 0 | 0 | 0
2018-06-08 | 2018-06-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2610 Cravey Drive Atlanta GA 30345 | 1300 | manhole 18-231-s201 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/8/2018 8:31:00 PM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-07 | 2015-12-07 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 1654 Overview Circle | 1580 | fax received 12/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/7/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in manhole | Debris removed |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-04-02 | 2016-04-02 | Tifton, City of (New River WPCP) | Tift | Tifton | 206 W. 26th Street, Tifton | 8400 | Email received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | tributary of New River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall event on April 1-2, 2016. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-24 | 2018-08-24 | Monroe, City of (Jack's Creek WPCP) | Walton | Monroe | Tractor Supply Pump Station - Monroe | 3000 | Email sent 2018-08-24 | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Collection System | Stream |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 8/24/2018 12:00:00 AM |  |  |  |  | 1 | Trib. to Jack's Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical issues - pump stopped. | Repaired. Cleaned location and spread lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-03 | 2015-08-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3669 MLK Jr. Drive, NW | 300 | fax received 8/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Contractor |  |  | Kim Hembree | Kim Hembree | 8/4/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was caused by private plumbers performing unauthorized work on the city mainline. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-13 | 2016-01-13 | Savannah, City of (President Street WRF) | Chatham | savannah | 2306 Vicksburg Drive | 475 |  | Raw Sewage | Coastal District |  | WWTP | Ditch | Pier | Grease |  | Steve Fox | Steve Fox | Steve Fox | 1/13/2016 12:00:00 AM | Savannah | 1/13/2016 12:00:00 AM |  |  | 1 | Placentia canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Overflowing manhole caused by grease blockage in gravity sanitary sewer main | Cleared stoppage with City jet-vacuum trucks and contained ditch and set up by-pass pumps to remove and pump contaminated water (mix of storm drainage and sanitary sewer) from ditch to City sanitary sewer collection system. Spill notification markers were placed at the spill site, at the Placentia Canal at Bonaventure Road, and at the Thunderbolt Fishing Pier. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-01-20 | 1 | 1 | 0 | 0 | 0 | 0
2017-02-07 | 2017-02-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 532 Ross St. SW - ATL | 50 | Fax received 2017-02-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Paul Moisan | 2/8/2017 12:00:00 AM |  |  |  |  | 0 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a partially collapsed mainline. | A point repair was made to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-01 | 2017-04-01 | Cobb County Water System | Cobb |  | 2922 owens points trl | 240 |  | Raw Sewage | Mountain District - Cartersville |  | Collection System |  | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | solids in 8" pvc | spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-17 | 2015-05-17 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 1358 Ronald Regan Blvd | 6000 | fax received 5/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream |  | Equipment failure |  | Kim Hembree |  | Kim Hembree | 5/18/2015 12:00:00 AM |  |  |  |  | 1 | Daves Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Transformer failure at the Ronald Regan Road Pumping Station | Replaced the transformer | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 |  | 2015-05-27 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CUMMING | 770.781.2007
2018-01-02 | 2018-01-02 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 8730 Roswell Road Sandy Springs, 30350 | 37710 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/2/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-23 | 2017-10-23 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 407 Stokesay Dr. - Lawrenceville | 954 | Fax sent 2017-10-23 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 10/23/2017 12:00:00 AM |  | 10/23/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Redland Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Removed all deposited solids, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-09 | 2017-09-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 377 Edgewood Ave. SE | 1760 | Fax sent 2017-09-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/10/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-20 | 2015-05-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1529 Piedmont Avenue, NE | 321 | fax received 5/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/21/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-13 | 2015-04-13 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 130 Lawshe Street, SW | 358 | fax received 4/14/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/13/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-29 | 2015-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3463 Chestnut Drive, Doraville | 21490 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 10" Creek Crossing sewer main | The problem was corrected at 15:00 hours, when a crew replaced 8ft of the PVC 10" pipe and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-26 | 2016-02-26 | Dahlonega, City of (Dahlonega WPCP) | Lumpkin |  | Intersection of Hwy 9 South and Radio Road | 1750 |  | Raw Sewage | Mountain District - Cartersville | GA0026077 | WWTP | Stream |  | Pipe failure |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 3/2/2016 12:00:00 AM | Chattahoochee |  | 2016-02-26 | 2016-03-03 | 1 | Cane Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | Split Sewer Line | Split line was replaced | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2016-01-04 |  | Fulton |  | Azalea Drive/Riverside Road Roswell 30075 | 2964249 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rains caused big creek to overflow the banks and inundate the sewer system along the chattahoochee river and Big Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-16 | 2017-02-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3136 Buford Highway, Atlanta | 347480 | Notification received on February 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Rags |  |  | Hsin Yeh | Hsin Yeh | 2/16/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Rags blockage | The problem was corrected at 12:03 hours when a crew pressure washed the 8" sewer main 35ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-09 | 2017-08-09 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1185 Tillman Street | 1980 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/9/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | yellow river | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Clean Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-17 | 2017-04-17 | Thomaston, City of | Upson | Thomaston | 408 Barnesville Highway | 675 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/19/2017 12:00:00 AM | Ogeechee |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Blockage | The site was cleaned, debris was removed and signs were posted at the site. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-04 | 2015-09-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2591 Etheridge Drive, NW | 1328 | fax received 9/05/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/5/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-03 | 2017-12-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2461 Metropolitan Pkwy SW - ATL | 175 | Fax sent 2017-12-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/3/2017 12:00:00 AM |  | 12/4/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "blockage" | Crew used a hydraulic pressure cleaner to clear the blockage. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-19 | 2018-07-23 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Intersection of Parkwood Drive and N. Cleburn Street. | 400 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Storm Drain | Ditch | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/19/2018 4:33:00 PM | Satilla | 7/17/2018 12:00:00 AM |  |  | 1 | Terry Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in gravity main obstructing flow from sewer pump station 4017 force main discharge to sewer gravity main. | Sewer crews observed the event and shut down the station within minutes of the event. Due to heavy rains the untreated sewage escaped from a manhole mixed with storm water within the flooded roadway and went down storm drains. It was not possible to recover the spill. Levels within the gravity lines and lift station were carefully maintained below overflow level while the line was cleared of debris. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-07-23 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-30 |  |  | DeKalb |  | 13100 Waldrop Cove | 3280 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded and pressure washed sewer main to remove blockage and restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-19 | 2017-04-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 4424 Burks Road, Forest Park | 10800 | Fax received on 04/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Vandalism |  |  | Paul Moisan | Paul Moisan | 4/20/2017 12:00:00 AM | Upper Ocmulgee |  | 2017-04-20 |  | 1 | Poole Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Vandalism | Cleared blockage and flow returned to normal. Lid was replaced, and lids in the area will be sealed to prevent this from occurring again. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-20 | 0 | 0 | 1 | 1 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2017-04-19 | 2017-04-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 4424 Burks Road, Forest Park | 10800 | Fax received on 04/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Vandalism |  |  | Paul Moisan | Paul Moisan | 4/20/2017 12:00:00 AM | Upper Ocmulgee |  | 2017-04-20 |  | 1 | Poole Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Vandalism | Cleared blockage and flow returned to normal. Lid was replaced, and lids in the area will be sealed to prevent this from occurring again. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-20 | 0 | 0 | 1 | 1 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2016-11-07 | 2016-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2779 Cascade Rd, SW, Atlanta | 25 | Fax received on 11/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/8/2016 12:00:00 AM |  |  |  |  | 0 | Dry land - did not reach waters of the state | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the service lateral. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-09-30 | 2016-10-01 | Ochlocknee, Town of (Ochlocknee WPCP) | Thomas | Ochlocknee | off Pine Road in Ochlocknee, GA | 0 |  | Raw Sewage | Southwest District | GA0046370 | Force Main | Ground | Stream |  |  | Jay Howell | Jay Howell | Jay Howell | 10/3/2016 7:40:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Raw sewage spill found on 9/30/2016 by private property owner. Root intrusion caused breakage in line work. Repaired on 10/1/2016. Undetermined volume - appears to have been greater than 10,000 gallons. | Repair broken force main, apply lime and remove contaminated soils. Major PN requirements and stream monitoring requested 10/18/2016. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2016-10-18 | 1 | 0 | 0 | 0 | 0 | 0
2017-05-07 | 2017-05-07 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 2840 Pierce Drive South, Macon MH ID 64565 | 2760 | Fax received on 05/08/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 5/8/2017 12:00:00 AM | Upper Ocmulgee | 5/7/2017 12:00:00 AM |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Debris was removed from the blockage, and the area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Foster Street | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 2/24/2016 12:00:00 AM | Chattahoochee | 2/24/2016 12:00:00 AM |  |  | 0 | South Fork of Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowed due to heavy rains |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-02 | 2015-06-02 | Cobb County MS4 | Cobb |  | 4683 Magnolia Circle | 4560 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of structural damage in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The Water System crew stopped the overflow at 11:29 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-26 | 2017-07-26 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | Outfall - 4590 Oakley Pirkle Road - Martinez | 10000 | Fax received 2017-07-26 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/26/2017 12:00:00 AM |  |  | 1 | Crawford Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive Rainfall | Monitored area. Follow up inspection of area. Continue to look for points of inflow. Posted signs. Begin sampling. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-16 | 2016-03-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1424 Sylvan Circle, Brookhaven | 6600 | Notification received on March 21, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/16/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The problem was corrected at 17:42 hours, when a crew rodded and pressure washed the sewer main upstream 1534ft, clearing the blockage at 132ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Fernside Drive, Toccoa | 5000 | Notice of sanitary sewer spill received on November 3, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/3/2015 12:00:00 AM |  |  |  |  | 0 | Ward Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | In an effort to minimize the overflow, City personnel went over right away to utilize the Vacuum Truck to manually transport wastewater from the Lift Station to the Eastanollee Creek Wastewater Treatment Plant located on Rose Lane. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-19 | 2017-06-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5092 club vista Point, Stone Mountain | 21120 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/20/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags blockage | The problem was corrected on June 20, 2017 at 00:45 hours when the crew pressure washed the 8" sewer main 60ft, cleared the grease/rags blockage at 40ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-05 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Lift Stations #78. | 86100 | Telephone call and email received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Lift Station | Ditch |  | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Cooleewahee Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The National Weather Service reported 8 - 9 tornadoes plus straight line winds resulting in power loss to 52 storm and sanitary lift stations. | Power was restored to all lift stations by 01/14/2017. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2017-12-23 | 2017-12-23 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 238 Colonial Drive, Woodstock | 4762 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/23/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary of Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewage line clogged by a deer in the line | Construction used a push camera to examine line and found deer in line and removed deer and jetted line | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-12-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-05 | 2015-11-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1296 Murphy Avenue, SW | 1155 | fax received 11/06/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/6/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-14 | 2016-09-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5123 North Peachtree Road, Dunwoody | 70 | Notification received on September 15, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/15/2016 12:00:00 AM |  |  |  |  | 0 | Kinsley Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken water main | The problem was corrected on September 14, 2016 at 12:30 hours when the crew shut the water valves off, open the fire hydrant, stopped the overflow, made the repair to the water line and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-27 | 2017-07-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 3100 Club Dr. - Lawrenceville | 8800 | Fax received 2017-07-27 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/27/2017 12:00:00 AM |  | 7/27/2017 12:00:00 AM |  |  | 1 | Tributary of Sweetwater Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Watered down imperveous surface and collected runoff; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-09 | 2015-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 290 | fax received 10/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/11/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed main line | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-23 | 2015-01-23 | Cochran WPCP | Bleckley | Cochran | Manholes located at S 5th St & E Lewis St, E Peter St & S 5th St, | 2500 | REC EMAIL 1/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0032107 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/23/2015 12:00:00 AM |  | 1/23/2015 12:00:00 AM |  |  | 1 | Jordon Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Groundwater infiltration | City working on inflow/infiltration reduction program | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN | 478-934-3235
2017-10-22 | 2017-10-22 | Columbus Water Works (South WRF) | Muscogee | Columbus | 7791 Stowers Road, Fort Benning, GA | 3233 | Telephone call received on 10/22/2017; fax received on 10/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tributary of Upatoi Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" sewer main was clogged with debris. | Once the debris was cleared, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-19 | 2015-02-19 | Cobb County MS4 | Cobb |  | 2015 Maple Drive | 160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8 in Clay Main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2017-08-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 914 Ridge Av. NW - ATL | 7520 | Fax received 2017-08-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 8/8/2017 12:00:00 AM |  | 8/7/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-24 | 2018-01-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 2634 Binghamton Drive Doraville GA 30360 | 6660 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/24/2018 6:16:00 PM | Ocmulgee |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Root-cut m/h 18-342-s215 and cleared blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Dekablb Co. Water & Sewer
2015-03-03 | 2015-03-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 211 Brookview Dr. | 11700 | REC FAX: 3/3/2015. Follow-up email REC 3/4/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Vandalism |  | Emily Wingo | Emily Wingo | Emily Wingo | 3/3/2015 2:46:00 PM | Flint | 3/4/2015 12:00:00 AM | 2015-03-04 | 2016-03-04 | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 0 | It was due to vandalism. Apparently kids threw everything they could find into the line | Cleared Blockage. Planned follow up: televise line and make repairs as needed. Manholes in the area will be sealed to prevent re-occurrence. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-04 | 0 | 1 | 1 | 1 | 1 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY
2015-12-21 | 2015-12-21 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 1952 Tanglewood Drive | 3340 | fax received 12/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/21/2015 12:00:00 AM |  |  |  |  | 1 | Watson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fractured force main | Repaired force main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-01-16 |  | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant. | 850000 | The local health department was notified on 1/19/18; spill signage posted at the effluent on 1/16/18 and ongoing; public notification was posted at City hall on 1/19/18; and public notification was also published again in The True Citizen on 2/7/18. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/30/2018 12:00:00 AM | Savannah | 1/16/2018 12:00:00 AM | 2018-01-22 |  | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Inadequately treated wastewater was discharged at the wastewater treatment plant effluent due to new mixers (as part of the treatment plant upgrades) installed within the aeration basin continuing to malfunction. The facility discharged water with a BOD concentration greater than 50% of the weekly average. | Signage will be placed at the location of the spill into State waters at the effluent discharge point of the WWTP. The local health department and local media are being notified. Upstream and downstream monitoring is being initiated to determine in there are any immediate or lasting harmful effects from the discharge in the stream. Monitoring is to be implemented for 1 year. The contractor performed site work on the mixers and removed debris in the areas surrounding the mixers. The facility has also extended monitoring to 2-3 additional grab samples per week from the clarifier and the aeration basin for BOD, TSS, NH3 and MLSS, settleability. A plan is being developed by the consultant engineer to remedy the continued malfunctioning of the new mixers. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2018-02-23 | 1 | 1 | 1 | 1 | 0 | 0
2017-05-15 | 2017-05-15 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 1 Ashley Lakes Drive - Peachtree Corners | 2690 | Fax received 2017-05-15 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/16/2017 12:00:00 AM |  | 5/15/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products. | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1833 Slade Drive, Columbus | 18488 | Telephone call and fax received on 01/04/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/4/2017 12:00:00 AM |  |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. Columbus received 2.19 inches of rain on 01/01/2017, and 4.59 inches of rain on 01/02/2017. | Once the rain subsided and flow returned to normal, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2017-12-12 | 2017-12-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2750 Peyton Rd. NW - ATL | 650 | Fax sent 2017-12-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 12/13/2017 12:00:00 AM |  | 12/12/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-24 | 2018-05-24 | Pembroke, City of (Pembroke WPCP) | Bryan |  | Lift Station #1, located at 144 West Ind. Blvd., Pembroke Ga, 31321. | 5000 | does not appear to have impact of marine life this email sent "I just talked to Keith Cook from the city of Pembroke ((912) 213-1777). They had a spill last night (5-24) from around 6:30-8 PM, caused by excessive rainfall. This spill occurred at the manhole at Lift Station #1, located at 144 West Ind. Blvd., Pembroke Ga, 31321. He estimated the volume to be approximately 5,000 gallons, into a drainage ditch to an unnamed tributary to Mill Creek which is in the Ogeechee River Basin. They have cleaned up the area and put out deodorizer. He did not know if this deodorizer contained lime or not. They have not seen anything to suggest a fish kill. They have written a letter to be sent to the health dept. and are going to city hall so it can be distributed among local media outlets. He has also created a sign which will be placed at the site of the spill. | Raw Sewage | Coastal District | GA0038377 | Lift Station | Ditch | Ditch | Hydraulic Overload |  | Brett Berry | Steve Wurtz | Steve Wurtz | 5/25/2018 12:00:00 AM | Ogeechee | 5/25/2018 12:00:00 AM | 2018-05-24 | 2018-05-28 | 1 | tributary of ogeechee Basin | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | several days of rain before spill which was the probable cause of overflow for storm drain, letter sent for file | removal of solids and disinfectant on spill, public notification and letter sent to EPD | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-05-29 | 1 | 1 | 0 | 0 | 0 | 0
2017-05-09 | 2017-05-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1461 Woodbine Ave. SE - ATL | 13500 | Fax received 2017-05-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 5/10/2017 12:00:00 AM |  | 5/9/2017 12:00:00 AM | 2017-05-10 | 2018-05-31 | 1 | Sugar Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed mainline. | Spill was contained using a by-pass pump. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-10 | 0 | 0 | 0 | 1 | 1 | 0
2016-09-16 | 2016-09-16 | Cobb County Water System | Cobb |  | 3111 Port Cobb Drive | 1980 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/16/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids in sewer main | The crews stopped spilled at 1:37 pm | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-12 | 2015-06-12 |  | Fulton | College Park | 4492 White City Rd. College Park, GA 30349 | 1760 |  | Raw Sewage |  |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1825 Clifton Road, Atlanta | 850 | Notification received on September 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/13/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 18:30 hours when the first responder crew completed the repairs on the deteriorated section of the creek crossing sewer line which restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-19 | 2016-12-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4016 Natalie Trail, Ellenwood | 210600 | Notification received on December 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/27/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease blockage | The problem was corrected at 17:00 hours, when a crew pressure washed the 8 inch sewer main 200ft, clearing the grease blockage at 56ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-13 | 0 | 1 | 0 | 1 | 1 | 0
2017-01-04 | 2017-01-04 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 1383 Cambridge Drive | 8640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2017 12:00:00 AM | Ocmulgee | 1/3/2017 12:00:00 AM |  |  | 0 | Big Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage release occurred due to inflow and infiltration related to rain event beginning on January 3, 2017 with an accumulation of nearly 5" inches of rain in a 48 hour rain event. | The contractors have cleaned the site and posted signs indicating the nature of the spill indicating contact information. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 2017-08-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 3480 Mill Creek Road, Brookhaven | 3938974 | Notification received on August 22, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Pipe failure |  |  | Hsin Yeh | Hsin Yeh | 8/17/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | 10 inch sewer main broken | The problem was corrected AT 16:46 hours when the repair crews built a berm to contain the spill until final repairs were completed. The final repair was completed at 22:30, which then restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-22 | 0 | 1 | 0 | 1 | 0 | 0
2015-01-29 | 2015-01-29 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3484 Fairburn Place, NW | 4500 | fax received 1/30/2015. Service Request No. 7386828 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/30/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-29 | 2017-06-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2631 Cascade Rd. SW - ATL | 3105 | Fax received 2017-06-29 | Raw Sewage |  | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/30/2017 12:00:00 AM |  | 6/29/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-30 | 2015-09-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1551 West Nancy Creek Drive, Brookhaven | 3120 | Notification received on October 2, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/1/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary to West Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24" Creek Crossing line leaking. | The problem was corrected at 15:21 hours, when a crew built a berm around 24" Creek Crossing line to contain the spill, repaired the line with a 24" full circle clamp and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-26 | 2015-08-26 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 103 North Cambridge Drive | 2600 | fax received 8/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Rags |  |  | Kim Hembree | Kim Hembree | 8/27/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Tobler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer line. Removed rags from line |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE | 478-414-4059
2016-01-11 | 2016-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1178 Garibaldi Street, SW | 5 | fax received 1/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 1/12/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-18 | 2016-11-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 302 East Howard Avenue, Decatur | 3120 | Notification received on November 22, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | 3rd party contractor |  |  | Hsin Yeh |  | 11/18/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Outside Contractor/Utility | The problem was corrected at 11:10 hours, when the contractor plugged the manhole, installed a bypassed pump, stopped the spill, made the repair to the 8" sewer main and restored the normal flow. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-22 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-12 | 2017-10-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 142 Rhodesia Ave. SE - ATL | 1605 | Fax sent 2017-10-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/13/2017 12:00:00 AM |  | 10/12/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-24 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1011 Lower Poplar Street, Macon (MH #64097) | 97765 | Fax and email received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-26 | 2016-11-28 | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 11800 | 0 | Hydraulic overload, the MWA service area received 5.75 inches of rain from December 21-24. | Debris was removed from the area, and the affected area was disinfected with lime. The MWA will continue its search for I/I into its sewer system through its CCTV and flow monitoring investigations. The MWA also has projects planned to rehabilitate two large sewer interceptors that feed the Lower Poplar Treatment plant. These projects will help to reduce the I/I into the MWA sewer. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-01-21 | 2016-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2300 Defoor Hills Road, NW | 3480 | fax received 1/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/22/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-17 | 2015-03-17 |  | DeKalb | Decatur | 2712 N. Decatur Road, Decatur | 2760 | Notification received on March 19, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 3/17/2015 12:00:00 AM |  |  |  |  | 0 | Tributary to Southfork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected at 9:05 hours when crew cut asphalt around manhole, pressured washed the sewer main 50ft downstream, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-22 | 2018-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1329 North Highland Ave. NE - ATL | 30 | Fax sent 2018-01-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 1/23/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "The main line was holding and cause the back up in the home" | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-12 | 2018-06-12 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4231 Macon Road | 888 |  | Raw Sewage |  | GA0020516 | Collection System | Stream |  | Pipe failure |  |  | Juan Robles | Juan Robles | 6/13/2018 11:39:00 AM |  |  |  |  | 0 | Copper Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A sewer main collapsed causing an overflow into Cooper Creek. The basin is Cooper Creek Basin. | CWW installed a pump around thus stopping the overflow. Once repairs were made the pumps were removed and the main was returned to normal use. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-12 | 2018-06-12 | Columbus Water Works (South WRF) |  |  | 4231 Macon Road | 888 |  | Raw Sewage |  | GA0020516 | Collection System | Stream |  | Pipe failure |  |  | Juan Robles | Juan Robles | 6/13/2018 11:39:00 AM |  |  |  |  | 0 | Copper Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A sewer main collapsed causing an overflow into Cooper Creek. The basin is Cooper Creek Basin. | CWW installed a pump around thus stopping the overflow. Once repairs were made the pumps were removed and the main was returned to normal use. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-13 | 2016-02-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2500 Pinetree Road, NE | 2250 | fax received 2/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/14/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-05 | 2018-01-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3803 Gothic Elm Court, Decatur A 30034 | 5 |  | Raw Sewage |  | GA0024147 | Collection System | Stream | Stream | Operator error |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/5/2018 6:05:00 PM | Ocmulgee | 1/5/2018 12:00:00 AM |  |  | 1 | shoals creek/ unnamed tributiary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | While cleaning lateral, manhole base leaked | Contiuned to rod |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Dekalb Co Dept. Watershed Management
2017-09-07 | 2017-09-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4637 Big Valley Road, Stone Mountain | 206740 | Notification received on September 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/21/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Creek crossing leaking. | The problem was corrected at 20:24 hours when a contractor setup a bypass pump to contain the spill, until repairs can be completed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-26 | 0 | 1 | 0 | 1 | 0 | 0
2018-03-13 | 2018-03-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6509 Veracruse Drive, Morrow | 3600 | Fax received on 3/14/2018. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 3/14/2018 12:00:00 AM |  |  |  |  | 1 | Panther Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-13 | 2017-07-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1330 Miller Reed Av. SE - ATL | 6050 | Fax received 2017-07-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/14/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Construction team made repairs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-28 | 2018-06-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1814 Peachtree Rd. NE - Atlanta | 15 | Fax sent 2018-06-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  |  | Alys Hannum | 6/29/2018 12:00:00 AM |  | 6/28/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | By-pass pump malfunction | Crew made repairs to the by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-07-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-14 | 2015-04-14 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 34.4 mg/L on 04/14/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-19 | 2018-04-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5881 Phillips Drive, Morrow | 6000 | Fax received on 04/20/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 4/20/2018 12:00:00 AM |  |  |  |  | 0 | Conine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage and shot line and returned flow to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-04-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-18 | 2018-03-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1695 Fairburn Rd. SW - Atlanta | 392 | Fax sent 2018-03-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/19/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-10 | 2016-05-10 | Forsyth County (Dick Creek WRF) | Forsyth | Suwanee | 2265 Manor Creek Court | 31135 | verbal notification received 5/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038563 | Collection System | Stream |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/10/2016 12:00:00 AM |  |  | 2016-05-11 | 2017-04-26 | 1 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Gravel from construction site upstream | Jetted the line, vac-ed up grey water, limed the area | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-11 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | Forsyth County
2015-12-30 | 2016-01-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2614 Sue Mack Drive, Columbus | 34508 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2018-07-05 | 2018-07-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1725 Kodiak Circle, Atlanta GA 30345 | 200 | related to 12600 gallon spill at 2234 Fairoaks Court, Decatur in July 5, 2018 Was initially reported as a private | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/6/2018 11:02:00 AM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | root blockage | rodded |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-19 | 2017-12-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 1606 E Fayetteville Rpad, Riverdale MH #2214021 | 9900 | Fax received on 12/20/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/20/2017 12:00:00 AM | Flint |  |  |  | 1 | Camp Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-21 | 0 | 1 | 1 | 0 | 0 | 0
2015-09-29 | 2015-09-29 |  | Rockdale |  | 1436 East View Road | 2320 | Fax received 09-30-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Vandalism |  |  | Dagny Pariani | Reginald Williamson | 9/30/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Boar Tusk Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris from vandalism | Clear and clean manhole and piping |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 89352e56-9649-4d50-9761-577155a9c85b | 2015-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ROCKDALE COUNTY | 770-278-7500
2017-06-02 | 2017-06-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3931 Pleasantdale Road, Doraville | 1250 | Notification received on June 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Hsin Yeh | 6/2/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Cfeek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | The problem was corrected at 12:27 hours when the crew removed the car tire from the manhole invert and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-28 | 2017-12-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Hampton | 11052 Knotty Pine Place - Hampton | 4000 | Fax sent 2017-12-29 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Paul Moisan | 12/29/2017 12:00:00 AM | Flint |  |  |  | 1 | Hurricane Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-31 | 2015-10-31 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 922 Park Place Drive (Outfall) | 6000 | email notification received 11/02/2015. CTS notified also. CTS No.78200. | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Little Haynes Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken force main | Crews repaired section of broken force main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2016-06-15 | 2016-06-15 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 920 Park Place Drive | 14400 | ERT contacted 6/15/2016. CTS No. 80082 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Lift Station | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 6/15/2016 12:00:00 AM |  |  | 2016-06-16 | 2017-07-17 | 1 | Little Haynes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Malfunction at the pump station | The station has been repaired |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-16 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF LOGANVILLE
2016-05-10 | 2016-05-11 | Thomaston, City of | Upson | Thomaston | Old City Hall Lift Station (3rd Ave & L St. SW) | 1600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson |  | 5/11/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was a broken sewer main. | The affected area was clean and disinfected. | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1820 Doug Barnard Pkwy | 8950000 | Verbal notification received 4/02/2016 and 4/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  | Marzieh Shahbazah | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain and possible dislodge influent pump. | After flow returned to normal, the dislodge pump was returned to its proper position. | 33e3f7fa-ee02-11e0-b8d8-000c29971acc | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-312-4154
2016-09-13 | 2016-09-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5686 Boggs Drive, Stone Mountain | 7380 | Notification received on September 15, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/14/2016 12:00:00 AM |  |  |  |  | 0 | Rockbridge Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected on September 13, 2016 at 10:26 hours when the crew turned off the pumps at a nearby lift station, stopped the spill, had the repairing crew completed the repair on the force main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-05 | 2016-08-05 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | Behind 148 Watson Drive | 2530 |  | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 8/5/2016 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Jetted line to break up the blockage, cleaned the line, cleaned up debris from overflow, spread lime over affected area, camera the line to check condition of the pipe | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-29 | 2016-01-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2020 Alison Court, SW | 1710 | fax received 1/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/30/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-03 | 2018-03-03 | Clayton County (Northeast WPCP) | Clayton | Lovejoy | 10952 Knotty Pine, Lovejoy | 7200 | Fax sent on 2018-03-04 | Raw Sewage | Wastewater Regulatory Program | GA0020575 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 3/4/2018 12:00:00 AM |  |  |  |  | 1 | Hurricane Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-20 | Fort Valley, City of (Fort Valley WPCP) | Peach | Fort Valley | Railroad behind Cemetery, beside Bluebird Body Company, Fort Valley | 17280 | Email received on 01/18/2017. | Raw Sewage | Wastewater Regulatory Program | GA0031046 | Collection System | Stream | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/18/2017 12:00:00 AM |  |  | 2017-01-24 |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 12" clay trunk line under Railroad tracks collapsed. | Contractor came in and repaired the broken pipe. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-28 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-24 | 2018-04-24 | Cobb County Water System | Cobb |  | 225 Fontaine Road | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/24/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural failure | The Water System was notified at 11:07 a.m. and our crew stopped the overflow at 12:40 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-24 | 2018-04-24 | Cobb County Water System | Cobb |  | 225 Fontaine Road | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/24/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural failure | The Water System was notified at 11:07 a.m. and our crew stopped the overflow at 12:40 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Highway 11 North Lift Station - Social Circle | 250 | Phone notification 2017-09-13. Fax sent 2017-09-14 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Pump Station | Ground | Swale | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/13/2017 12:00:00 AM |  | 9/13/2017 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage from Hurricane Irma | Used portable generator to stop overflow. Pumped wet well down with pump truck. Lime applied to site and signs posted. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-15 | 2016-04-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 311 Scott Street, SW | 6000 | fax received 4/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/17/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-05 | 2018-09-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4104 Tahoe Court Stone Mountain GA 30083 | 3660 | manhole 18-014-s074 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System |  |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/5/2018 8:59:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | pressure washed to clear grease |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-29 | 2015-08-29 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Reynolds & Mansfield Street Lift Station 4002 | 1000 |  | Raw Sewage | Coastal District | GA0025313 | Lift Station | Storm Drain | Bay | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 8/29/2015 4:07:00 PM | Satilla | 8/29/2015 12:00:00 AM |  |  | 1 | Oglethorpe Bay | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station 4002 was unable to maintain flow due to the amount of storm water infiltration. | A by-pass pump was installed to Lift Station 4002. Vac-Con trucks recovered approximately 700 gallons. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-09-11 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1200 Block of Lake Drive | 33900 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-02-06 | 2015-02-06 |  | Columbia |  | 5089 Windmill Lake Drive | 250 | Received by Fax on 2/6/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Rags |  |  | Sarita Banjade | Sarita Banjade | 2/6/2015 12:00:00 AM |  |  |  |  | 1 | Private Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Rags | 'Unstopped sewer main with high pressure jet machine. Limed and cleaned up. Posted signs. Planned Video inspection.' |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-02-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY WATER UTILITY | 7068636928
2017-12-26 | 2017-12-26 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 9680 Ivey Ridge Circle - Jonesboro | 2400 | Fax sent 2017-12-27 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Paul Moisan | 12/27/2017 12:00:00 AM | Flint |  |  |  | 1 | Swamp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Site was mitigated, work orders generated for additional work to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | chamblee | 2748 South Bamby Lane, Chamblee | 1000 | Notification received on August 19, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/18/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris blockage | The problem was corrected at 11:40 hours, when the clean-up crew, pressure washed the 18" sewer main a total of 600 ft upstream, eliminated obstructiona t 50 ft and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-10 | 2016-02-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2177 Parkview Run, NW | 20 | fax received 2/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/11/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-09 | 2017-03-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1319 Halter Lane, Lithonia | 40 | notification received on March 10, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/9/2017 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station pump failure. | The problem was corrected at 13:04 hours when a crew pumped down the lift station, stopped the overflow and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-10 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-29 | 2017-06-29 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 3519 Stone Cliff Way in Eagle Watch Golf Course Woodstock | 3000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/8/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hole in 10 inch main | Construction crews fixed the main with a band and the main was put back in service | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-09 | 2017-01-09 | Jackson, City of (Yellow Water Creek WPCP) | Butts | Jackson | Brownlee Rd @ right of way - Jackson | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0021831 | Collection System |  |  | Debris |  |  | Alys Hannum | Hsin Yeh | 1/9/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Jetted and uncleared sewer main |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-28 | 2017-06-03 | Andersonville, City of (Andersonville WPCP) | Sumter | Andersonville | Outfall into the unnamed tributary that flows into Sweetwater Creek. | 10000 | Mr. Stephen Hilliard contacted Mr. Jay Howell on June 8, 2017 to notify this Division of the through plant spill. | Treated Effluent | Southwest District | GA0033669 | WWTP | Stream |  | Wet weather |  | Jay Howell | Linda Stevens | Linda Stevens | 6/8/2017 12:00:00 AM | Flint |  | 2017-06-08 |  | 1 | Unnamed Tributary to Sweetwater Creek to the Flint River in the Flint River Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | This was a through plant spill that was likely caused by heavy rainfall in the area combined with inflow and infiltration issues within the City's sewerage collection system. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 2017-07-05 | 1 | 1 | 0 | 1 | 1 | 1
2015-08-31 | 2015-08-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 80 Peachtree Park Drive,NE | 357 | fax received 9/01/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/1/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-11 | 2017-01-11 | Cobb County Water System | Cobb |  | 3185 Brookview Rd. | 5700 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Flushed and limed area | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | Richard Richey |  | Cobb Co Water & Sewer
2016-02-04 | 2016-02-05 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1200 Block of Wainwright Street | 90500 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-11-16 | 2017-11-16 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 2411 Bailey Road - Norcross | 4611 | Fax sent 2017-11-16 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | 3rd party contractor |  |  | Alys Hannum | Alys Hannum | 11/16/2017 12:00:00 AM |  |  |  |  | 1 | Unnamed Trib. of Bromolow Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Third party damage - pipe broken during tree work | Raked area and spread lime. Posted signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2614 Sue Mack Drive, Columbus, GA | 43073 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Lindsay Creek. | Once the rainfall subsides and flow returns to normal, the overflow is anticipated to stop. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 1 | 1 | 0 | 1 | 0 | 0
2015-08-13 | 2015-08-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snapfinger Woods Drive, Decautur | 1120 | Notification received on August 14, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/13/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary to Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:51 hours, when the clean-up crew, rodded the sewer main6' downstream and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-23 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2225 Waterville Road, Macon MH #56575 | 27040 | Fax and email received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/24/2015 12:00:00 AM | 2015-12-29 | 2016-11-28 | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Hydraulic overload due to 5.75 inches of rain from December 21-24. | The manhole is located in the street. The street was washed down and debris removed. MWA will continue its search for inflow and infiltration into its sewer system through CCTV and flow monitoring investigations and will develop rehabilitation projects based on this information and contractor conducted sewer evaluations. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2015-12-30 | 2015-12-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Woodbine Circle, SE | 85 | emailed received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-23 | 2015-12-23 | Warner Robins, City of (Sandy Run Creek WPCP) |  | Warner Robins | 267 Shannon Ridge Drive, Warner Robins | 225000 | Notification received on December 24, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0030325 | WWTP | Stream |  |  |  |  | Hsin Yeh | Hsin Yeh | 12/23/2015 12:00:00 AM |  |  |  |  | 0 | Sandy Run Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Excessive rainfall | Excessive rainfall in the Warner Robins area caused high infiltration and inflow into the collection system. The rainfall caused the sewer system to surcharge the manholes in the area of the spill. The manhole failed when the bricks just below the concrete manhole ring gave way allowing inflow to exit from the collection system. The spill stopped when the flow decreased and the surcharged manhole level dropped below the level of the failed manhole wall. The City is pouring a concrete patch to provide a temporary repair to this manhole on December 23rd. In addition, the City has a design contract under way to rehabilitate this portion of the collection system. The rehab will include replacing this manhole. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-28 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 |  | Baldwin | Milledgeville | Central Shop Rd. by Camp Creek | 2190 | Spill to State Waters | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2017 12:00:00 AM | Oconee | 1/23/2017 12:00:00 AM |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Other 2x4 Lumber, Cloth Towels | Rodded sewer main on January 23, 2017 at 12:35 PM | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-26 | 2017-12-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 761 Woodward Way NW - ATL | 250 | Fax sent 2017-12-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 12/27/2017 12:00:00 AM |  | 12/26/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-24 | 2017-07-24 | Commerce, City of (Northside WPCP) | Jackson | commerce | Manhole B-120 | 5000 |  | Raw Sewage | Wastewater Regulatory Program | GA0026247 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/24/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Cornelia, City of (Cornelia WPCP) | Habersham | Cornelia | J Warren North Lift Station | 3000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | Collection System | Stream | Stream | Natural Disaster |  | Brian Koehler | Brian Koehler | Brian Koehler | 9/14/2017 12:00:00 PM | Chattahoochee | 9/12/2017 12:00:00 AM | 2017-09-12 | 2017-09-19 | 0 | tributary to the North Fork of Little Mud Creek | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-490-4613 | CITY OF CORNELIA WPCP
2015-03-25 | 2015-03-25 |  | DeKalb | Doraville | 3567 Hidden Acres Drive, Doraville | 1520 | Notification received on March 26, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 3/25/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage | The problem was corrected at 13:28 hours when a crew rodded and pressure washed the 8" sewer main 320ft upstream, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-21 | 2017-06-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2660 Peachtree Rd. NW - ATL | 1720 | Fax received 2017-06-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 6/22/2017 12:00:00 AM |  | 6/21/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-06-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-25 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3221 Broadway, Macon (MH #57899) | 57810 | Fax and email received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-26 | 2016-11-28 | 1 | Ephemeral drainage ditch with no known outlet | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Hydraulic overload. The MWA service area received 5.78 inches of rain from December 21-26. | The manhole is located in the street. The street has been washed down and any debris removed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2018-04-02 | 2018-04-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2923 Greenbush Place, Atlanta GA 30345 | 2340 | manhole 18-208-s075 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain | Stream | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/3/2018 4:46:00 PM | Ocmulgee |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Root cut |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1200 Block of Wainwright Drive - Valdosta | 9800 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/22/2017 12:00:00 AM | 2017-01-22 |  | 1 | One Mile Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Large amounts of rainfall in excess of 6 inches within a 24-hour period. | Cleanup and disinfecting at overflow location and stream discharge points. Began monitoring and testing the area.The location has been added to the city's list for rehabilitation. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-26 | 2015-06-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2500 Center Street, NW | 4290 | fax received 6/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/29/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-14 | 2016-02-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2209 Wingate Street, SW | 65 | fax received 2/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 2/23/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew replaced the suction hole |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-26 | 2017-04-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3669 Martin L. King Jr. Dr. NW - ATL | 775 | Fax received 2017-04-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/27/2017 12:00:00 AM |  | 4/26/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-28 | 2018-02-28 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 426 Ronthor Drive - Social Circle | 600 | Email sent 2018-03-01 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 3/1/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken clean-out on adjacent lateral line. | Property owner was notified that the clean-out was broken and must be repaired. Crew used a jet machine to clear the grease/paper blockage. Degreaser was applied to sewer main, lime was applied to the spill site. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-29 | 2015-06-29 | Brunswick-Glynn County JWSC (Exit 29 WPCP) | Glynn |  | 2752 US Highway 17 near exit 29 interstate I-95 | 1200 |  | Raw Sewage | Coastal District | GA0038938 | Collection System | Basin | Ditch | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 6/29/2015 3:00:00 PM | Satilla | 6/29/2015 12:00:00 AM |  |  | 1 | Fancy Bluff Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by debris within the collection line. | The debris was removed and catch basin was pumped out to remove as much sewage a as possible. Approximately 1000 gallons was collected. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-07-02 | 1 | 1 | 0 | 0 | 0 | 0
2017-02-24 | 2017-02-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1868 Winthrop Drive, Atlanta | 13161 | Notification received on February 28, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/24/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:33 hours when a crew pressure washed the 8" sewer main between manholes 417ft, removed the blockage at 200ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-28 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-17 | 2018-05-17 | Cobb County Water System | Cobb |  | 170 Holt Rd | 160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/17/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural failure/creek crossing broke down, 8 " clay mainconnecting to ductile iron. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-21 | 2017-05-21 |  | Upson | Thomaston | Tanglewood Drive | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/21/2017 12:00:00 AM | Flint |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line blockage | The debris was removed. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-08 | 2017-08-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2407 Miriam Lane, Decatur | 30 | Notification received on August 11, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/9/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A broken 6-inch lateral. | The problem was corrected on August 3, 2017 at 11:47 hours when the contractor completed the dye test and stopped the spill. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-14 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5900 North Cheryl Drive, Morrow | 148000 | Telephone call received on 12/30/2015. Fax received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Severe rain event caused hydraulic overload on system. | Lines upstream of event will be inspected for I/I. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-23 | 2016-01-04 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2250 Mallard Ave., Macon MH # 55952, 55951 | 1685215 | Fax and email received on 01/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/28/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-26 | 2016-11-29 | 1 | Ditch feeding Rocky Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was hydraulic overload. MWA service area received 12.62 inches of rainfall duirng December 2015. | Debris was removed and the area was disinfected with lime. MWA will continue its search for I/I into its sewer system. The MWA will also research a possibile rehabilitation project in order to correct hydraulic issues in this area. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-07 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-02-23 | 2016-02-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1731 S. Gordon Street, SW | 50 | fax received 2/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/24/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-07 | 2016-11-07 | Cobb County Water System | Cobb |  | 1024 Ector Chase/Stilesboro Road | 210 |  | Raw Sewage | Wastewater Regulatory Program | GAW000527 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 inch PVC Main | Lime Spill Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-31 | 2015-04-01 | McRae-Helena, City of (McRae-Helena WPCP) | Dodge | Helena | Homer Avenue behind Telfair State Prison in Helena, GA. | 3500 | PN requirements completed on 4/1/2015 and copies of PN provided to SW District Office and are attached. | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ditch | Ditch | Power failure |  | Jay Howell | Jay Howell | Jay Howell | 4/1/2015 9:00:00 AM | Ocmulgee | 4/1/2015 12:00:00 AM |  |  | 0 | Unnamed tributary to Little Ocmulgee River Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | power outage at lift station. | power restored to lift station upon discovery. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-04-28 | 1 | 1 | 1 | 0 | 0 | 0
2015-03-31 | 2015-04-01 | McRae-Helena, City of (McRae-Helena WPCP) | Dodge |  | Homer Avenue behind Telfair State Prison in Helena, GA. | 3500 | PN requirements completed on 4/1/2015 and copies of PN provided to SW District Office and are attached. | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ditch | Ditch | Power failure |  | Jay Howell | Jay Howell | Jay Howell | 4/1/2015 9:00:00 AM | Ocmulgee | 4/1/2015 12:00:00 AM |  |  | 0 | Unnamed tributary to Little Ocmulgee River Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | power outage at lift station. | power restored to lift station upon discovery. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-04-28 | 1 | 1 | 1 | 0 | 0 | 0
2017-01-12 | 2017-01-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1107 Seaboard Ave, NW - ATL | 20 | Fax received on 01/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan |  | 1/13/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-05-18 | 2015-05-18 |  | DeKalb | Atlanta | 1760 Mason Mill road, Atlanta | 5040 | Notification received on May 19, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/18/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary to South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blocakge | The problem was corrected at 12:10 hours when a crew rodded the 8" sewer main 174ft upstream, clearing the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-05-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-18 | 2015-11-19 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Social Circle Little River WPCP | 451383 | verbal notification received 11/19/2015 | Primary Effuent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/19/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Due to hydraulic overload, the motors at the end of the aeration basin had to be shut down. | When hydraulic flow in to the plant slowed, the motors were turned back on. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-24 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE | 770-464-2380
2017-01-09 | 2017-01-10 |  | DeKalb | Doraville | 2746 Laurelwood Road, Doraville | 56140 | Notification received on January 11, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/10/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The crew experienced difficulty accessing the area but were able to clear the blockage and restore normal service on January 10th at 10:00. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-11 | 2015-11-11 | Paulding County (Pumpkinvine Creek WRF) | Paulding |  | Graves Road | 1500 | Have scada checked out/Monitor | Raw Sewage | Mountain District - Cartersville | GA0039021 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 11/11/2015 12:00:00 AM | Coosa |  |  |  | 0 | Branch of Westbrook Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station out of commision | Reset pump station / have soft start checked out | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey | 770-655-8342 | PAULDING CO
2016-06-11 | 2016-06-11 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 3495 Old Petersburg Road | 3200 | fax received 6/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/13/2016 12:00:00 AM |  |  |  |  | 1 | Kelley Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Unstopped sewer main with high pressure jet machine. Cleaned up overflow. Posted signs. Follow up sewer main cleaning and CCTV inspection. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY | 706.863.6928
2017-06-18 | 2017-06-18 | Cobb County Water System | Cobb |  | 3627 Stonehenge Way | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/18/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rubes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | stopped the spill and cleaned out manhole and spread lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-03 | 2015-02-03 |  | DeKalb | Lithonia | 3788 Crossvale Road, Lithonia | 3492 | Notification received on February 5, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 2/4/2015 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole damage | The problem was corrected at 1:45 hours when a crew installed a bypass pump, made repair and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-22 | 2016-11-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1488 Metropolitan PKWY, SW, ATL | 1710 | Fax received on 11/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 11/23/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crew made repairs to the mainline. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-28 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 9020000 | CTS No. 78615 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-12 | 2018-06-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5004 Vermack Road Dunwoody GA 30338 | 4020 | manhole 18-368-s099 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/13/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-08 | 2017-05-08 | Columbia County (Little River WPCP) | Columbia | Evans | 2063 Egret Circle - Evans | 1000 | Fax received 2017-04-09 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/9/2017 12:00:00 AM |  | 5/8/2017 12:00:00 AM |  |  | 1 | Tributary to Jones Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction Debris | Unstopped sewer with high pressure jetting machine. Spread lime. Posted signs. Follow up cleaning of sewer main and video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-07 | 2018-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | CORRECTION: 1004 Woodland Ave. SE - Atlanta 1008 Woodland Ave. SE - Atlanta | 1000 | Fax sent 2018-06-08 CORRECTION sent 2018-06-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/8/2018 12:00:00 AM |  | 6/7/2018 12:00:00 AM |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-12 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-08 | 2018-08-08 | Pine Mountain, Town of (Pine Mountain WPCP) | Harris |  |  | 500 |  | Raw Sewage | West Central District | GA0025691 | Lift Station | Stream | Stream | Equipment failure |  |  |  | Stephanie Edwards | 8/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 426838fe-eb6e-11e0-b8d8-000c29971acc |  | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2300 Defoor Hills Road, NW | 1100 | fax received 1/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/23/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Th crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-11 | 2017-09-11 | Jesup, City of (Jesup WPCP) | Wayne | Jesup | US 301 North Lift Station | 7500 |  | Raw Sewage | Coastal District | GA0026000 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/11/2017 12:00:00 PM | Altamaha | 9/11/2017 12:00:00 AM |  |  | 1 | Penholloway Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power | Used diesel by-pass until power was restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-11 | 2015-12-11 | Tifton, City of (New River WPCP) | Tift | Tifton | 109 Lakewood Drive, Tifton, GA | 1800 | Telephone call received on 12/11/2015, followed up by a written report received on 12/16/2015. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch |  | Roots |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/11/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was root intrusion into the sewer main. | The service line was repaired, and the area was cleaned and disinfected. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-29 | 2015-01-29 | Sylvania, City of (Sylvania WPCP) | Screven | Sylvania | West Ogeechee St above Blalock L.S. | 400 |  | Raw Sewage | Coastal District |  | WWTP | Ground | Ditch | Debris |  | Steve Fox | Steve Fox | Steve Fox | 1/29/2015 12:00:00 AM | Savannah | 1/29/2015 12:00:00 AM |  |  | 1 | Savannah River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | See Mike Smith's Comments: "On January 29, 2015 at 1510 hours we experienced a high level alarm at the Blalock Lift Station via our SCADA. The only other assumption I can make is maybe there was some blockage in the drainage area that let loose and the resulting water over taxed the pumps." At 1530 hours the | See Mike Smith's Comments: "Crews were immediately dispatched along with myself. When we arrived at 1513 hours we found the lift station starting to overflow.We found both lift station pumps running and pressures indicated they were pumping as designed. I immediately dispatched a crew to the manhole where the force main dumps. The flow there indicated the same as the pump data. The flow indicated no blockage in the force main. The crew then immediately began to open manholes in the Sylvan Heights area to assess the severity of the back up. The only one backed up was the manhole located at West Ogeechee Street above the lift station.Another crew was dispatched to the Bi Lo Lift Station and it was found to be operating as designed and no back up. This station was placed in the off position until the problem could be determined. This station was placed back in service at 1535 hours.Crews are cleaning the area and will apply lime to areas we can access. I will notify the local health " | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-03-13 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-08 |  | SOUTH COBB WATER RECLAMATION FACILITY | Cobb |  | 777 Townpark Ln | 920 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/8/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 15" Main Line | The crew were able to stop the spill and wash down the area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-04 | 2015-03-05 | Thomaston, City of | Upson | Thomaston | 512 North Center Street | 3500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-17 | Fulton County (Big Creek WPCP) | Fulton |  | Azalea Drive/Riverside Road Roswell 30075 | 1954359 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2015 12:00:00 AM | Chattahoochee | 11/2/2015 12:00:00 AM |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rains caused Big Creek to overflow the Banks and inundate the sewer system along the Chattahoochee River and Big Creek. | Ongoing I/I Reduction Program | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-27 | 2015-02-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2150 Joseph E Boone Blvd. NW | 2340 | fax received 2/28/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/28/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-04 | 2018-02-04 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 682 Meadowbrook Drive - Winder | 575 | Email sent 2018-02-04 | Raw Sewage | Wastewater Regulatory Program | GA0038776 |  | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 2/4/2018 12:00:00 AM |  | 2/6/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Cedar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rain | Area sanitized with powdered lime. Line will be CCTV'ed. UPDATE: Roots found and removed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-06 | 2017-02-06 | Cobb County Water System | Cobb |  | 1306 Old Powder Springs Rd. | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Pine creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Clay Main | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-05 | 2017-01-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6691 Tribble Street - Lithonia | 9840 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Hsin Yeh | 1/6/2017 12:00:00 AM |  | 1/5/2017 12:00:00 AM |  |  | 1 | Polebridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease caused a blockage in the manhole. | Pressure washed around the manhole to restore flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 4100 Block of Bemiss Road | 2000 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Cherry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-01-16 | 2016-01-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4520 Riverwood Cricle, Decatur | 1500 | Notification received on January 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/16/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:00 hours, when a crew rodded the main, cleared the blockage at 150ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-01 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-30 | 2017-09-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 679 Blue Ridge Drive - Forest Park Manhole - 2194293 | 3750 | Fax received on 10/01/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 10/1/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Poole Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Roots | Blockage was cleared and flow was returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-02 | 0 | 1 | 1 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Tifton, City of (New River WPCP) | Tift | Tifton | 61 TC Golden Road, Tifton | 63000 | Email received on 04/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Suwannee |  | 2016-04-04 | 2017-04-24 | 1 | Cow House Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall event that occurred on April 1-2, 2016. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 1 | 1 | 0
2015-06-26 | 2015-06-26 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 273 Industrial Park Drive | 44400 | ERT contacted 6/26/2015, CTS No. 77139. WRP notified verbally 6/26/2015. Fax received 6/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Other |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/26/2015 12:00:00 AM |  |  |  |  | 1 | City Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Broken 8" sanitary sewer main |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-12-30 | 2015-12-30 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Manhole No. 1269, near 444 Brauham Circle | 48375 | fax received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Stroud's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-04-13 | 2016-04-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 431 Glen Iris Drive, NE | 5 | fax received 4/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/14/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-02 | 2017-03-02 | Cobb County Water System | Cobb |  | 391 Pine Valley Road | 210 |  | Raw Sewage |  |  | Collection System | Stream |  | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-05 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1400 Block of Gornto Road - Manhole No. 0036 | 173750 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-03-09 | 2018-03-09 | Dahlonega, City of (Dahlonega WPCP) | Lumpkin |  | Hwy 9 South directly across from Trammel Tie (1651 Morrison Moore Parkway West) | 4500 |  | Raw Sewage | Mountain District - Cartersville | GA0026077 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/20/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Barlow Branch tributary to Cane Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Force Main | Replaced broken pipe | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-24 | 2015-03-24 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 40.0 mg/l
2015-12-24 | 2015-12-24 |  | Cobb |  | 787 Stone Harbor Pkwy | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain Surcharge/Infiltration in 8 inch Clay Main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-09 | 2016-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 E. Pelham Road, NE | 10 | fax received 02/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/10/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-02 | 2017-01-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4824 A Miller Road, Manhole #2, Columbus | 27916 | Telephone call and fax received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Cooper Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Cooper Creek. Columbus received 2.19 inches of rain on 01/01/2017, and 4.59 inches of rain on 01/02/2017. | Once the rain subsided and flow returned to normal, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2017-01-02 | 2017-01-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4824 A Miller Road, Manhole #2, Columbus | 27916 | Telephone call and fax received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Cooper Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Cooper Creek. Columbus received 2.19 inches of rain on 01/01/2017, and 4.59 inches of rain on 01/02/2017. | Once the rain subsided and flow returned to normal, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2016-05-25 | 2016-05-25 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 2929 Cardinal Trace | 2102 | fax received 5/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/26/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Sweetwater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-12-15 | 2017-12-15 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | Between MH#1163 and MH#1003 | 4500 | Spill notice placed on City Web Page and City Channel | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Contractor |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/15/2017 12:00:00 AM | Coosa |  |  |  | 0 | Weaver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor cutting R/W for Georgia Power, hit aerial line with bushhog, causing a break in line, blockage and spill | Vacuumed all liquids pooled on ground once blockage was broke free in line, cleaned area of all solids and debris, applied line to affected area | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-12-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3420 East Lindsay Drive / Flint Drive, Columbus, GA | 27388 | Fax received 12/25/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/25/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Lindsay Creek. | Once the rain subsided and flows returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-18 | 2016-05-18 | Cedartown, City of (Cedartown WPCP) | Polk |  | Clyde Drive | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0024074 | WWTP | Stream |  | Grease |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 5/18/2016 12:00:00 AM | Coosa |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease caused a blockage in the main sewer line causing manhole to back up and run over | Line has been upstopped and we will continue to monitor this location for farther problems | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 796 Gracewood Ave. SE - ATL | 2860 | 5-Day report received via mail 2017-10-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/11/2017 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed water main caused the sewer main to fill and overflow. | Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-07 | 2017-05-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4076 Sonoma Wood Trail, Decatur | 4000 | Notification received on May 9, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/7/2017 12:00:00 AM |  |  |  |  | 0 | Lehigh Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:30 hours when a crew pressure washed 8" sewer main 60 ft., cleared the blockage at 15 ft, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-13 | 2015-10-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 240 | fax received 10/14/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/14/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed main line | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-28 | 2018-07-28 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | 101 Blain Street | 100000 |  | Raw Sewage | Coastal District | GA0025313 | Force Main | Stream | Stream | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/28/2018 12:00:00 AM | Satilla | 7/29/2018 12:00:00 AM | 2018-07-28 |  | 1 | Hog Crawl & Hidden Lakes Drainage Lake | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Malfunction of a gasket on a 16" PVC C-900 force main by-pass that was installed by a contractor lass than 6 months ago. | 2 vac trucks used to stop the spill until repairs were made:The force main connection/gasket has been properly installed by contractors before placing back into service. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-08-03 | 1 | 1 | 0 | 0 | 0 | 0
2016-08-21 | 2016-08-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3000 Martin Luther King, Jr. Drive, SW | 2205 | fax received 8/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/22/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-07 | 2018-01-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 6701 Peachtree Industrial Boulevard Doraville GA 30360 | 8000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/8/2018 7:18:00 AM | Ocmulgee | 1/7/2018 12:00:00 AM |  |  | 1 | Nancy Creek and unnamed tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | sewer main break | sewer pump bypass sewer |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | Earnest Veal |  | Dekalb Co Dept. Watershed Management
2016-03-28 | 2016-03-28 | Rome, City of (Coosa WRF) | Floyd |  | Dead End of Garrard Avenue | 4500 |  | Raw Sewage | Coastal District | GA0024341 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 3/29/2016 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Little Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots in the sewer main | The sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1357 Deerwood Drive, Decautr | 181760 | Notification received on October 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/11/2016 12:00:00 AM |  |  |  |  | 0 | Shoals Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 20:05 hours, when a crew contained the spill by building a berm, replacing a section of the 18" sewer main to make a permanent repair and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-17 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-19 | 2018-07-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 58880000 | This spill is also entered as a violation. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 7/23/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | South River Major TSS Spill From midnight July 19 to midnight July 20, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. July 19 TSS - 26 mg/L July 20 TSS - 25 mg/L Permit Limit = 15 mg/L | Seeking additional landfill options for the removal of excess solids. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-20 | 2015-02-20 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3438 Stratford Road, NE | 5 | fax received 2/21/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 2/21/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-20 | 2015-05-20 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Yam Grandy WWTP | 50000 |  | Treated Effluent | Wastewater Regulatory Program | GA0039225 | WWTP | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/21/2015 12:00:00 AM |  |  |  |  | 1 | Yam Grandy Creel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A leak was discovered in the effluent discharge pipe. | Effluent line being repaired | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO
2015-01-22 | 2015-01-22 |  | DeKalb | Stone Mountain | 4154 Redan Road, Stone Mountain | 6000 | Notification received on January 23, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/22/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 15:47 hours when a crew pressure washed the 8" sewer main 100ft upstream, cleared the grease blockage, and restored services |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Highway 278 Lift Station - Social Circle | 200 | Voicemail received 2018-01-16 | Raw Sewage | Wastewater Regulatory Program | GA0026107 |  | Ground | Swale | Equipment failure |  |  | Alys Hannum | Alys Hannum | 1/17/2018 12:00:00 AM |  | 1/16/2018 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical malfunction | A sign was posted to notify the public. Lime applied to spill site. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-17 | 2015-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3761 Rockport Place, SW | 800 | fax received 12/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/18/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-15 | 2017-11-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1635 Sugar Downs Court, Atlanta | 100 | fax received on 11/16/17 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 11/16/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Sugar Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe leakage | Contained spills on 11/16/2017 until final repairs are made |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-17 | 0 | 1 | 0 | 0 | 0 | 0 | Nghai Suggs |  | DeKalb County
2015-12-13 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 22500 | Verbal notification received 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outfall No. 3 plug failure |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-26 | 2018-06-26 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | Withlacoochee WWTP - Valdosta | 300000 | Phone call received 2018-06-26 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | WWTP | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 6/26/2018 12:00:00 AM |  | 6/26/2018 12:00:00 AM |  |  | 0 | Unnamed Trib. to Withlacoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "The City of Valdosta's Withlacoochee Wastewater Treatment Plant experienced some equipment malfunction as the bar screens designed to remove debirs from incoming water faulted due to weather related issues. | However, the operator on shift was able to identify the issue and correct the problem, but not before approximately 300,000 gallons of primarily storm water spilled onto the city plant property as well as into a nearby waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Arrowhead Park on Arrowhead Drive, Tobesofkee Park, Macon MH ID 69430 | 5125 | Call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Lake Tobesofkee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was hydraulic overload due to heavy rains in the MWA service area. According to the National Weather Service, Macon-Bibb County received 5.42 inches of rain on Friday, April 1st. | Debris was removed from the area and the affected area has been disinfected with lime. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-04 | 2017-04-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Piedmont Rd. NE - ATL | 5000 | Fax received 2017-04-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/5/2017 12:00:00 AM |  | 4/4/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 485 Valleyview Drive | 3000 | ERT Notified 2/03/2016. CTS No. 78978 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Cedar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | Cleared blockage and removed roots |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER
2017-04-05 | 2017-04-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 506 South McDonough Street, Decatur | 3600 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 16:00 hours, when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Monroe, City of (Jack's Creek WPCP) | Monroe | Monroe | King's Ridge Easement - Monroe | 4800 |  | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 1/17/2017 12:00:00 AM |  |  |  |  | 0 | Mt. Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Grease | Cleaned up location and spread lime |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-09 | 2017-01-09 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Sugar Hill | 4685 Pine Isle Way - Sugar Hill | 4472 | Fax received 2017-01-10 | Raw Sewage |  | GA0038130 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Hsin Yeh | 1/9/2017 12:00:00 AM |  | 1/9/2017 12:00:00 AM |  |  | 1 | Level Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Raked area and spread lime. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | 3983 Darien Highway, Brunswick | 10000 |  | Raw Sewage | Coastal District | GA0025313 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2016 9:00:00 AM | Satilla | 10/27/2016 12:00:00 AM | 2016-10-27 |  | 1 | Hog Crawl Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Lift Station (#4048) power failure due to Hurricane Matthew. | A 300 kw generator was connected to restart the lift station until permanent power was restored days later. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-31 | 1 | 1 | 0 | 0 | 0 | 0
2015-09-11 | 2015-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1150 Collier Road, NW | 835 | fax received 8/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/12/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-24 | 2016-12-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 45 Royce Drive, Riverdale | 400 | Fax received on 12/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/24/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause was grease in the line. | Cleared blockage and flow returned to normal. Line will be televised to determine if any structural repairs are needed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2018-07-24 | 2018-07-25 | Macon Water Authority (Rocky Creek WPCP) | Macon | Macon | Corbin Avenue Lift Station, MH ID 69834 | 34005 |  | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Lift Station | Ditch | Ditch | Hydraulic Overload |  |  | Juan Robles |  | 7/25/2018 12:00:00 AM |  | 7/25/2018 12:00:00 AM |  |  | 0 | Bowman Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to heavy rains in the MWA service area. | Debris will be removed from the area and disinfected with lime. |  |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-06 | 2015-11-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1620 Ezra Church Drive, NW | 2485 | fax recieved 11/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-22 | 2018-03-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Northside Dr. NW Springlake Dr. NW - Atlanta | 22 | Fax sent 2018-03-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 |  | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/23/2018 12:00:00 AM |  | 3/23/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-09 | 2015-04-09 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Hospice of the Golden Isles at the intersection of Glynco Parkway & Hibbard Lane. | 700 |  | Raw Sewage | Coastal District | GA0025313 | Force Main |  | Ditch | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/9/2015 12:17:00 PM | Satilla | 4/9/2015 12:00:00 AM |  |  | 1 | Ditch leading to Yellow Bluff Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ruptured sewer main caused during the process of cleaning the roadside ditch. | Sewer main was repaired and cleaned up area and disinfected with lime. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-04-15 | 1 | 1 | 0 | 0 | 0 | 0
2015-10-26 | 2015-10-26 |  | Upson | Thomaston | 649 S. Center Street | 6755 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/26/2015 12:00:00 AM | Flint |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill is a broken sewer main. | Debris will be removed from the surronding area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-17 | 2018-07-17 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 2987 Samples Road - Cumming | 600 | Email sent 2018-07-18 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Pump Station | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/18/2018 12:00:00 AM |  | 7/17/2018 12:00:00 AM |  |  | 1 | Haw Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Leaking pipe gasket | Gasket replaced; area cleaned of debris; lime applied; signage posted; Health Dept. notified |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-01 | 2015-09-01 | Social Circle, City of (Little River WPCP) | Morgan | Social Circle | GDOT Rest Area No. 52 | 500 | fax received 9/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Power failure |  |  | Kim Hembree | Kim Hembree | 9/2/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lightening strike that knocked out the control circuit power. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-02-23 | 2016-02-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jester Lake Drive, Jonesboro Manhole 2215621 | 121500 | Telephone call received on 02/23/2016; fax received on 02/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan |  | Paul Moisan | 2/23/2016 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | Capacity due to heavy rainfall | Televise lines and if problem is found, make a repair. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-02-29 | 0 | 1 | 1 | 0 | 0 | 0
2017-07-17 | 2017-07-22 | Cuthbert, City of (Cuthbert WPCP) | Randolph | Cuthbert | Town Branch Creek Tributary to Carter Creek (Flint River Basin) | 0 | PN in The Southern Tribune, dated August 3, 2017. | Treated Effluent | Southwest District | GA0037249 | WWTP | Stream | Stream | Equipment failure |  | Linda Stevens | Linda Stevens | Linda Stevens | 7/23/2017 9:47:00 AM | Flint | 8/2/2017 12:00:00 AM | 2017-07-20 | 2018-07-25 | 1 | Town Branch Creek Tributary to Carter Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The effluent decanter lost prime on the south basin, which prevented any effluent from leaving the basin. This caused the water level to rise in the basin, triggering the SBR to go into storm mode and overloaded the north basin. It was a through plant spill with elevated levels of Total Suspended Solids. | The decanter was repaired. | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 2017-09-29 | 1 | 1 | 0 | 1 | 1 | 0
2017-06-21 | 2017-06-21 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 226 Cherry Bark Way | 650 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Equipment failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 6/21/2017 12:00:00 AM | Coosa |  |  |  | 0 | Logan Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment malfunction at Dalton Utilities Lift Station | Restored pumps to operation Faulty equipment replaced. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-31 | 2017-06-01 | Temple, City of (Temple WPCP) | Carroll | Temple | Villa Rosa Lift Statopm | 360000 |  | Raw Sewage | Wastewater Regulatory Program | GAJ020134 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/7/2017 12:00:00 AM |  |  |  |  | 0 | William Mills Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station pump failure | After careful examination it was determined an air blockage was in the bypass line. Inclement weather may have been a contributing factor for the pump failures. The spill area has been cleaned and lime has been added to the affected area. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-20 | 2017-02-20 | Cobb County Water System | Cobb |  | 2157 Unity Trail | 280 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural Collapse |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-23 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Coleman Road (3 Manholes) - Augusta | 6285 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County Area. | Will assess the system via flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-04 | 2016-03-04 | Baldwin, City of (Baldwin WPCP) | Habersham |  | Near 501 Willingham Avenue Baldwin | 100 |  | Raw Sewage | Mountain District - Cartersville | GA0033243 | WWTP | Stream |  | Debris |  | Brian Koehler | Kathy Lewis | Brian Koehler | 3/4/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Fork Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line clog | Hydro jetted line | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-31 | 2016-10-31 | Newton County (Yellow River WPCP) | Newton |  | Alcovy River at Hwy 278 | 2688 | verbal notification received 10/31/2016 | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 10/31/2016 12:00:00 AM |  |  |  |  | 1 | Alcovy River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Back up from faulty air release valve. | Valve isolated and repair planned. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-06 | 2017-11-06 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 223 East Midlake Parkway - Swainsboro | 75 | Call received 2017-11-06 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Ground |  | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 11/6/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at the pump station caused a backup. | Power restored. Solids removed, area limed. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-21 | 2018-06-21 | Cobb County Water System | Cobb |  | 4515 Apache Ct | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/21/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Allatoona Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spill stopped at 1130 hrs | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-02 | 2017-08-02 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Conley | 438 Greenhill Way, Conley Manhole - 2194512 | 1125 | Fax received on 08/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 8/3/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Thames Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared line, and flow returned to normal |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-07 | 0 | 1 | 1 | 0 | 0 | 0
2015-02-26 | 2015-02-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3376 Lake Valley Road, NW | 49320 | verbal and fax notification received 2/27/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/27/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-04 | 2017-09-04 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 5838 N. Castlegate Dr, Riverdale MH 2210032 | 4600 | Fax received on 09/05/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 9/5/2017 12:00:00 AM | Flint |  |  |  | 1 | Camp Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared, and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-07 | 0 | 1 | 1 | 0 | 0 | 0
2017-12-28 | 2017-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3581 Revere Rd. SW - ATL | 560 | Fax sent 2017-12-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/29/2017 12:00:00 AM |  | 12/28/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-02 | 2018-03-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 617 Handley Ave. SW - ATL | 1345 | Fax sent 2018-03-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/4/2018 12:00:00 AM |  | 3/3/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew made mechanical repairs to the mainline to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-09 | 2015-12-09 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 1810 Mills B Lane | 4648 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Grease |  | Cliff Swiger | Steve Fox | Steve Fox | 12/9/2015 12:00:00 AM | Savannah | 12/9/2015 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Grease Stoppage in City of Savannah Gravity Main | Ditch was contained and buy-pass pumps to mitigate area and get overflow waters from getting further into the City storm drainage system. All agencies (i.e. Health Department, State EPD, and the City of Savannah Public Information Office (who will issue the Public News Release)) were notified as required by State Guidelines. Notification will be posted at Spill site, at Bowles Ford / Springfield Canal, and at Gwinnett / Springfield Canal. | 67692807-818f-496b-9fb6-018f0decdb42 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-12-14 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1528 Cherokee Ave., Columbus | 21534 | Fax and email received on 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-11-09 | 2015-11-10 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Social Circle Little River WPCP | 518852 | Email and verbal notification received 11/10/2015 | Primary Effuent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Due to hydraulic overload, operators at the Little River WPCP had to shut down the motors at the end of the aeration basin |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-01-13 | 2016-01-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 650 Thomasville Blvd, SE | 33900 | fax received 1/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/14/2016 12:00:00 AM |  |  | 2016-01-14 | 2017-02-03 | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-11 | 2017-06-11 |  | DeKalb | Atlanta | 1266 Sheridan Road, Atlanta | 4995 | Notification received on June 14, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/11/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 19:40 hours when the crew pressure washed the 12" sewer line 630ft, cleared the grease blockage at 405ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-12 | 2016-04-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 147 West Wesley Road, NW | 375 | Hard copy notification received via mail on 5/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/4/2016 12:00:00 AM |  |  |  |  | 0 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This is a private spill | This is a private spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-08 | 2016-06-08 |  | DeKalb | Doraville | 4422 Northeast Expressway, Doraville | 50 | Notification received on June 9, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/8/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment | The problem was corrected at 13:47 hours, when a crew used a full circle clamp around the steel pipe to seal the crack, stopped the leak and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-11 | 2015-10-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 3000 | fax received 10/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/12/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-23 | 2017-08-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3724 Eagles Beek Circle, Lithonia | 6378500 | Notification received on August 29, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Pipe failure |  |  | Hsin Yeh | Hsin Yeh | 8/24/2017 12:00:00 AM |  |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | A tree had damaged the connecting point between the 54 inch creek crossing and the junction box. | The spill was contained at 16:15 hours on August 26, 2017 when repair crews were able to divert the flow around the crossing and install temporary repairs. Permanent repairs are still ongoing. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-29 | 0 | 1 | 0 | 1 | 0 | 0
2018-05-09 | 2018-05-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 296 The Plaza | 2109 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/9/2018 8:50:00 AM | Oconee |  |  |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Clogged from rags | Rodded and flushed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-29 | 2015-09-29 | Marietta (City of)- Sewers | Cobb | Marietta | 428 Saint Marys LN | 45 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/29/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Marietta Water personnel quickly relieved the blockage thus restoring normal service. The sewer main was examined by CCTV to look for potential pipe issues. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2017-06-23 | Rome, City of (Rome WRF) | Floyd |  | 107 Homes Ave Rome | 900 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 6/23/2017 12:00:00 AM | Coosa |  |  |  | 0 | Little Dry Creeki | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease and roots in the sewer main | The sewer main was thoroughly cleaned. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 |  | Henry | Stockbridge | 100 Stapleton | 4500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/11/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Brush Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration from 11.5 inches of rain in the past 10 days. | Cleaned up spill area around manhole, placed spill notification signs around spill area and notified all of the proper agencies. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-07 | 2015-03-07 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 28th Prado NE | 519 | fax received 3/08/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/7/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-22 | 2017-01-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 3670 | Notification received on January 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/23/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 10:30 hours on January 23, 2017 when a crew drained the EQ tank back into the influent lift station and stopped the leak. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-08 | 2017-02-08 | Fulton County MS4 | Fulton |  | 650 Colebrook Court | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/8/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Long Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-17 | 2016-06-17 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Lift Station | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  |  |  | Reginald Williamson | Reginald Williamson |  | 5/17/2016 12:00:00 AM | Satilla |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Outage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-12 | 2017-10-12 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Rocky Springs Road lift Station in Eastman, GA. | 5000 | Incident did not enter into state waters per City. | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground | N/A | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 9/11/2017 12:00:00 AM | Ocmulgee | 9/11/2017 12:00:00 AM |  |  | 0 | N/A | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rainfall and power outage at lift station during Hurricane Irma event. | 9/20/2017 - Received written report of incident an PN that was published in the legal organ (Dodge County News) on September 20, 2017. 10/11/2017 - Written report received including start and stop times, and documentation showing TV, Radio, and health department were notified of incidents. Pictures of PN at spill location also provided | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-10-03 | 1 | 1 | 0 | 0 | 0 | 0
2016-01-17 | 2016-01-17 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 937 Canary Ct., Riverdale MH #2206385 | 1800 | Fax, email and voice mail received on 01/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/19/2016 12:00:00 AM | Flint |  |  |  | 1 | Camp Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and grease. | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Lines will be televised and roots cut, and if a problem is located it will be repaired. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-20 | 0 | 1 | 1 | 0 | 0 | 0
2016-05-26 | 2016-05-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2472 Cove Circle, Brookhaven | 1 | Notification received on May 31, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 5/26/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment | The problem was corrected at 10:28 hours, when a crew placed a tar sealant around the bell joint, stopped the leak and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Talbotton, City of (Talbotton WPCP) | Tift | Tifton | 720 Tifton Eldorado Road, Tifton | 8000 | Telephone call and email received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0047805 | Collection System | Stream | Shoreline | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  |  |  |  | 1 | Gum Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a power surge that tripped the breaker on the lift station. | Switched breaker back on. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0 | Thomas Corker | 229-391-3904 | TIFTON NEW RIVER WPCP
2018-02-08 | 2018-02-08 | Rockdale County (Quigg Branch WPCP) | Rockdale | Conyers | 1060 Scott Street | 16 | Report inclded | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/8/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Tanyard Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Piping Sagging | Clean Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Cobb County MS4 | Cobb |  | 1795 Martin Place | 2900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of solids in ser main causing the manhole to overflow into a tributary of Nickajack Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2017-06-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 3450 Jones Mille Rd. - Peachtree Corners | 158 | Fax received 2017-06-28 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 6/28/2017 12:00:00 AM |  | 6/27/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravity Main pipe failure. | Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 934 Glenwood Ave SE - ATL | 408 | Fax received on 01/21/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2016-01-28 | 2016-01-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2475 Alta Vista Drive, Brookhaven | 1 | Notification received on January 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 1/28/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe leaking | The problem was corrected when at 13:00 hours, when a crew strapped a cooler under the pipe to catch the drips and contained the spill, called in a request for repair and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-23 | 2015-01-23 |  | Lowndes | Valdosta | 1404 Gornto Road | 72000 | Verbal notification from John Waite received @ 4:30pm on 1/23/2015. Email follow-up from City sent 1/24/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/23/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-08-31 | 2018-08-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1280 Oakland Dr. SW - Atlanta | 5 | Fax sent 2018-09-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/1/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-15 | 2017-12-15 |  | Fulton | East Point | 1955 Dunlap St. | 1125 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 211 1/2 Leeds Gate Road, two manhole locations at Windsor/Wilshire Water Reclamation Plant. | 9000 |  | Raw Sewage | Coastal District | GA0020443 | Lift Station | Storm Drain | Canal | Power failure |  | David Lyle | Hailey Harden | Hailey Harden | 10/10/2016 12:00:00 AM | Savannah | 10/8/2016 12:00:00 AM |  |  | 1 | Wilshire Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Weather event from Hurricane Matthew caused lift station generator failure and caused two manhole overflows | Set up a portable generator. Spill notification markers were placed at the spill site and White Bluff/Wilshire Canal. | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-15 | 2017-01-16 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3602 Northside Drive, Macon GM ID 66885 | 54600 | Fax received on 01/19/2017, call received on 01/17/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/17/2017 12:00:00 AM |  | 1/15/2017 12:00:00 AM |  |  | 1 | Sabbath Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | The cause of this spill was a broken sewer main. | The sewer main was put on by-pass pumping and contractors were called to make the repair. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 1 | 0 | 1 | 0 | 0
2015-12-08 | 2015-12-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2625 Pautone Trace, Decatur | 1980 | Notification received on December 15, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/8/2015 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:11 hours when a crew pressure washed the 8" sewer main 300ft, clearing the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-11 | 2015-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 112 Ormond Street, SE | 500 | fax received 9/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-20 | 2017-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Rd. NW - ATL | 4875 | Email received 2017-06-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  | 6/20/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-22 | 2015-09-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1903 Sunbury Place, NW | 2400 | fax received 9/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/25/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-12 | 2015-08-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way, SW | 2210 | Fax received on 08/13/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/13/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a mechanical rod to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-24 | 2017-01-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 600 Mountain View Drive, Stone Mountain | 200 | Notification received on January 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:15 hours when the crew pressure washed 8" sewer main 200 ft between manholes, cleared the grease blockage at 100 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-10 | 2017-10-10 | Commerce, City of (Northside WPCP) | Jackson | commerce | commerce | 1200 |  | Raw Sewage | Wastewater Regulatory Program | GA0026247 | Force Main | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/10/2017 12:00:00 AM | Oconee |  |  |  | 0 | Beaver Dam Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | spilled stopped | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-02 | 2015-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 976 Rebel Forest Drive, SE | 500 | fax received 8/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/3/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-27 | 2017-04-27 | Fulton County (Big Creek WPCP) | Fulton |  | 5100 Old Alabama Road | 4320 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahooche River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Stopped Spill | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-20 | 2016-06-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 5376 Warrington Place, College Park Manhole 2213142 | 9000 | Fax received on 06/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 6/21/2016 12:00:00 AM | Flint |  |  |  | 1 | Sullivan Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. Work orders were generated for additional work to determine the cause. Lines will be televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-22 | 0 | 1 | 1 | 0 | 0 | 0
2016-02-18 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | Springrun Drive, Decatur | 3619 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek crossing reported leaking | Installed full circle clamp to repair the creek crossing |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-04 | 2016-04-04 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | 1416 11th St SW, Moultrie | 9600 | Using CCTV, dye, and smoke testing to search for additional I/I issues. | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System |  |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall impacted the area causing surcharging of the collection system | Monitoring location. Area limed. Could not cap cleanout for fear of backups into home. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2015-04-22 | 2015-04-22 | Cobb County MS4 | Cobb |  | 3999 Loch Highland Pass | 230 |  | Raw Sewage |  |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/22/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of roots in sewer main causing the manhole to overflow into a tributary of Willeo Creek. | The Cobb County Crew stopped the overflow at 10:17 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 |  |  | DeKalb |  | 3145 Briarcliff Road | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-24 | 2017-01-24 | Greenville, City of (Kennel Creek WPCP) |  |  |  | 0 |  | Raw Sewage | West Central District | GA0047813 | Lift Station | Ground |  |  |  |  | Tilden Bembry |  | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | no | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | 488bfc66-eb6e-11e0-b8d8-000c29971acc | 2017-02-07 | 1 | 0 | 0 | 0 | 0 | 0
2018-07-29 | 2018-07-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 244 E Lake Dr. SE - Atlanta | 153 | Fax sent 2018-07-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 7/30/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-20 | 2016-03-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 335 Flint River Road, Jonesboro MH # 123355 | 18000 | Fax received on 03/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 3/21/2016 12:00:00 AM | Flint |  | 2016-03-21 | 2017-03-02 | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Pump failure. | Bypass pumps at construction site were brought back online allowing flows to return to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-23 | 0 | 1 | 1 | 1 | 1 | 0
2017-12-10 | 2017-12-10 | East Point (City of)- Sewers | Fulton | East Point | 4090 Janice Drive | 9000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags Debris | Cleaned Debris | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-07 | 2016-01-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 825 Bolton Road, NW | 346 | FAX RECEIVED 1/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/8/2016 12:00:00 AM |  |  |  |  | 0 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-31 | 2017-08-31 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 304 Woodley Rd and 302 Briarcliff Rd., Savannah, GA | 3780 | Initial notification and full report received via email on 9/1/17. | Raw Sewage | Coastal District | GA0020443 | Collection System | Canal | Canal | Debris |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/1/2017 12:00:00 AM | Ogeechee | 8/31/2017 12:00:00 AM |  |  | 1 | Holland Canal to Vernon River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer main blockage caused two manholes to overflow | Cleared blockage and a sewer lateral. Vac trucks removed contaminated water from canal, applied lime to area. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-09-05 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2015-11-02 | 2015-11-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1735 Colt Drive, Brookhaven | 8200 | Notification received on November 4, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/2/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 12:30 hours, when the heavy rain subsided however, a crew inspected five (5) manholes upstream and seven (7) manholes downstream which were flowing full pipe due to high water level. After the heavy rain the manhole stopped spilling and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-19 | 2015-01-19 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3466 Paces Place NW | 2010 | fax received 1-20-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/20/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-05 | 2016-02-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | ATLANTA | 2833 Glenlocke Circle, NW | 4170 | fax received 2/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/6/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-20 | 2016-10-20 |  | DeKalb | Brookhaven | 3292 Buford Hwy, Brookhaven | 350 | Notification received on October 24, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 10/20/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 16:15 hours, when a crew pressure washed the service lateral 30ft, cleared the blockage at 20ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-03 | 2017-08-03 | Athens-Clarke County (North Oconee WPCP) | Clarke | athens | 223 Lake Vista Way | 84 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/19/2017 12:00:00 AM | Oconee |  |  |  | 0 | Turkey Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Line | Repaired broken pipe | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-24 | 2017-03-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 118 Roseclaire Dr. SE - ATL | 2085 | Fax Received Saturday, 2017-03-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/25/2017 12:00:00 AM |  | 3/24/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 |  | Lowndes | Hahira | Manholes at the intersection of W. Sargent and S. Newsome Street (reference address = 213 N. Nelson Street) | 3000 | The City has a 5-year plan to correct I/I problems and is looking to increase capacity to the WWTP | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani |  | 4/4/2016 12:00:00 AM | Suwannee | 4/2/2016 12:00:00 AM |  |  | 1 | tributary to Franks Creek and Hodges Pond | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall, I/I problems, and local flooding overwhelmed conveyance system pump stations leading to backup in sewage lines | Pump stations running full time |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-25 | 2016-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1595 Dodson Drive, SW | 20 | fax received 4/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/26/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to remove the blockage. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-30 | 2017-08-30 | PILGRIMS PRIDE PROCESSING PLANT | Coffee | Douglas | 113 McNeal Drive, Douglas, GA | 5300 | Signs posted at Highway 441 North (Broxton Hwy) & Highway 221 North (West Green Hwy). | Primary/Secondary Effluent | Coastal District |  | Pump Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 8/30/2017 11:00:00 AM | Satilla | 8/30/2017 12:00:00 AM |  |  | 1 | Twenty Mile Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure | Power restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2015-01-12 | 2015-01-12 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 6009 Seren Cove Woodstock | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 1/12/2015 12:00:00 AM | Coosa |  |  |  | 0 | Rose Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blocked the pipe. This caused the line to back up and overflow from a manhole. | CCWSA Construction Crews jetted the line and removed the grease. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 770-591-7156 | Cherokee Co W & S Auth
2016-12-15 | 2016-12-15 | Cobb County Water System | Cobb | Marietta | 6289 Pisgah rd./SweetBriar Dr. | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Reginald Williamson | Reginald Williamson | 12/15/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Georgon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 10 inch clay main | Stopped Spill and used lime around the manhole |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-01 | 2015-06-01 | Oconee County (Calls Creek WPCP) | Oconee |  | Mars Hill and Hwy 316 | 200 |  | Raw Sewage | Northeast District - Athens | GA0050211 | Lift Station | Stream |  | Pipe failure |  | Steve Walker | Steve Walker | Steve Walker | 6/1/2015 12:00:00 AM | Oconee |  |  |  | 0 | McNutt's Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | 2015-06-01 | 1 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1380 Battleview Dr. NW - ATL | 46000 | Fax received 2017-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM | 2017-04-12 | 2018-04-27 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rain-induced. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 1 | 1 | 0
2016-02-06 | 2016-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | ATLANTA | 2833 Glenlocke Circle, NW | 936 | fax received 2/07/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/7/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-20 | 2018-03-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4347 Flat Shoals Parkway, Decatur GA 30034 | 27900 | manhole 15-070-s050 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System |  |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/20/2018 5:45:00 PM | Ocmulgee | 3/20/2018 12:00:00 AM |  |  | 1 | Shoal Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | storm | Upon arrival was not spilling. |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-21 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 489 Sterling Street, NE | 3353 | fax received 11/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-19 | 2016-02-19 | Cobb County MS4 | Cobb |  | 109 Peregrine Way | 200 |  | Chlorinated Effluent | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids Build up in 12" Clay Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-10 | 2015-12-10 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2271 Flat Shoals Road | 360 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Inoperative Pump Station | Return PUmp Station to operatable status | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-23 | 2016-08-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 5420 Riverdale Road, Riverdale Manhole #2213461 | 9000 | Fax received on 08/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 8/24/2016 12:00:00 AM | Flint |  |  |  | 1 | Sullivan Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Lines will be televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-08-25 | 0 | 1 | 1 | 0 | 0 | 0
2016-02-22 | 2016-02-22 | Dekalb County (Snapfinger Creek WPCP) |  | Brookhaven | 1009 Lenox Valley, Brookhaven | 3960 | Notification received on February 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/22/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots | The problem was corrected at 9:50 hours, when a crew rodded the sewer main 100ft downstream clearing the blockage at 30ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-25 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-17 | 2018-07-17 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | Sandalwood Lift Station | 4200 | City lift station maintenance is completed per manufactures guideline | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Equipment failure |  | Katie Meade | Kathy Lewis | Katie Meade | 7/24/2018 12:00:00 AM | Coosa |  |  |  | 1 | Tributary to Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer Lift Station-electrical equipment failure | Replaced electrical equipment | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-24 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jester's Lake, Jonesboro MH #2215621 | 60000 | Fax received on 02/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 2/8/2016 12:00:00 AM | Flint |  | 2016-02-05 | 2017-03-02 | 1 | Jester Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | Capacity. | Lines will be inspected for source of inflow and infiltration to resolve capacity issue. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-08 | 0 | 0 | 1 | 1 | 1 | 0
2016-02-25 | 2016-02-25 | Vidalia, City of (Swift Creek WPCP) | Toombs | Vidalia |  | 0 |  | Chlorinated Effluent | Coastal District | GA0025488 | WWTP | Stream | Stream | Power failure |  | Beth Stevenson | Charlotte Nevill | Charlotte Nevill | 2/26/2016 10:00:00 AM | Altamaha | 2/25/2016 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  |  | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 2016-03-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-08-18 | 2016-08-25 | Smithville, City of (Smithville WPCP) | Lee | Smithville | Outfall into the Muckaloochee Creek in the Flint River Basin. | 63000 | The major spill was not reported by the facility, but was recognized by EPD personnel during a review of the August 2016 DMR. | Treated Effluent | Southwest District | GA0047422 | WWTP | Stream | Stream | Other |  |  | Linda Stevens | Linda Stevens | 9/15/2016 12:00:00 AM | Flint | 9/17/2016 12:00:00 AM | 2016-09-17 | 2017-09-30 | 1 | Muckaloochee Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the higher than normal suspended solids was the result of an algae bloom that occurred in the pond causing more algae than normal to be discharged in the effluent. | The amount of algae in the pond returned to normal levels the following week with no action taken. There is no need for additional corrective action to be taken. Stream monitoring and PN's began on 9/17/2016. Stream monitoring completed on 9/26/2017. |  | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-09-19 | 0 | 1 | 1 | 1 | 1 | 1 | John Hatcher |  | CITY OF SMITHVILLE WPCP | [5 empty] | CITY OF SMITHVILLE WPCP | 229-846-2101 |  |  | 74 mg/L
2016-03-22 | 2016-03-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 232 Sewanee Avenue, NW | 3950 | fax received 3/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/23/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-28 | 2015-05-29 | Tignall, Town of (Tignall WPCP) | Wilkes |  |  | 5040 |  | Raw Sewage | Northeast District - Athens | GA0046141 | Lift Station | Stream | Stream | Power failure |  | Steve Walker | Steve Walker | Steve Walker | 5/29/2015 10:46:00 AM |  | 5/29/2015 12:00:00 AM |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | transformer failure |  | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | 2015-06-01 | 1 | 0 | 0 | 0 | 0 | 0
2018-02-24 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 0 Gates Cir. SE | 0 | Fax sent 2018-02-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 2/26/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Section of pipe leaking at the joints. | As of 2018-02-24 9:10 AM, the spill has not been contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-10 | 2016-07-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 2760 | fax received 7/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/11/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-21 | 2016-09-21 | Cobb County Water System | Cobb | Marietta | 791 Mitsy Ridge Drive. | 1200 | 35 Fish Kill. Need Letter from Fish and Wildlife | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Broken Creek Crossing (12 in Ductile iron to Clay) 35 Fish Kill |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-22 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-26 | 2017-05-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1116 McConnell Drive, Decatur | 270 | Notification received on May 31, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/27/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:40 hours when the crew pressure washed the 8" sewer main 406ft., cleared the blockage at at 378ft., and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-31 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Homer Avenue Lift Station in McRae-Helena | 5000 |  | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ground, Stream |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM | Ocmulgee |  |  |  | 1 | Little Ocmulgee River | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma. | Power was restored to lift station as soon as possible due to it's capacity. Area was cleaned and lime was liberally applied. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-26 | 2017-01-26 | Cobb County Water System | Cobb |  | 1860 Atlanta Road | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/26/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Theater Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-10 | 2016-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 365 Peachtree Hills Avenue, NE | 100 | fax received 6/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/13/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-08 | 2017-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 346500 | Complaint received 2017-02-09. Update fax received 2017-02-15. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Paul Moisan | 2/9/2017 12:00:00 AM |  | 2/9/2017 12:00:00 AM | 2017-02-09 | 2018-03-01 | 1 | Utoy Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill is a collapsed mainline. | Crew installed a by-pass pump to contain the spill. A contractor is scheduled to make repairs at this site. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-10 | 0 | 1 | 0 | 1 | 1 | 1
2018-04-10 | 2018-04-10 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Line between 5523 and 5625 Bells Ferry Road Near intersection with Hwy 92 Down embankment across from McDonalds. | 6000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Grease |  | Eric Dykes | Kathy Lewis | Eric Dykes | 4/11/2018 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Tate Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage caused overflow to manhole, sewage came out between the riser. | Jetted the line to clear the blockage and contacted the FOG coordinator to work with restaurants in the area. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Fulton County (Big Creek WPCP) | Fulton |  | 375 Pine Grove Road Roswell | 6420 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Willeo Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | spill stopped at 11:31 am | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Fulton County (Big Creek WPCP) | Fulton |  | 375 Pine Grove Road Roswell | 6420 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Willeo Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | spill stopped at 11:31 am | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-05 | 2018-07-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 30580000 | Call received 2018-07-10 | Primary Effuent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream | Stream | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 7/10/2018 12:00:00 AM |  | 7/6/2018 12:00:00 AM |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | From midnight July 5 to midnight July 6, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. TSS - 37 mg/L. (Limit - 15 mg/L) This spill is also entered as a violation. | Excess biosolids to be removed from the facility | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-02 | 2017-10-02 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 4334 Windward Cir. - Norcross | 2283 | Fax sent 2017-10-02 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  | Alys Hannum |  | Alys Hannum | 10/2/2017 12:00:00 AM |  | 10/2/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Beaver Ruin Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, Paper, and Other Products | Raked area and spread lime. Placed signs at spill and waterway. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-18 | 2017-03-18 | Monroe, City of (Jack's Creek WPCP) | Walton | Monroe | Vine Street Pump Station - Monroe | 30000 | Email received Sunday 2017-03-19 | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Pump Station | Stream |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 3/19/2017 12:00:00 AM |  |  | 2017-03-20 | 2018-04-05 | 1 | Tributary to Hard Labor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Mechanical Issues | Cleaned up location and spread lime out. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 1 | 1 | 0
2018-06-10 | 2018-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1670 Benjamin Weldon Bickers Dr. SE - Atlanta | 1170 | Fax sent 2018-06-11 CORRECTION sent 2018-06-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/11/2018 12:00:00 AM |  |  |  |  | 1 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-16 | 2017-05-16 |  | Monroe | Forsyth | 552 Virginia St. | 10000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/17/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-03 | 2017-03-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2075 Gordon Hwy - Augusta | 600 | Email received Sunday, 2017-03-05. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 3/5/2017 12:00:00 AM |  | 3/3/2017 12:00:00 AM |  |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, rags and debris. | Sewer gravity main was cleaned and videoed. Further investigation is underway. Lime was spread in the affected area; notifications posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-07 | 2017-08-07 | Cobb County Water System | Cobb |  | 831 Pat Mell Road | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/7/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-03 | 2018-05-03 | Glennville, City of (Glennville WPCP) | Tattnall | Glennville | 600 Pecan Road Glennville, GA | 0 | Phone call on May 31, 2018. Full report emailed 6/3/2018 | Treated Effluent | Coastal District | GA0037982 | WWTP | Stream | Stream | Other |  | Jonathan Dance | Jonathan Dance | Jonathan Dance | 5/31/2018 12:00:00 AM | Altamaha | 5/3/2018 12:00:00 AM |  |  | 1 | Brickyard Branch Tribuatary | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Facility undergoing maintenance along heavy rain shortened detention time and created algae bloom contributing to high BOD | Completed maintenance to bring the facility back to full capacity | 3c961d94-0dba-4b14-af92-55314e79f9da | 3c961d94-0dba-4b14-af92-55314e79f9da | 3c961d94-0dba-4b14-af92-55314e79f9da | 2018-06-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-07 | 2017-03-07 | Douglasville, City of (South Central WPCP) | Douglas | Austell | 131 Maxham Rd., Austell Manhole 11335 | 570 | Fax received on 04/18/2017. It was first thought that this was a Cobb County spill, until it was determined later that it was actually in Douglas County. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream |  | Roots |  | Paul Moisan |  | Paul Moisan | 4/18/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Sweetwater Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was roots growing in the manhole. | Jet Truck crews from Cobb County first responded to the spill, cleared the blockage to stop the spill and disinfected the area. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-04-20 | 0 | 1 | 0 | 0 | 0 | 0 | Charles Butts | 770-949-7617 | Douglasville - Douglas County Water and Sewer Authority
2015-10-27 | 2015-10-28 |  | DeKalb | Dunwoody | 3981 Spalding Drive, Dunwoody | 38 | Notification received on October 29,l 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/28/2015 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 15:46 hours, when a crew contain the spill with a 5 gallons bucket under the upstream pipe, made a restoration by installing 18 ft of PVC pipe and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-22 | 2017-09-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 120 Johnson Rd. NW - ATL | 1 | Fax sent 2017-09-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 9/23/2017 12:00:00 AM |  | 9/22/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause unknown. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-02 | 2018-01-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3147 Bonway Drive Decatur GA 30032 | 200 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/3/2018 12:06:00 AM | Ocmulgee | 1/2/2018 12:00:00 AM |  |  | 1 | Cobbs Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | lateral issue | Work order to have lateral repaired issued |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-10 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Romel Davis |  | Dekalb Co Dept. Watershed Management
2015-07-30 | 2015-07-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2829 Osborne Road, Atlanta | 25 | Notification received on July 31, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 7/31/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 15:30 hours when vactors truck crew vacuum the sewage from the 8" main, and restored services. The repair to the culvert box was completed at 12:00 am on July 30, 2015. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 250 Orton Street, Tallapoosa | 100000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Roots |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/12/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Greene Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage to an 8" gravity line was blocked by a root ball and collected debris | Blockage removed and flow restored | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-03 | 2015-03-24 | Portal, City of | Bulloch |  | Unnamed stream that feeds into East Oglesby Pond which feeds into series of streams and ponds, ultimately to a finger of Little Lotts Creek. | 10000 | The adjacent landowners whose property may be affected were notified of the spill in person by Mayor Motes. | Irrigation Water | Coastal District | GAJ020041 | N/A | Stream | Stream | Wet weather |  | Beth Stevenson | Beth Stevenson | Beth Stevenson | 2/3/2015 2:00:00 PM | Ogeechee | 2/4/2015 12:00:00 AM | 2015-02-04 | 2016-02-04 | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3.85 | 0 | The LAS storage pond for this system was formerly a farm pond. There is a stand pipe in an adjacent stream (otherside of the impoundment for the storage pond) that acts as an overflow for the storage pond. The LAS storage pond was over full due to lots of rain and no spraying causing an overflow to the stand pipe. The operators did not realize the overflow was still in place; they thought it was removed when the farm pond was converted to a storage pond for the LAS. Additionally, the pipe is down slope on private property and obscured by vegetation. | The stand pipe was capped and spraying commenced to pull down the level of the storage pond. | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 2015-03-24 | 1 | 1 | 0 | 0 | 0 | 0
2015-08-13 | 2015-08-13 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6022 Harvest Drive | 5078 | REC CALL 8/14/2015. REC EMAIL 8/14/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo |  | 8/14/2015 12:00:00 AM | Chattahoochee | 8/13/2015 12:00:00 AM |  |  | 1 | Tributary of Bull Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" pipe was overflowing due to a stop up caused by grease. The stream was a tributary of Bull Creek. The basin is King's Branch Basin. | Once the stop up was cleared and flows returned to normal the overflow stopped. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | 706-649-3490
2016-08-12 | 2016-08-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 7538 Mountain Creek Bluff, Lithonia | 4120 | Notification received on August 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 8/13/2016 12:00:00 AM |  |  |  |  | 0 | Stone Mountain Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 21:55 hours when the crew pressure washed the 8" sewer main 250ft, clearing the blockage at 183ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-18 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-08 | 2018-07-08 | Rome, City of (Rome WRF) | Floyd |  | Behind 707 Oakland Avenue. Water coming out of a 4" cleanout | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Wet weather |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/9/2018 12:00:00 AM | Coosa |  |  |  | 1 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather events on 7/6/2018 & 7/7/2018 | We will be inspecting the sewer main with CCTV | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-10 | 1 | 0 | 0 | 0 | 0 | 0
2015-10-08 | 2015-10-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1509 Ponce De Leon Avenue, NE | 30 | fax received 10/09/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/9/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-30 | 2015-08-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2631 Cascade Road, SW | 0 | fax received 8/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 8/31/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism to the bypass pump. | The crew restored the bypass pump. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-01 | 2018-05-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 584 Tarragon Ct. SW - Atlanta | 2625 | Fax sent 2018-05-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/2/2018 12:00:00 AM |  | 5/1/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-01 | 2016-06-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3302 North Drid Hills road, Dectur | 3000 | Notification received on June 3, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/2/2016 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment | The problem was corrected at 16:22 hours, when a crew set up a 10" bypass pump to containthe sewer spill until the repair is completed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 700 Block of Cypress Street | 72050 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-09-05 | 2017-09-05 | Cobb County Water System | Cobb |  | 275 Shiloh Manor Drive | 12600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Crews stopped the overflow at 2:12 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2017-09-05 | Cobb County Water System | Cobb |  | 275 Shiloh Manor Drive | 12600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Crews stopped the overflow at 2:12 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-12 | 2015-06-12 | Fulton County MS4 | Fulton |  | 4492 White City Rd. College Park, GA 30349 | 1760 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The section of the system is being inspected upstream of SSO M/H. Those sewer lines will be put on a quarterly schedule for cleaning with grease control. Enzymes were applied to minimize the odor. The area impacted cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-06-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-30 |  | Pulaski | Hawkinsville |  | 3698 | Volume of spill was calculated accordingly: Lift station only serves 3 houses, which typically use about 3,880 gallons of water/day. Three days underwater = 11,640 gallons. Lift station holds 7,942 gallons. Therefore spill estimated at 3,698 gallons. | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Stream |  | Wet weather |  |  | Dagny Pariani |  | 12/28/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Ocmulgee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station was submerged for 3 days during a major rain event. |  |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-01 | 2018-02-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3648 Walton Way Ext. - Augusta | 350 | Email sent 2018-02-02 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Rags |  |  | Alys Hannum | Alys Hannum | 2/2/2018 12:00:00 AM |  |  |  |  | 1 | Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy amount of rags and debris. | Used vac truck to jet the line. Road was washed down and storm drain was flushed and vaccumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-02 | 2018-05-02 |  | Coffee | Douglas | Southeast WWTP on Iron Road. | 100000 | EPD contacted DNR Fisheries to investigate the spill. Fisheries reported a total of 35 dead fish were collected during their investigation. Major spill sampling nor public notice was conducted as chlorine dissipates quickly and does not pose a risk to the public. | Chlorinated Effluent | Coastal District |  | WWTP | Ditch | Ditch | Operator error |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 5/2/2018 1:00:00 PM | Satilla | 5/2/2018 12:00:00 AM | 2018-05-02 | 2018-05-02 | 1 | Seventeen Mile Creek | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Operator error resulted in excess chlorine (50 lbs of Sodium Hypochlorite) being released from the WWTP effluent into the ditch-way and creek. Seven dead fish were observed by the operators during the downstream inspection. | A standard operating procedure has been developed to prevent a future release of chlorine from the WWTP effluent. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-06-06 | 1 | 0 | 0 | 0 | 0 | 0
2017-06-14 | 2017-06-14 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1615 Hickory Street Dalton | 8425 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Debris |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 6/15/2017 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris Blockage | Blockage removed using a high pressure jet. Disinfected the immediate vicinity of the spill with lime. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-06-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-03 | 2015-01-03 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Airport #1 Pump Station at 4710 Ball Ground Highway | 3990 | See report dated 1/5/2015 | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Cindy Nix | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Coosa |  |  |  | 0 | Edwards Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Force main had a 1/2 diameter hole in pipe | CCWSA Construction Crew built a berm and funneled the wastewater into a nearby manhole. They removed the debris and placed a saddle around the pipe. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 770-591-7156 | Cherokee County W & S Authority
2015-10-01 | 2015-10-01 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton |  | 6852 Maddox Road (Manhole No. 2206582) | 2400 | Fax received on 10/02/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 10/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Roots were the probable cause of the blockage. | Blockage was cleared and flow was returned to normal. Site was cleanead and work orders were generated for additional work to determine cause (televise line and cut additional roots if located). |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-10-02 | 1 | 1 | 1 | 0 | 0 | 0
2015-07-17 | 2015-07-17 |  | Upson | Thomaston | City Hall Lift Station | 1000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown |  |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/17/2015 12:00:00 AM | Flint |  |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to a portable bypass pump failing to start. | All debris associated with the overflow has been cleaned up and the local health department has also been notified. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 170 Springlakes Drive - Martinez | 3150 | Fax sent 2017-09-13 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 9/12/2017 12:00:00 AM |  | 9/12/2017 12:00:00 AM |  |  | 1 | Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Unstopped sewer main with high pressure jetting machine and Vac truck. Removed large chunks of grease. Limed area. Posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-28 | 2018-03-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 955 Shadow Lakes Drive, Lithonia GA 30058 | 1000 | manhole 16-095-s002 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/28/2018 6:01:00 PM | Ocmulgee | 3/28/2018 12:00:00 AM |  |  | 1 | Upper Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressurewashed grease blackage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-29 | 2018-01-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3345 Lake Valley Rd. NW - ATL | 1020 | Fax sent 2018-01-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 1/30/2018 12:00:00 AM |  | 1/29/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 161 Hood Circle, Decatur | 100 | Notification received on January 5, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/3/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rain | The problem was corrected at 10:30 hours, when a crew cleaned up and disinfected the contaminated area. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-19 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-21 | 2017-08-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1964 Jones Ave. NW - ATL | 330 | Fax received 2017-08-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 8/22/2017 12:00:00 AM |  | 8/21/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-18 | 2017-02-18 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6650 Peacock Blvd., Morrow | 3600 | Fax received on 02/19/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/19/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | York Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Blockage was cleared. CCWA will televise to find how sewer was escaping system. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-20 | 0 | 1 | 1 | 0 | 0 | 0 | Billy Vonderbosch |  | CLAYTON COUNTY WATER AUTHORITY
2018-06-04 | 2018-06-04 | Cobb County Water System | Cobb | Marietta | 1085 Woodruff Plantation | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/4/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rotten Wood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" PVC main | Stopped spill and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-16 | 2016-10-16 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 195 Epps Bridge Rd., Athens | 42 | Initial email and full report received 10/17 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 10/17/2016 12:00:00 AM | Oconee |  |  |  | 1 | Middle Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disposable wipes clogged the sewer line | Rodded sewer line |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-01-27 | 2017-01-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 992 Virginia Ave NE - ATL | 10 | Fax received on 01/28/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/28/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-09-12 | 2017-09-12 | Pembroke, City of (Pembroke WPCP) | Bryan | pembroke | lift station #1 144 west industrial boulevard in pembroke ga | 9000 | did not appear to be in state waters | Raw Sewage | Coastal District | GA0038377 | Pump Station |  |  | Natural Disaster |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 9/11/2017 12:00:00 AM | Ogeechee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | result of inflow from heavy rain from hurricane Irma the overwhelmed the lift stations pumping capacity | lift station was monitored until the pumps caught up with the flow | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2017-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1830 Slade Ave., Columbus | 1169 | Fax, email and voice mail received on 02/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-07 | 2017-09-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4175 Bakers Ferry Rd. SW - ATL | 4475 | Fax received 2017-09-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/8/2017 12:00:00 AM |  | 9/7/2017 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-23 | 2015-02-25 | Cobb County MS4 | Cobb |  | 1190 Kennestone Cir | 320 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/23/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids in 8" Clay Main | Cleaned and limed the area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 21750 | Notification received on November 12, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/7/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 08:42 hours, when the heavy rain subsided and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-20 | 2016-07-21 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville | The spill entered the effluent channel downstream of the metering and sampling point, which ultimately reached Taylor Creek. | 1620000 | This occurred sometime between the hours of 1735 on 7/20 and 0600 on 7/21. Staff arrived on site at 0600, 7/21 and observed the overflow from the secondary clarifier splitter box. Upon investigation, they found the first and second stage trickling filter re-circulation pumps faulted out on the VFDs. They reset the pumps, operated them in manual mode halting the overflow, then returned the system to automatic operation. In addition to the trickling filter re-circulation pumps, the contact basin blowers had tripped and were off, the duplex pump system had tripped out, and the SCADA failed to activate alarms to alert personnel that these systems were down. All equipment and systems are now back in normal operation. | Secondary Effluent | Coastal District | GA0047180 | WWTP | Stream | Stream | Power failure |  | John Kalp | Hailey Harden | John Kalp | 7/21/2016 7:45:00 AM | Ogeechee | 7/21/2016 12:00:00 AM | 2016-07-21 | 2017-07-27 | 1 | Taylor Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | yes | 0 | On the evening of July 20th 2016 severe weather - lightning and high wind gusts- impacted Hinesville and Ft. Stewart. Electrical disturbances associated with the storm caused several equipment failures at the Fort Stewart Plant. Trickling filter re-circulation pumps tripped out resulting an overflow of partially treated wastewater from the secondary clarifier splitter box into the effluent channel downstream of the metering and sampling point, which ultimately reached Taylor Creek. | All actions called for the "Major Spill" protocol, and as defined by NPDES permit number GA0047180 have been performed or are in progress. These include: Notified GA EPD Notified Liberty County Health Department Notified media outlets: WTOC TV, WSGA TV, WSGA Radio, Coastal Courier Newspaper Notified City of Hinesville Posted notices at three pre-specified locations: Hero road Bridge, Hwy 119 Tank Trail FS 144, and Hwy 119 Bridge #29 Initiated sampling program on Taylor Creek | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-07-27 | 1 | 1 | 0 | 0 | 0 | 0
2016-01-30 | 2016-01-30 | Thomaston, City of | Upson | Thompson | 855 N. Center Street Wal-Mart Lift Station | 12500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/30/2016 12:00:00 AM | Flint |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this major spill is a broken sewer main. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-30 | 2016-08-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6256 Hillandale Drive, Lithonia | 1220 | Notification received on August 31, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/30/2016 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The spill was contained at 14:26 hours when a crew pressure washed the 8' main 184ft to remove the grease blockage at 115ft, which then restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-01 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-21 | 2016-04-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2101 Snapfinger Road, Decatur | 950 | Notification received on April 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/21/2016 12:00:00 AM |  |  |  |  | 0 | Cobb Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 17:55 hours, when a crew repaired the sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-04-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-04 | 2015-10-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Hampton Inn Lift Station | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 10/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | North Fork of Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Torrential Rains |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-894-3085 | City of Cornelia
2016-09-13 | 2016-09-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3714 Roswell Road, NE | 350 | fax received 9/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 9/14/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-27 | 2017-07-27 | Cobb County Water System | Cobb |  | 378 Oak Glen Drive | 250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | chattahoochee river | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | roots | spilled stopped at 12:20 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-13 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 6144 Wandering Way - Norcross | 1068 | Fax received 2017-01-13 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Hwan Cho | 1/13/2017 12:00:00 AM |  | 1/13/2017 12:00:00 AM |  |  | 1 | Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked area and spread lime, then posted signs at the spill and waterway. |  | 32edc8ca-b615-42f5-a2d3-37d9a41cbfe8 | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-28 | 2016-01-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1024 Litherland Court, SE | 7350 | fax received 1/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/28/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-27 | 2017-11-27 | Thomasville, City of (Oquina Creek WPCP) | Thomas | Thomasville | Robin Hood Road at Old Monticello Road, Thomasville | 9900 | Telephone call and email report received on 11/22/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024082 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/22/2017 12:00:00 AM | Ochlockonee |  |  |  | 1 | Olive Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially blocked 8-inch gravity main caused leak at bell joint | Blockage removed, bell joint replaced, and the flow returned to normal. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-22 | 0 | 0 | 0 | 0 | 0 | 0 | Jom Ridley | 229-227-3275 | CITY OF THOMASVILLE
2017-01-12 | 2017-01-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3535 Lawrenceville Highway, Tucker | 1980 | Notification received on January 13, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/12/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:44 hours when the crew pressure washed and root cut the sewer main 45ft, removed the grease and rags blockage and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-20 | 2018-01-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4940 Fairforest Drive Stone Mountain GA 30088 | 2160 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/20/2018 9:02:00 AM | Ocmulgee | 1/20/2018 12:00:00 AM |  |  | 1 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Pressure washed manhole 18-17-s072 to clear blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-22 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Artis Benton |  | Dekalb Co Dept. Watershed Management
2015-11-30 | 2015-11-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1810 Perry Blvd. NW | 2270 | fax received 12/01/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/1/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-17 | 2015-02-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | City of Atlanta - R.M. Clayton WRC | 0 | Verbal and email notification received 2/18/2015. Spill volume is 22.84 million | Secondary Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/18/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | "the total suspended solids concentration (TSS) was found to be 62 mg/L, which is a daily value of more than 50 percent greater than the 15 mg/L weekly permit limit for effluent TSS, which qualifies as a major spill per the NPDES Permit. This exceedence is believed to be related to a bypass of the sand filters that occurred as a result of a loss of clarifier solids caused by a storm surge on Tuesday, February 17th." Volume = 84,700,000 gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-23 | 2016-05-23 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 606 Grenier Terrace | 8208 | fax recevied after hours on 5/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/24/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Alcovy River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-01-02 | 2017-01-03 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 4590 Oakley Pirkle Road - Martinez | 10001 | Received 2017-01-12 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/6/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM |  |  | 1 | Crawford Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Surcharging from excessive rainfall. | Monitored area, searched for inflow, and spread lime over the affected area. Sampling creek and posting signs. Follow-up inspections, sampling, and reporting will continue as required. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 1 | 1 | 0
2017-05-19 | 2017-05-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2677 Lake Erin Drive, Tucker | 1080 | Notification received on May 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWRF | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/19/2017 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 09:59 hours, when a crew pressure washed the 8(in) main 230(ft) to remove the grease blockage at 220(ft), which restored the flow back to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-08 | 2015-02-08 | Marietta (City of)- Sewers | Cobb | Marietta | 1003 Brownstone Dr. (At manhole by creek behind property. | 7200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Lyn Mickelson | 2/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Olley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A root blockage caused a sewer main to back up and overflow into a nearby creek. | Marietta Water personnel quickly relieved the blockage thus restoring normal service. The affected area was cleaned, limed and deodorized. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 7ab946ee-6ee0-11e1-a69e-12313d2b7a91 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-01 | 2015-04-01 | Cobb County MS4 | Cobb |  | 2403 Hembree Station CT. | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/6/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sewell Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks in 8" Ductile Iron Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-01 | 2016-01-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2440 Eastland Road, Atlanta | 1340 | Notification received on January 5, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/1/2016 12:00:00 AM |  |  |  |  | 0 | Entrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 15:47 hours, when a crew pressure washed the 8" sewer main 250' and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-09 | 2015-01-09 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | City of Swainsboro Yam Grandy WPCP | 1504000 | The City reported the incident verbally to EPD on 1-09-2015 | Treated Effluent | Wastewater Regulatory Program |  | WWTP | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/9/2015 12:00:00 AM |  |  |  |  | 1 | Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "On January 9, 2015 the operator was checking the discharge at the Yam Grande sample location point. It was noted that there was no flow at mechanical aerators. The operator checked the transfer station and found the 16’’ treated effluent line split on bottom of pipe. The treated effluent was flowing from the ruptured line, across the field and into Crooked Creek. To prevent significant erosion and to make access to the area for repairs, the treated effluent was diverted to the original (now non-permitted) outfall to Crooked Creek." | The line to the Yam Grandy discharge was repaired/replaced. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO
2018-01-02 | 2018-01-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 335 Harper Rd. SE - ATL | 10 | Fax sent 2018-01-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum |  | 1/4/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Spill was self-contained |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-24 | 2017-03-24 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 4288 Old Club Road East, Macon MH ID - 63870 | 3000 | Fax received on 03/27/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 3/27/2017 12:00:00 AM | Upper Ocmulgee | 3/24/2017 12:00:00 AM |  |  | 1 | Wolf Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grass and roots. | Debris was removed from the area, and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0 | Heather Veal |  | MACON WATER AUTHORITY
2015-04-03 | 2015-04-03 | Thomaston, City of | Upson | Thomaston | 801 W. Gordon Street, Thomaston, Georgia | 2500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/3/2015 12:00:00 AM | Flint |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to blockage in the sewer line. | All debris associated with the overflow has been cleaned up and the area was disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-09 | 2017-01-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 428 Page Ave, NE - ATL | 924 | Fax received on 01/10/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/10/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell |  | ATLANTA, CITY OF
2018-01-23 | 2018-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 804 Gresham Ave. SE - ATL | 890 | Fax sent 2018-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/24/2018 12:00:00 AM |  | 1/23/2018 12:00:00 AM |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2017-09-06 |  | DeKalb | Clarkston | 3954 Memorial College Avenue, Clarkston | 6000 | Notification received on September 8, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh |  | 9/6/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:10 hours when the first responder crew pressure washed the 8-inch sewer main 400-ft, cleared the blockage at 5-ft and restored normal flow. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-13 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-07 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3010 Mcaffe road, Decatur GA 30032 | 90800 | sewage leak from manholes 15-172-s003 and 15-149-s007 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/7/2018 6:08:00 PM | Ocmulgee | 2/7/2018 12:00:00 AM |  |  | 1 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm | wait for storm to end |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-17 | 2015-09-17 | Gibson, City of (Gibson WPCP) | Glascock | Gibson |  | 0 |  | Unknown | Northeast District - Augusta | GA0021849 | N/A | Stream | Stream | Operator error |  | Joe Sills | Joe Sills | Joe Sills | 9/23/2015 9:00:00 AM | Ogeechee | 11/11/2015 12:00:00 AM | 2015-11-11 |  | 0 | Rocky Comfort Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The event was not related to gallonage. Instead, it is a BOD limit violation. The reported BOD qualified for the major spill designation. The laboratory reported the high BOD, but noted that the sample appearance was not consistent with treated wastewater from this oxidation pond system. The lab believes the sample is non-representative of the effluent; therefore, likely collected at an incorrect location. The person who collected the sample was unavailable to clarify the situation. The certified operator investigated and could find no operating problems at the pond system. Though the sample is believed to be non-representative, the major spill was declared by EPD and corrective actions began. | The city did the notifications and began the stream monitoring. | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 2016-05-31 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 743 San Antonio Dr NE - ATL | 20 | Fax received on 01/22/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2015-12-05 | 2015-12-05 | CITY OF SAVANNAH WILSHIRE/WINDSOR WWTF | Chatham | Savannah | 422 Windsor Road near intersection of Windsor Rd / Deerfield Rd | 5400 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 12/5/2015 12:00:00 AM | Savannah | 12/5/2015 12:00:00 AM |  |  | 1 | Hoover Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Gravity Sanitary Sewer pipe defect caused stoppage which caused manhole overflow to ditch | Shut lift station off to stop overflow. Repaired pipe defect, spread lime over affected area, contained ditch and removed storm / sewage mix of water with City vacuum trucks. Spill notifications will be placed at spill site and at Bells Landing. All entities - Georgia Environmental Protection Division, Heath Dept. and City Public Information Office (who will send out a news release to the media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-12-07 | 1 | 1 | 1 | 0 | 0 | 0
2017-12-09 | 2017-12-09 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | adjacent to 3434 Pinemont Drive, Douglasville Manhole # 9683 | 187500 | Fax and email received on 12/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Lift Station | Stream |  | Power failure |  |  | Paul Moisan | Paul Moisan | 12/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Anneewakee Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Electrical and controls failures due to heavy snow storm and power outages. | Mechanics and electricians were able to repair the controls issues and get the station running under generator power stopping the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-12 | 0 | 1 | 0 | 0 | 0 | 0 | Lyndsey Sargent | 770-949-7617 | Douglasville-Douglas County Water and Sewer Authority
2017-09-11 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | 14th Street Lift Station in McRae-Helena | 2000 |  | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ground, Stream |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM | Ogeechee |  |  |  | 1 | Little Ocmulgee River | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma | Bypass pump installed on September 13, 2017 in order to pump water directly into force main which leads to WWTP. Spill was cleaned and lime was applied liberally. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2015-07-30 | 2015-07-30 |  | Cobb |  | 1852 King Arthurs CT | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids built up in 8in Truss Main | cleaned area and spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-04 | 2017-02-04 | Cobb County Water System | Cobb |  | 4428 Cove Island Drive | 1030 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | ADMINTEST ADMINTEST | Reginald Williamson | 2/4/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 9:18 a.m. and the crew stopped the overflow at 12:10 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-06 | 2016-06-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1074 Hill Street, SE | 500 | This overflow did not reach State waters. Fax received 6/07/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/7/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-21 | 2018-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4480 North Shallowford Road, Dunwoody GA 30338 | 8880 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/22/2018 10:00:00 AM | Ocmulgee |  |  |  | 1 | Nancy Creek Tributary A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, rags, and wipes | Root cut sewer main to remove blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-22 | 0 | 0 | 0 | 0 | 0 | 0 | Artis Benton |  | Dekalb Co Dept. Watershed Management
2018-07-03 | 2018-07-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 4311 Chamblee Dunwoody Road Chamblee GA 30341 | 2080 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/4/2018 12:19:00 AM | Ocmulgee |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | roots | rodded cleanout |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-29 | 2017-09-29 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3301 Greening Lane - Augusta | 13500 | Email sent 2017-09-29 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/29/2017 12:00:00 AM |  | 9/30/2017 12:00:00 AM |  |  | 1 | Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The overflow was caused by a collapsed concrete brace and brick wall that supported a storm drain outfall pipe. The brick wall and concrete brace was severely cracked, which settled atop of the concrete sewer gravity main causing sewer to spill through the damaged sewer pipe. | The engineering division was notified about the damaged storm structure. The storm structure was removed and the 13’ section of RCP sewer pipe was replaced with PVC sewer pipe. Notifications will be placed in the area. Sampling is being prepared. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-21 | 2015-04-21 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3529 Stafford | 5400 | fax received 4/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 4/22/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, grease, debris | The line was opened and resumed normal flow. This line will be added to our root and grease control program. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-03-20 | 2017-03-20 | Henry County Water Authority (Indian Creek WRF) | Henry |  | Hwy 81 W. Manhole ID #3092 | 5600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/30/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-08 | 2017-12-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3136 Martin L. King Jr. Dr. SW - ATL | 5125 | Email sent 2017-12-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 12/9/2017 12:00:00 AM |  | 12/8/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-14 | 2018-09-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1671 James Jackson Pkwy - Atlanta | 890 | Fax sent 2018-09-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/15/2018 12:00:00 AM |  | 9/14/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 1011 Lower Poplar Street, Macon MH ID 61093 | 5300 | Telephone call received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024538 | WWTP | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor overflow was hydraulic overload due to heavy rains in the MWA service area and a loss of power at the Lower Poplar Water Reclamation Facility. | Debris has been removed from the area and the affected area has been disinfected with lime. The Lower Poplar Water Reclamation Facility lost power during the storms on Friday morning April 1st. Once power was restored to the plant, the manhole stopped overflowing. The MWA will also continue to search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 3820 | fax received 12/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-24 | 2018-07-24 | Columbia County (Little River WPCP) | Columbia | Evans | 4600 Blanchard Woods Drive - Evans | 45750 | Phone Call received 2018-07-24 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Pump Station | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/24/2018 12:00:00 AM |  | 7/24/2018 12:00:00 AM |  |  | 1 | Euchee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Undersized pump provided by contractor | Contractor added additional pump; raked area; spread lime; posted signs |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-19 | 2018-07-19 | Rome, City of (Rome WRF) | Floyd |  | Behind 707 Oakland Avenue | 500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Equipment failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/20/2018 12:00:00 AM | Coosa |  |  |  | 1 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Very heavy wet weather event caused a brief pump failure at Horseleg Creek lift station | Spill site was a 4" cleanout behind the noted address. A backwater/check value is scheduled to be installed next week. Video inspection of the sewer main continues. Video inspection of the sewer main continues. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-24 | 1 | 0 | 0 | 0 | 0 | 0
2018-05-24 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1 Aflac Parkway | 135009 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Bull Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, maihole has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-23 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 2662 Spring Cast Drive | 590 |  | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Hsin Yeh | 1/13/2017 12:00:00 AM |  | 1/13/2017 12:00:00 AM |  |  | 1 | Little Mulberry Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure - cracked | Raked area and spread lime. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Lift Station | 450 |  | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Lift Station |  |  | Wet weather |  |  | Alys Hannum | Hsin Yeh | 12/8/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A lift-station backup pump was reported as not working. | Spent the rest of the night collecting the 450 gallons of raw sewage that did NOT enter state waters. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-11 | 2017-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 348 Armour Dr, NE, ATL | 2250 | Fax received on 01/12/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/12/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-09-07 | 2016-09-07 |  | Cobb | Marietta | 1677 Buckner Dr. | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Removed debris and spread lime . Will return 9-8 for further debris removal. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-25 | 2017-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1811 Moores Mill Rd. NW - ATL | 5450 | Fax received Sunday 2017-02-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Paul Moisan | 2/26/2017 12:00:00 AM |  | 2/25/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-04 | 2018-08-04 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1500 Cleo Way Dalton, GA | 2325 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWRF | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 8/4/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed tributary of Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer main surcharge likely caused the release from a broken sewer pipe | Dalton Utilities cleared blockage with high pressure jet, release was stopped. Dalton Utilities will follow up with camera inspection to find potential break and will repair when located | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-07 | 1 | 0 | 0 | 0 | 0 | 0
2018-02-03 | 2018-02-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC - Atlanta | 0 | Feb 4th - TSS = 437 mg/L Feb 5th - TSS = 60 mg/L | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Hydraulic Overload |  | Alys Hannum | Alys Hannum | Alys Hannum | 2/6/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | From 11:45 AM on February 3rd to 7:30 AM February 4th, City of Atlanta experienced a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. This spill is also entered as a violation. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-31 | 2016-08-31 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 72.6 TSS, weekly average concentration (mg/L): permit = 30, reported = 71.1 Flow was 0.908 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 72.6 | 71.1
2016-09-04 | 2016-09-04 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 435 Fortson Dr., Athens | 300 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/4/2016 12:00:00 AM | Oconee | 9/4/2016 12:00:00 AM |  |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fell on aerial pipe | Cut and removed the tree, repaired the pipe |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-04 | 2018-09-04 | Cleveland, City of (Cleveland WPCP) | White |  | 2103 Hwy 129 South, Cleveland | 450 | Overflow that did not enter state waters | Raw Sewage | Mountain District - Cartersville | GA0036820 | WWTP |  |  | Pipe failure |  | Matthew Stickney | Kathy Lewis | Matthew Stickney | 9/4/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defective saddle strap on a 12" sewer line at manhole | Replaced fitting to stop leak. Cleaned up around the manhole, spread lime, posted area. | 77dbdd3c-0b48-49c2-b623-a78b1b0170cf | 77dbdd3c-0b48-49c2-b623-a78b1b0170cf | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-09-18 | 1 | 0 | 0 | 0 | 0 | 0
2018-07-23 | 2018-07-24 | Kingsland, City of (Kingsland WPCP) | Camden | Kingsland | At the intersection of Al Gay Drive and Vickey Lane in Kingsland Georgia 31548 | 7000 |  | Raw Sewage | Coastal District | GA0037800 | Collection System | Ditch | Ditch | Other |  | Brett Berry | Brett Berry | Brett Berry | 7/24/2018 8:00:00 AM | Saint Mary's | 7/24/2018 12:00:00 AM |  |  | 1 | Unnamed tributary of the St. Mary's River | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Automobile hit an air release valve which was part of the collection system. | They shut down the lift station, made a repair on the pipe, had a Via- Con truck vacuum the water from road and ditch and spread lime on the ground. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-07-27 | 1 | 1 | 0 | 0 | 0 | 0
2018-04-10 | 2018-04-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 5604 Peachtree Industrial Blvd, Chamblee GA 30341 | 101850 | m/h 18-309-s200 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/11/2018 9:49:00 AM | Ocmulgee | 4/10/2018 12:00:00 AM |  |  | 1 | Nancy Creek Tributary B | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | rock blockage | pressured washed unknown blockage. Partial flow restored |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 4492 Chambers Rd., Macon MH ID 53714 | 1050 | Fax recievied on 05/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 5/24/2016 12:00:00 AM |  | 5/24/2016 12:00:00 AM |  |  | 1 | Ditch feeding Tobesofkee Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of the spill was grease. | Debris was removed form the area, and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-26 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Waycross, City of (Waycross WPCP) | Ware | Waycross | 2900 Lakeview Drive - Waycross Drainage Canal | 3857 |  | Raw Sewage | Coastal District | GA0020966 | Lift Station | Canal | Canal | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/11/2017 12:30:00 PM | Satilla | 9/11/2017 12:00:00 AM |  |  | 1 | Waycross Drainage Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive flows to the WWTP as a result of Hurricane Irma. | A third influent pump was activated to stop the spill. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-09-18 | 1 | 1 | 0 | 0 | 0 | 0
2018-05-29 | 2018-05-29 | Cobb County Water System | Cobb |  | 1756 Bertram Lane | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/29/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | stopped spill and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-17 | 2016-06-17 | Savannah, City of (President Street WRF) | Chatham | Savannah | 5859 Abercorn Street | 580 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Unknown |  | Cliff Swiger | Steve Fox | Steve Fox | 6/17/2016 12:00:00 AM | Savannah | 6/17/2016 12:00:00 AM |  |  | 1 | Hempstead Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Overflowing manhole caused by unknown stoppage in gravity sanitary sewer main | Cleared stoppage with City jet-vacuum trucks and mitigated spill site. Wireless alarm will be installed to give staff an advanced warning if system becomes surcharged. Spill notification markers were placed at the spill site, at Casey Canal at Eisenhower, Casey Canal at Sallie Mood Driver and Casey Canal at Montgomery Crossroads. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | 67692807-818f-496b-9fb6-018f0decdb42 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-20 | 1 | 1 | 0 | 0 | 0 | 0
2016-06-21 | 2016-06-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Ellenwood | 5368 Sapphire Circle, Ellenwood Manhole 22703752 | 2400 | Fax received on 06/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 6/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Upton Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Blockage was cleared and flow was returned to normal. Work orders were generated for additional work to determine the cause, and the lines will be televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-22 | 0 | 1 | 1 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3528 Misty Valley Road, Decatur | 5500 | Notification received on February 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/25/2016 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing sewer main broken | The problem was corrected at 17:56 hours, when a crew replaced the 10" broken pipe and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-19 | 2015-10-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3476 Donald Lee Hollowell Parkway, NW | 3710 | fax received 10/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/20/2015 12:00:00 AM |  |  |  |  | 0 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew installed a bypass pump to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-27 | 2016-02-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 5260 Peachtree Industrial Boulevard, Chamblee | 5000 | Notification received on March 4, March. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/29/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | malfunction pump | The problem was corrected at 13:40 hours, when a crew built another berm around the broken 12" main to contain the spill, replaced the 4" pump with a 6" pump, restored normal flow until the repair is made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-17 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-20 | 2018-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 848 Forrest Cir. SE - ATL | 150 | Fax sent 2018-01-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/21/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-02 | 2015-03-02 |  | Henry |  | Summit Subdivision off of Highway 42 beyond the cul-de-sac at paramount Drive. | 3850 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/3/2015 12:00:00 AM | Chattahoochee | 3/3/2015 12:00:00 AM |  |  | 0 | Little Cotton Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease accumulation was deemed to be the cause of the blockage. | The crew were able to free the blockage and restore the gravity flow in the system the same day. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-02 | 2015-03-02 |  | Henry |  | Summit Subdivision off of Highway 42 beyond the cul-de-sac at paramount Drive. | 3850 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/3/2015 12:00:00 AM | Chattahoochee | 3/3/2015 12:00:00 AM |  |  | 0 | Little Cotton Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease accumulation was deemed to be the cause of the blockage. | The crew were able to free the blockage and restore the gravity flow in the system the same day. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-28 | 2015-05-28 | Columbus Water Works (South WRF) | Muscogee | Columbus | Columbus Water Works South Water Reclamation Facility | 0 | REC 1st REPORT on 6/5/2015. REC final REPORT on 6/17/2015. | Secondary Effluent | Wastewater Regulatory Program | GA0020516 | WWTP | Stream | Stream | Other |  | Emily Wingo | Emily Wingo | Emily Wingo | 6/5/2015 12:00:00 AM | Chattahoochee | 6/5/2015 12:00:00 AM | 2015-05-29 |  | 1 | Chattahoochee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This spill was due to high Ammonia entering into the sewer. The Ammonia loading temporarily interfered with the biological activated sludge process causing increased Total Suspended Solids in the plant effluent system resulting in a discharge of 4744 kg of suspended solids, 50% above the permitted limit. CWW continues to investigate the high result. | The influent NH3 has returned to tolerable limits and the South Columbus Water Resource Facility has returned to normal operations. CWW anticipates no adverse impact to the Chattahoochee River. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-17 | 0 | 1 | 1 | 1 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490 |  |  | 88 mg/L
2015-04-22 | 2015-04-22 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 36.8 mg/L on 04/22/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-03 | 2018-06-03 | Douglasville-Douglas County Water & Sewer Authority (Northside WPCP) | Douglas | Douglasville | St Andrews Lift Station – 8521 St Andrews Pkwy, Douglasville, GA 30135. | 5625 |  | Raw Sewage | Wastewater Regulatory Program | GA0030350 | Lift Station | Stream | Stream | Equipment failure |  |  | Juan Robles | Juan Robles | 6/4/2018 12:00:00 AM | Chattahoochee | 6/4/2018 12:00:00 AM |  |  | 0 | Little Wolf Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Piping thrust restraint system in the valve pit failed causing a leak in the line at a pipe joint. | - Mechanics were dispatched to the site and turned off the pumps stopping the spill. - Pumper trucks were used to pump down the well and while a repair was made. - Crews cleaned and disinfected the area around the manhole where the spill occurred. - Signs were posted in the area to notify residents and the public of the spill. - Notification given to EPD, the Health Department, and local media. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-01 | 2017-12-01 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Thomas Field Rd. & Central Shop Rd | 800 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System |  |  | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/4/2017 12:00:00 AM | Oconee |  |  |  | 1 | Camp Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Unstopped line, built a containment wall Lime area Continued monitoring |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-08 | 0 | 0 | 0 | 0 | 0 | 0 | Kevin Veal |  | CITY OF MILLDEGEVILLE
2017-03-27 | 2017-03-27 | CITY OF SMYRNA - PUB WORKS | Cobb | Smyrna | 3351 Lee St. and 3331 Lee St. | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nicjack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the pipe. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-24 | 2015-04-24 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2375 Butner Road, SW | 440 | fax received 4/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-02 | 2016-09-02 | Douglas, City of (Southeast WPCP) | Coffee |  | 1303 South Peterson Ave | 30000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne |  | 9/2/2016 11:15:00 AM | Satilla | 9/2/2016 12:00:00 AM | 2016-09-03 |  | 1 | Un-named tributary of Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Hydraulic overload of the collection system from Tropical Storm Hermine. |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-09-08 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-08 | 2015-05-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2043 Brewer Blvd, SW | 318 | fax received 5/09/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/9/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-14 | 2015-01-14 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6059 Arden Ct | 1200 | REC FAX 1/15/2015. SPECIALIST REC FAX 1/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  |  | Emily Wingo | Emily Wingo | 1/15/2015 12:00:00 AM | Ocmulgee | 1/15/2015 12:00:00 AM |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease | Cleared Blockage. Cleared gravity main of roots and grease blockage, cleaned other gravity mains downstream of blockage and restored flow back to normal. Post signs in area of spills. Follow up: Root cut and televise gravity mains. |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-22 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 678.422.2834
2017-11-02 | 2017-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1335 Donald Lee Hollowell Pkwy. | 1960 | Fax sent 2017-10-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 11/3/2017 12:00:00 AM |  | 11/2/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause not specified. | Crew used a hydraulic pressure cleaner to clear the blockage. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-12 | 2017-04-12 | Cobb County MS4 | Cobb |  | 2345 Cobb Parkway | 5080 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The Water System was notified at 9:46 a.m. and our crew stopped the overflow at 2:00 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-14 | 2016-09-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 926 Fellswood Court, Stone Mountain | 2160 | Notification received on September 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/14/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected on September 14, 2016 at 19:30 hours when a crew pressure washed the 8" sewer main 200ft, removed the blockage at 153ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-19 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-28 | 2018-06-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Avondale Estates | 1064 Hess Drive Avondale Estates, GA 30002 | 980 | manhole 15-218-s012 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/28/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Cobb Fowler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure wash |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-10 | 2016-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2730 Peyton Springs Circle, SW | 2191 | fax received 8/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/11/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-06 | 2018-08-06 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 614 Little Ridge Lane | 680 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/6/2018 12:00:00 AM |  |  |  |  | 0 | McClane Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-22 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 4566 Elan Church Rd, Forest Park | 1600 | Fax received on 02/22/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 2/22/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Conley Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of spill was roots. | Cleared blockage, cleaned line and returned flow to normal. Root will be cut and line televised to assess collection system. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-24 | 0 | 1 | 1 | 0 | 0 | 0
2015-02-03 | 2015-02-03 |  | Hall | Flowery Branch | McEver Road, Flowery Branch | 7200 | Notification received on February 13, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/4/2015 12:00:00 AM |  |  |  |  | 0 | Mud Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Force main leaking | In order to permanently repain the leaking force main, a new jack and bore had to be completed with a new force main under McEver Road. The new line was completed on Saturday, February 6, 2015 at 10:30 PM. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 |  | DeKalb | Decatur | 1948 East Starmount Way, Decatur | 31500 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 19:00 hours when the heavy rain subsided and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2018-09-07 | 2018-09-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2906 N Hills Dr. NE - Atlanta | 300 | Fax sent 2018-09-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/8/2018 12:00:00 AM |  | 9/8/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-06 | 2017-03-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 394 Cleveland Ave. SW - ATL | 5900 | Fax received 2017-03-07. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Paul Moisan | 3/7/2017 12:00:00 AM |  | 3/6/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-07 | 2016-02-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | ATLANTA | 2833 Glenlocke Circle, NW | 2000 | fax received 2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/8/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-16 | 2015-04-16 |  | DeKalb | Brookhaven | 3768 Ashford Creek Ave, Brookhaven | 2480 | Notification received on April 28, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh |  | 4/28/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:20 hours when a crew rodded and pressure washed the 8" sewer main upstream 700ft, cleared the grease blockage, and restored services. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-14 | 2016-06-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1464 McLendon Avenue, NE | 5 | fax received 6/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  |  |  |  | Kim Hembree | Kim Hembree | 6/15/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This is a private spill | This is a private spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-08 | 2015-09-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2567 Candler Woods Drive, Decatur | 3760 | Notification received on September 16, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/8/2015 12:00:00 AM |  |  |  |  | 0 | Doless Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:15 hours, when the clean up crew, pressure washed the 8" sewer main 172ft, cleared the grease blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-23 | 2018-03-23 | Columbia County (Little River WPCP) | Columbia | Evans | 607 Ronald Reagan Dr.- Evans | 200 | Fax sent 2018-03-36 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/26/2018 12:00:00 AM |  |  |  |  | 1 | Tributary to Betty's Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Dirt and debris | Unstopped sewer main with high pressure jet machine. Vacuumed sewer main. Cleaned up around manhole. Planned follow-up with video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-17 | 2016-05-17 | Savannah, City of (President Street WRF) | Chatham | savannah | 1835 Mitchell Street | 125 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Hydraulic Overload |  | Steve Fox | Steve Fox | Steve Fox | 5/17/2016 12:00:00 AM | Savannah | 5/17/2016 12:00:00 AM |  |  | 1 | springfield canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Major rain event caused overflow of storm water and sewage mix from a manhole to the storm system | Reduced flows to spill by reducing flows from an upstream sewer lift station. Spill notification markers were placed at the spill site where discharge went into canal and along other locations – Springfield Canal / West Gwinnett Street and Bowles Ford Park / Springfield Canal. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-01 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-21 | 2016-05-21 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 3113 Glynn Mill Drive | 1402 | fax received 5/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/21/2016 12:00:00 AM |  |  |  |  | 1 | Jacks Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-03-11 | 2015-03-11 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1895 Plaza Lane, SW | 1250 | fax received 3/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/16/2015 12:00:00 AM |  |  |  |  | 1 | Utoy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-01 | 2017-12-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1829 Lawrenceville Highway Decatur Ga 30033 | 30 | four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/1/2017 7:12:00 PM | Ocmulgee |  |  |  | 1 | South Fork Peachtree Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage causing overflow | Pressurewashed sewer lateral from manhole 18-062-s067 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Kathy Eads |  | Dekalb County Department of Watershed Management
2016-11-29 | 2016-11-29 | Cobb County Water System | Cobb |  | 3111 Port Cobb Drive | 1310 |  | Raw Sewage | Wastewater Regulatory Program |  |  | Stream | Stream | Contractor |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/29/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of an installed plug and contractor pumps were off in sewer main causing the manhole to overflow into the Chattahoochee River. | The crew stopped the overflow at 12:40 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-22 | 2015-02-22 |  | DeKalb | Decatur | 2597 Dusty Lane, Decatur | 2320 | Notification received on February 23, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/22/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 17:24 hours when a crew pressure washed downstream 160ft, removed blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-28 | 2017-03-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1386 Sylvan Rd. SW - ATL | 2475 | Fax received 2017-03-29 Correction received 2017-03-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/29/2017 12:00:00 AM |  | 3/28/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-13 | 2017-11-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3466 Paces Pl. NW - ATL UPDATE: This is not a city problem. Changed to private spill. | 875 | Fax sent 2017-11-13 UPDATE: This is not a city problem. Changed to private spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/14/2017 12:00:00 AM |  | 11/13/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. UPDATE: This is not a city problem. Changed to private spill. | Crew used a hydraulic pressure cleaner to contain the spill. UPDATE: This is not a city problem. Changed to private spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-20 | 2017-03-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4 Adair Ave. SE - ATL | 50 | Fax received 2017-03-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/22/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4100 Cusseta Road, Columbus | 6577 |  | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Alys Hannum | Paul Moisan | 1/18/2017 12:00:00 AM |  |  |  |  | 1 | Tributary of Bull Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. The basin is No Name Creek Basin. | Once the debris was cleared from the main the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 |  | DeKalb | Decatur | 217 Green Street, Decatur | 200 | Notification received on April 6, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/5/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 15:48 hours, when the heavy rain subsided and the sewer flow returned to normal./ |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 348 Armour Dr. NE - ATL | 13450 | Fax received 01/18/2017 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Storm Drain, Stream |  | Debris |  | Paul Moisan | Alys Hannum | Paul Moisan | 1/18/2017 12:00:00 AM |  | 1/17/2017 12:00:00 AM | 2017-01-14 | 2018-02-07 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill is debris in the mainline. | Steps taken to prevent reoccurence. Placed on periodic inspection schedule. Need for upgrading, etc. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-19 | 0 | 0 | 0 | 1 | 1 | 0
2017-04-11 | 2017-04-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2503 Skyland Trail, Atlanta | 2080 | Notification received on April 14, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/11/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:59 hours when a crew root-cut the 8" sewer main 150ft, clearing the blockage at 80ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-04 | 2015-06-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2545 Forrest Hills Drive, SW | 8500 | fax received 6/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/4/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-25 | 2016-08-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2049 Rector Drive, SW | 750 | fax received 8/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/27/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-07 | 2017-03-07 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 230 Wolfe Lane | 6921 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/13/2017 12:00:00 AM | Oconee |  |  |  | 0 | Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, Rags, large rocks | Rod and flush; removed rocks | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-12 | 2016-05-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Wood Street, NW | 6360 | fax received 5/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/13/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-17 | 2016-02-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 601 McDonough Blvd, SE | 25875 | fax received 2/18/2016. CTS No. 79094 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/18/2016 12:00:00 AM |  |  | 2016-02-18 | 2017-03-03 | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-19 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-05 | 2017-11-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2419 Greenwat Drive Decatur 30035 | 735 | Handwritten | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/5/2017 12:00:00 AM |  |  |  |  | 1 | Cobbs Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Trenched around manhole removing concrete from around manhole and ring and cover so sewer would flow into the manhole, |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 | Earnest Veal |  | Dekalb County Department of Watershed Management
2017-07-05 | 2017-07-05 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 351 Pellet Court - Martinez | 4500 | Fax received 2017-07-06 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/6/2017 12:00:00 AM |  | 7/5/2017 12:00:00 AM |  |  | 1 | Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Unstopped overflow with high pressure jet machine. Cleaned up area. Posted signs. Main line will be cleaned thoroughly and videoed to determine cause. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-02 | 2016-08-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Atlanta | 3700 Block of Knights Academy Road | 1500 | Verbal notification received 8/3/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/3/2016 12:00:00 AM |  |  |  |  | 1 | Cherry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-02-26 | 2015-02-26 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1339 Rev. J. L. Mills Sr. Way | 6555 | REC CALL 2/27/2015. REC EMAIL 3/2/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/27/2015 12:00:00 AM | Ocmulgee | 2/27/2015 12:00:00 AM |  |  | 1 | Ocmulgee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sewer main | Debris will be removed from the surrounding area. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-27 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2015-04-29 | 2015-04-29 |  | Fulton | Atlanta | Hartsfield-Jackson Atlanta Airport, College Park Lift Station No. 1 | 2500 | Verbal and email confirmation received 4/29/2015. | Raw Sewage | Wastewater Regulatory Program |  | N/A | Stream |  | Vandalism |  | Kim Hembree | Kim Hembree | Kim Hembree | 4/29/2015 12:00:00 AM |  |  |  |  | 1 | Sullivan Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The pump station was damaged by vandals. | Damaged equipment repaired. Police report filed. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Hartsfield-Jackson Atlanta International Airport
2018-05-30 | 2018-05-30 | Columbia County (Little River WPCP) | Columbia | Evans | 4550 Wilma Court - Evans | 3000 | Fax sent 2018-05-31 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Other |  | Grease |  |  | Alys Hannum | Alys Hannum | 5/31/2018 12:00:00 AM |  |  |  |  | 0 | Private Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags | Unstopped sewer main with high pressure jet machine. Cleaned up around manhole and spread lime. Planned follow up video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 |  | Henry | Stockbridge | 678 Fairhaven Blvd. Stockbridge, GA 30281 | 7250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/28/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 678 Fairhaven Blvd. Stockbridge |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-24 | 2016-03-24 | Nicholls, City of | Coffee | Nicholls | Coffee County Correctional Facility in Nicholls GA. | 5000 | Notification was made Coffee County EMA who contacted the local health department. The local media was also contacted according to Ms. Latasha Battle, Facility Safety Manager. | Raw Sewage | Coastal District | GAJ020267 | Collection System | Ground, Stream | Stream | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/24/2016 5:08:00 AM | Satilla | 3/24/2016 12:00:00 AM |  |  | 1 | Unnamed Tributary to Hog Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was caused by clogged manholes on facility grounds. | Blocked manholes were cleared restoring flow. Sand bags were utilized to stop the spill and lime was applied at spill site. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-04-07 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2400 Block of Meadowbrook | 44280 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2018-04-21 | 2018-04-21 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 4050 Carolene Way - Cumming | 3500 | Call received 2018-04-24 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Pump Station | Ground | Swale | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 4/24/2018 12:00:00 AM |  | 4/21/2018 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Float got stuck in a high position, preventing pumping; auto-dial alarm did not call operator as it should have. | Fixed float, called in SCADA tech to fix auto-dialer. Limed area, posted signs. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-28 | 2015-02-28 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 4033 Stovall Terr. NE | 291 | fax received 3/01/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/28/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-27 | 2016-01-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2847 Bouldercrest Road, Atlanta | 3000 | Notification received on January 28, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 1/27/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 15:00 hours, when a crew built a berm around ther broken joint, called in an emergency repair and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-11 | 2017-08-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3932 Tipperary Trail, Tucker | 6000 | Notification received on August 15, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/11/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 13:41 hours when the first responder crew dug up and repaired the 10-inch sewer main and restored nromal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-14 | 2017-04-14 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 3749 Clubhouse Lane | 2700 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/14/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Honey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Repair piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-17 | 2015-12-17 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Social Circle - Little River Water Pollution Control Plant | 374026 | verbal notification received 12/18/2015 | Treated Effluent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/18/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This is an outfall spill of partially treated waste water. According to facility personnel, the aerators in the aeration basin had to be turned off and partially treated waste water passed through the facility to the permitted outfall. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-08-09 | 2016-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill Street, NW | 4600 | fax recieved 8/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/10/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | The crew used a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-21 | 2015-12-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 559 Woodward Way, NW | 720 | fax received 12/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/22/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | the crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-10 | 2015-04-10 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1275 Springhouse Lane, SW | 2763 | fax received 4/11/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 4/11/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-11 | 2017-09-11 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 403 Bear Branch Pump Station | 21000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/12/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Big Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Outage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-28 | 2017-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 650 Selig Dr. SW - ATL | 137200 | Call received 2017-12-28. Fax received 2017-12-29. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 12/29/2017 12:00:00 AM |  | 12/28/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Collapsed pipe. | Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 250 Carriage Court, Athens | 21820 | Initial call 11/3, Full report faxed 11/4 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Oconee | 11/2/2015 12:00:00 AM | 2015-11-02 |  | 1 | North Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | overflow due to flooding during major rain event | sewer upgrade is under design |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-04 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-02-11 | 2015-02-11 | International Paper Company (Savannah) | Chatham | Savannah |  | 18000 |  | Treated Effluent | Coastal District | GA0001988 | Pump Station | Bay | N/A | Equipment failure |  | John Kalp | John Kalp | John Kalp | 2/11/2015 2:30:00 PM | Savannah |  |  |  | 0 | Savannah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | NA | 0 |  |  | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2015-02-19 | 1 | 0 | 0 | 0 | 0 | 0
2016-07-25 | 2016-07-25 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 2700 Jefferson Rd., Athens | 320 | Initial email 7/26, full report faxed 7/27 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 7/26/2016 12:00:00 AM | Oconee | 7/25/2016 12:00:00 AM |  |  | 1 | unnamed tributary to Brickyard Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disposable wipes and grease blocked the sewer line creating a pressure break at the pipe joint | Rodded the line and repaired the joint |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | (706) 613-3481
2017-11-09 | 2017-11-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 532 Cleveland Ave. SW | 30 | Fax sent 2017-11-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 11/10/2017 12:00:00 AM |  | 11/9/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 |  | Hart | Hartwell | Harliway South Forest Wastewater Plant Trunk Line | 750000 | this is one of three major spills that occurred in the area on 11/2/2015. Total volume = 1.478 mgd | Unknown | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Savannah | 11/3/2015 12:00:00 AM | 2015-11-03 |  | 1 | un-named tributary to Little Cedar Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | extremely heavy rainfall overloaded the sewer system |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-23 | 2017-02-23 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 6550 McDonough Drive - Norcross | 2351 | Fax received 2017-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/23/2017 12:00:00 AM |  | 2/23/2017 12:00:00 AM |  |  | 1 | North Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and other products | Removed all deposited solids; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-27 | 2015-02-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3333 Lake Valley Road, NW | 280 | fax received 2/28/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/27/2015 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-27 | 2017-12-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2177 Parkview Run Run - ATL | 226 | Fax sent 2017-12-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 12/28/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-01 | 2016-11-02 |  | Fulton |  | 6442 Grey Fox Way Riverdale Georgia, 30296 | 900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-12 | 2015-08-12 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 2484 River Ridge Road | 660 | Email received 8/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/12/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Tobler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1303 West Fair Street, SW | 2500 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-22 | 2017-02-28 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | Crossroads WWTP, Gulfstream Rd., Savannah, GA | 0 | Initial and full report received via email 3/2/17. | Treated Effluent | Coastal District | GA0038326 | WWTP | Stream | Stream | Other |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 3/2/2017 12:00:00 AM | Savannah | 3/2/2017 12:00:00 AM | 2017-02-28 | 2018-01-31 | 1 | St. Augustine Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Slug flow from an industrial facility upset the biological process at the plant affecting floc formation. Effluent turbidity and TSS concentration increased as a result. Permitted weekly TSS is 7.5 mg/L. Reported TSS results were: 2/22 = 31.4 mg/L 2/23 = 36.1 mg/L 2/24 = 42 mg/L 2/25 = 42 mg/L 2/26 = 46.6 mg/L 2/27 = 39.2 mg/L 2/28 = 28.8 mg/L | Operations staff made adjustments to plant processes to mitigate the impact of the slug. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-03-03 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6620
2015-10-10 | 2015-10-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 1239 | fax received 10/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/11/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed main line | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-09 | 2017-11-09 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 241 Brookwood Way | 3420 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/9/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Almand Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris from Vandalism | Remove Debris | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-17 | 2015-06-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3095 Revere Court, Doraville | 5640 | Notification received on June 22, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  |  |  | 6/17/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:41 hours when a crew rodded and pressure washed the 8" sewer main upstream 700ft, cleared the grease blockage, and restored services. |  |  |  | 2015-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Near Frazier Drive | 33084 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/1/2016 12:00:00 AM | Oconee | 4/1/2016 12:00:00 AM | 2016-04-01 |  | 1 | unnamed tributary to Oconee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Extremely wet weather caused amount of flow through sewer line to rise high enough to breach the opening of a manhole with a failed structural integrity. | Contractors have been hired to repair this manhole. Once the rain stopped (April 4), lime was applied to the area and the manhole was temporarily patched. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-04 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2016-12-10 | 2016-12-13 |  | Rockdale |  | 2362 Brent Moore Point | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2016 12:00:00 AM | Oconee |  |  |  | 0 | Snapping Shoal Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gease/Debris | Removed | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-09 | 2015-11-09 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Stockbridge | 300 Speer Road, and the CCWA lift station. | 19500 | Fax received 11/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/10/2015 12:00:00 AM | Ocmulgee | 11/10/2015 12:00:00 AM | 2015-11-10 | 2016-11-01 | 1 | Cotton Indian Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Due to heavy rains, infiltration and inflow was the cause of this spill. | SSO was stopped, and lift station was able to resume operations. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-13 | 0 | 1 | 1 | 1 | 0 | 0
2016-02-24 | 2016-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2 Hanover West Court, NW | 100 | fax received 2/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/25/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed manhole |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-03 | 2017-01-05 | Cochran WPCP | Bleckley | Cochran | S. 6th St & Ann St. (MH 1284/MH 1293), E. Peter St & S. 5th St (MH 1264/MH 1265), Cochran | 10000 | Phone call received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0032107 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Jordan Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause of the spill was 10.2" of rainfall. The 100 year 24 hour storm event is 8.4". | Phase 3 GEFA will target the remaining manholes that need rehabilitation and any terracotta lines will be replaced. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | Jacob Daniel |  | CITY OF COCHRAN
2018-03-21 | 2018-03-21 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 403 Bear Branch Rd. Perry, GA 31069 | 18800 | I contact Travis Falcione and he mentioned that the spill did not reach waters of the State and that there was a nearby pond in the area. The facility has started sampling for the upstream and downstream sites. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/21/2018 12:00:00 AM |  |  |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Line Break | The site has been cleaned and signs were posted. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-30 | 2016-01-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6852 Maddox Road, Morrow | 2700 | Fax received on 01/31/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/31/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Probable cause of spill - grease. | Blockage cleared, flow returned to normal. The area was cleaned, and work orders were made to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-01 | 0 | 1 | 1 | 0 | 0 | 0
2016-01-22 | 2016-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | Verbal notification received 1/25/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outfall Spill due to TSS violation: Reported Daily TSS = 85 mg/L. Total volume = 75,630,000 |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-15 | 2017-01-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3810 Ellsworth Way, Atlanta | 1600 | Notification received on January 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/15/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:49 hours when the crew pressure washed the sewer main 200 ft to clear the blockage at 181 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-30 | 2016-09-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5540 Glenrich Drive, Dunwoody | 2760 | Notification received on October 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 10/1/2016 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected on September 30, 2016 at 18:31 hours when a crew pressure washed the sewer main 105ft, removed the blockage at 100ft and restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-18 | 2015-06-18 | Fulton County MS4 | Fulton |  | 2600 Fox Hall Ln College Park, GA 30349 | 9920 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/23/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collaped Spillway /Broken Pipe | Applied enzymes to affected area. Contractors have the authorization to repair broken pipe. By-pass pump set up to stop the SSO. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-06-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1851 Mclendon Avenue, NE | 1420 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-29 | 2016-01-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way, SW | 1200 | Fax received 1/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/30/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-27 | 2017-12-27 | Cobb County Water System | Cobb |  | 2081 Twelve Oaks Cir/Cherokee Street | 640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and solids in 8" Concrete |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-08 | 2017-07-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 1953 Crescent Centre Blvd, Tucker | 8500 | Notification received on July 10, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/8/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:03 hours when a crew pressure washed the 8 inches sewer main 155 ft and removed the grease blockage at 150 ft to restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1013 Standing Boy Court, Columbus | 207 | Telephone call received on 04/01/2016; fax received on 04/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Reservoir |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lake Oliver | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overload due to exscessive rainfall. | When the hydraulic overload subsided, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-22 | 2016-11-22 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 574 Industrial Way - Swainsboro | 15615 |  | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System |  | Ditch | Equipment failure |  |  | Alys Hannum | Hsin Yeh | 11/22/2016 12:00:00 AM |  | 11/22/2016 12:00:00 AM |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The spill was caused by a malfunctioning level sensor at the pump station. A back-up emergency floar was also damaged during the high level event. | A high vacuum truck was used to reclaim 100% of the spill. Lime was then applied to the ditch area. Sensor and emergency floats were replaced. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-09 | 2015-11-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 616 Mitchell Bridge Rd., Athens | 7885 | Initial email 11/9, full report faxed 11/10 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/9/2015 12:00:00 AM | Oconee | 11/9/2015 12:00:00 AM |  |  | 1 | tributary to Middle Oconee | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | manhole overflow caused by flooding during a major rain event | sewer upgrade is under design |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-06-08 | 2015-06-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 237 Brookview Dr. | 2700 | REC FAX 6/9/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 6/9/2015 12:00:00 AM | Flint | 6/8/2015 12:00:00 AM |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease | Cleared blockage. Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Televise. Lines will be televised and root cut and if problem is located it will be repaired. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-10 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 770-960-5205
2017-01-17 | 2017-01-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1277 Cornwell Road, Decatur | 5020 | Notification received on January 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 1/17/2017 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sewer main crossing | The problem was corrected at 12:20 hours when the crew installed an 8 inch solid sleeve, stopped the spill and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-11-14 | 2017-11-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1879 Glenwood Avenue Atlanta GA 30316 | 4800 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/16/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Sugar Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Dug up and bermed broken 8" main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Travis Lucy |  | Dekalb County Department of Watershed Management
2018-06-06 | 2018-06-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1835 Piedmont Ave. NE - Atlanta | 200 | Fax sent 2018-06-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 6/7/2018 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed Mainline | Crew set up a by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-26 | 2017-01-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3204 Chamblee Dunwoody Road, Chamblee | 6240 | Notification received on January 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/26/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:43 hours when the crew pressure washed the 15" sewer main upstream 150 ft between manholes, cleared the grease/rag blockage at 80 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-18 | 2015-01-18 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1430 North Chase Street | 1351 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/18/2015 12:00:00 AM | Oconee |  |  |  | 1 | Brickyard Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Shop towels clogged the sewer line resulting in an overflow estimated at 1351 gallons | Corrective action has been taken to mitigate and reduce the adverse effects of the overflow. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-24 | 2015-09-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2013 Claude Street, NW | 15 | fax received 9/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-01 | 2015-08-01 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | 9508-9682 Hwy 92 Woodstock | 4500 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 8/4/2015 12:00:00 AM | Coosa |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in outfall line | Jetted line to remove blockage. Cleaned spill area with vac truck, raked and limed affected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Hooper | 770-592-6000 | CITY OF WOODSTOCK
2018-04-23 | 2018-04-23 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Fern Valley Drive, Toccoa, GA | 5000 | Email received on 04/23/2018 | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/23/2018 12:00:00 AM |  |  |  |  | 0 | Ward Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive inflow due to the heavy rainfall | Wait until the rain stopped |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-04-25 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Monroe, City of (Jack's Creek WPCP) | Walton | Monroe | 1407 South Madison | 31200 | verbal notification received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Hard Labor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Manhole surging due to excessive rain. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MONROE
2015-10-13 | 2015-10-14 | Cobb County (RL Sutton WRF) | Cobb |  | 8140 Troon Circle | 104400 |  | Raw Sewage | Wastewater Regulatory Program | GA0026140 | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/14/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The creek bank collapsed and caused the 36 " pipe to break and shift allowing the ser to escape directly into the tributary to Chattahoochee River. | The Water System was notified at 9:00 a.m. and the contractor set up by-pass pumping to stop overflow by 9:00 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2017-07-17 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd | 70000 |  | Raw Sewage | Wastewater Regulatory Program | GA0025852 | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/16/2017 12:00:00 AM | Suwannee |  |  |  | 1 | Hat Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Wet Weather 2.3 inches of rain | The spill stopped during the night of July 18, 2017. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2922 Pemberton Court, MH ID 70653 (address and ID are the location of the manhole). | 1440 | Email received on 08/20/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 8/20/2015 12:00:00 AM | Ocmulgee | 8/19/2015 12:00:00 AM |  |  | 1 | Ditch feeding Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of the spill was grease and roots. There are no commercial sources of grease upstream from this location and residential grease is not regulated. | Debris has been removed and the affected area is being disinfected with lime. This line has been scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly "hot spot" inspection list and chemically treated for root control. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-08-21 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY
2015-01-26 | 2015-01-26 | Cobb County MS4 | Cobb |  | 1307 Pebble Creek Rd. | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/26/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 in Clay Main | Spread Lime at Spill Area | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-29 | 2016-09-29 | Cobb County Water System | Cobb |  | 213 Indian Hills Trails | 440 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/29/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-21 | 2017-02-22 | Kingsland, City of (Kingsland WPCP) | Camden | Kingsland | Little Catfish Creek, adjacent to lift station on Clarks Bluff Road | 100000 |  | Raw Sewage | Coastal District | GA0037800 | Collection System | Stream | Stream | Power failure |  | Charlotte Nevill | Charlotte Nevill | Charlotte Nevill | 2/22/2017 12:00:00 AM | Saint Mary's | 2/22/2017 12:00:00 AM | 2017-02-22 |  | 1 | Little Catfish Creak | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 21 | 1 | Power failure at a lift station next to the gravity line was being repaired | Installed pipe liner to 10" gravity line crossing under Little Catfish Creek to the Lift Station on Clarks Bluff Road. A video camera inspection confirmed proper liner placement. | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 2017-03-13 | 1 | 1 | 1 | 0 | 0 | 0
2015-02-27 | 2015-02-27 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1339 Reverend J.L. Mills Sr Way | 22500 | REC EMAIL 2/27/2015 with no detail. REC REPORT 3/3/2015 | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 3/3/2015 12:00:00 AM | Ocmulgee | 3/27/2015 12:00:00 AM | 2015-03-03 |  | 1 | Ocmulgee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | broken sewer main | The MWA has hired a contractor to make the repair on the sewer main. A by-pass pump has also been set-up to reroute the sewage to a downstream manhole. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-03 | 0 | 1 | 0 | 1 | 1 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2018-01-10 | 2018-02-05 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens |  | 0 | Water did not enter spill way | Unknown |  | GA0021725 | [6 empty] | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/2/2018 12:00:00 AM | Oconee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-04 | 2015-12-04 | Cobb County (RL Sutton WRF) | Cobb |  | 4941 South Cobb Dr. | 2860 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8 inch DI Main | Spread Lime at Spill area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-07 | 2015-12-08 | Cobb County (Noonday Creek WPCP) | Cobb |  | 1800 Barrett Lakes Blvd | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Casue in 8 in PVC Main | Grease Cause in 8" PVC Main | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-07 | 2015-12-08 | Cobb County (Noonday Creek WPCP) | Cobb |  | 1800 Barrett Lakes Blvd | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Casue in 8 in PVC Main | Grease Cause in 8" PVC Main | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-30 | 2017-03-30 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 3620 Longlake Dr. - Duluth | 2374 | Fax received 2017-03-30 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 3/31/2017 12:00:00 AM | Chattahoochee | 3/30/2017 12:00:00 AM |  |  | 1 | Unnammed Tributary of Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease; Debris - wipes, paper, and other products. | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 2017-06-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1697 Line Street, Decatur | 100 | Notification received on June 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/28/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:30 hours when a crew rodded the right of way clean out 30(ft) to clear the blockage at 15(ft) and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-12 | 2015-06-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1077 Peeples Street, SW | 1014 | fax received 6/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/13/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-29 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 4462 W Anderson Road | 10 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1741 Willis Mill Rd. SW - ATL | 9150 | Fax received 2017-02-28. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 2/28/2017 12:00:00 AM |  | 3/27/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-15 | 2016-12-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 441 Clairmont Avenue, Decatur | 2880 | Notification received on December 19, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/16/2016 12:00:00 AM |  |  |  |  | 0 | Peavine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | The problem was corrected at 21:45 hours, when a crew pressure washed the 8 inch main 400 feet to remove the blockage and restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-19 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-16 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 28350 | Notification of this spill was not received until 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outfall No. 3 plug failure. | Plug replaced | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-30 | 2018-06-30 | Cobb County Water System | Cobb | Marietta | 5011 White Blvd | 280 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clay Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" main | stopped spill and spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-13 | 2017-12-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 938 Mathews St. SW - ATL | 4425 | Fax sent 2017-12-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/14/2017 12:00:00 AM |  | 12/13/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-22 | 2018-03-22 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3241 Cherry Street - Augusta | 0 | Anonymous caller reported there was a manhole overflowing behind the building. Technicians found no active spill but they did find a manhole holding. Undetermined spill amount. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Unknown |  |  | Alys Hannum | Alys Hannum | 3/22/2018 12:00:00 AM |  |  |  |  | 1 | Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Undetermined | Opened up with the jet truck. Lime was placed at the base of the manhole where it was wet looking. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-21 | 2016-09-21 | Cobb County Water System | Cobb |  | 791 Mitsy Ridge Drive | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Pipe |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-05 | 2016-12-05 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift Station in Eastman, GA | 5000 | District Office made aware of incident on December 6, 2016. Requested emergency action requirements be implemented for spill. | Raw Sewage | Southwest District | GA0046485 | Lift Station | Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 1/5/2017 10:00:00 AM | Ocmulgee |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall accumulation in the area (3.5") prior to overflow. | Public notification requirements started on 12/6/2016. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-01-05 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 6826 James B Rivers Memorial Drive, Stone Mountain | 1425 | Notification received on September 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/12/2017 12:00:00 AM |  |  |  |  | 0 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 10:25 hours, when the crew setup vacuum trucks to hold the sewer in the wet well until the power board was repaired, which restored the normal flow at 10:25. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-07 | 2015-03-07 |  | Gwinnett | Norcross | 6027 Mary Jo Lane | 3060 | fax received 3/08/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/7/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-02-23 | 2018-02-23 | Cobb County Water System | Cobb |  | 123 Saine Drive | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/23/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-10 | 2017-04-10 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn |  | Harry Driggers Blvd. | 8400 |  | Raw Sewage | Coastal District | GA0025313 | Force Main | Ditch | Canal | Pipe failure |  | Charlotte Nevill | Bill Hawthorne | Bill Hawthorne | 4/10/2017 11:00:00 AM | Altamaha | 4/10/2017 12:00:00 AM |  |  | 1 | Altamaha Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken force main | Repaired force main | 778eb569-f488-4d14-a790-403523838de4 | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-04-14 | 1 | 1 | 0 | 0 | 0 | 0
2015-03-12 | 2015-03-12 |  | DeKalb | Chamblee | 2515 Northeast Expressway, Chamblee | 67560 | Notification received on March 16, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 3/12/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The problem was corrected at 13:09 hours when a crew pressure washed the 8" sewer main 320ft upstream, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-03 | 2018-04-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2933 Laguna Drive Decatur GA 30032 | 2140 | pressure washed from m/h 15-200-s055 and 15-200-s066 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/3/2018 9:10:00 PM | Ocmulgee |  |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-11 | 2015-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 1260 | fax received 9/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/12/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-09 | 2016-07-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3748 Salem Springs Court, Lithonia | 126075 | Notification received on July 13, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Natural Disaster |  |  | Hsin Yeh | Hsin Yeh | 7/11/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 1:25 pm, when a crew recharged the generator's battery, started the pump and contacted Georgia Power to restore power. The battery and the battery charger to the generator were replaced on Monday July 11, 2016. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-13 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-11 | 2018-02-22 | Springfield, City of (Springfield WPCP) | Effingham | Springfield |  | 3800000 |  | Raw Sewage | Coastal District | GA0020770 | Force Main | Stream | Stream | Pipe failure |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 2/22/2018 12:00:00 AM | Ogeechee | 2/26/2018 12:00:00 AM | 2018-02-23 | 2019-03-29 | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 0 | failure of section of force main not at beaded connection | replaced damaged force main, relocation of force main at head works of plant to create air gap, extraction of water with vac trucks, spreading of lime, and major spill protocol followed | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-03-06 | 1 | 1 | 1 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1239 Ladd Street, SW | 1360 | fax received 2/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-23 | 2017-02-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 445 Kendrick Ave. SE - ATL | 840 | Fax received 2017-02-24. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Paul Moisan | 2/24/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-24 | 2016-01-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 914 Ridge Avenue, NW | 1000 | fax received 1/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-22 | 2015-09-22 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/14/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 49.0 mg/L on 09/22/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-09 | 2015-03-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 105 Westchester Dr. | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/9/2015 12:00:00 AM | Satilla |  |  |  | 0 | un-names tributary to Middle Oconee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Dead tree fell, damage aerial sewer line | used 3 vac trucks to eliminate overflow while repairs were being made | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-08 | 2016-12-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | DeKalb | Atlanta | 349 Clifton Rd, NE, ATL | 900 | Fax received on 12/09/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/9/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 4045461328 | ATLANTA, CITY OF
2018-06-07 | 2018-06-07 | Cobb County Water System | Cobb |  | 1030 Bud Ct | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/7/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Allatoona Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" PVC main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-02 | Imerys Clays Inc. (Deepstep Road Plant - Buffalo China Operations) | Washington |  |  | 0 |  | Primary Effuent | Wastewater Regulatory Program | GA0002780 |  | Stream |  |  |  | Jill Causse | Jill Causse | Sarita Banjade | 1/2/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-28 | 2016-12-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 3341 Jim Moore Rd - Lawrenceville | 1435 | Fax received 2016-12-29 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Force Main | Stream | Stream | 3rd party contractor |  |  | Alys Hannum | Hsin Yeh | 12/29/2016 12:00:00 AM |  | 12/28/2016 12:00:00 AM |  |  | 1 | Little Mulberry Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure caused by third party damage from excavation/grading. | Raked area and spread like, placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-31 | 2017-07-31 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2620 Chaucer Drive | 3250 | Email received 2017-08-01 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Rags |  |  | Alys Hannum | Alys Hannum | 8/1/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Debris | The sewer gravity main was jet washed to open the line. The Sewer main will be videoed to determine condition of pipe and information will be used to determine next course of action. Lime was spread in the area and covered with fresh dirt. Hard surface areas were washed and vacuumed |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-15 | 2016-09-15 |  | Cobb |  | 3111 Port Cobb Dr./ South Cobb Dr. | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Removed Debris and Spread Lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-15 | 2016-09-15 |  | Cobb | Marietta | 3111 Port Cobb Dr./ South Cobb Dr. | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Removed Debris and Spread Lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-28 | 2017-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2096 Niskey Lake Trl. SW - ATL | 1500 | Fax sent 2017-12-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 12/29/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pumping system malfunction. | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-28 | 2015-09-28 | Social Circle, City of (Little River WPCP) | Walton |  | Rest Area No. 52 | 2150 | fax received 9/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/29/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | blockage caused by shop towels | debris cleaned out |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2345 Adams Drive | 255 | fax recieved 2/04/2016. COA Service Request No. 7519562 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-26 | 2017-05-26 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 125 Autry Rd. & Tucker Rd. - Winder | 5040 | Call received 2017-05-26; Email received 2017-06-02 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Pump Station | Stream |  | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 6/2/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the pumping station primary pump caused when a low level float became dislodged and was sucked up into the pumping volute. Backup pump was in the shop for repairs. | Barrow county will look into procuring an additional bypass pump to have on hand for emergency situations. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 304 Bay Street (underpass), Macon MH ID 57603 | 49835 | Phone call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this major spill was hydraulic overload due to heavy rains in the MWA service area. According to the National Weather Service, Macon-Bibb County received 5.42 inches of rain on Friday, April 1st. | This manhole is located in the street. Any debris was removed from the area. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0 | Anthony Hopkins | 478-464-5677 | MACON WATER AUTHORITY
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2334 Adams Drive, NW | 25 | fax received 1/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-03 | 2015-08-03 |  | Fulton |  | 3422 Cape York Trace Alpharetta 30022 | 11640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/6/2015 12:00:00 AM | Chattahoochee | 8/3/2015 12:00:00 AM |  |  | 0 | Big Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, Debris | The manhole has been cleaned. The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. The area impacted by the spill is in the proces of being cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-30 | 2018-06-30 | Cobb County Water System | Cobb |  | 5011 White Blvd | 280 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Other | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clay Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 11:05 a.m. an our crew topped the overflow at 1:23 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3691 Collier Dr NW - ATL | 6375 | Fax received on 01/21/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2018-04-16 | 2018-04-16 | Dawson, City of (Dawson WPCP) |  | Dawson | lynwood Dr. Off Lee St. | 3000 | manhole 2110 | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Ground |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/16/2018 12:00:00 AM | Flint |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | clog | Jet/vat truck cleared debris |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-21 |  |  | DeKalb |  | 4009 Flakes Mill Road | 50 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-01 | 2015-05-01 |  | Columbia |  | 4708 Woodbridge Drive | 400 | fax received 5/01/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Other |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/1/2015 12:00:00 AM |  |  |  |  | 1 | Private pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken force main | Shut down lift station. Repaired force main. Posted signs |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-04-13 | 2015-04-13 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 644 Joseph E. Lowery Boulevard, NW | 180 | fax received 4/14/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/16/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-19 | 2016-06-25 | Rochelle, City of (Southeast WPCP) | Wilcox | rochelle | At outfall location of WPCP. | 20000 | NOV issued to WPCP for failure to recognize and report MS as required. | Treated Effluent | Southwest District | GA0024236 | WWTP | Stream | Stream | Other |  |  | Jay Howell | Jay Howell | 8/23/2016 12:00:00 AM | Suwannee | 7/19/2016 12:00:00 AM | 2016-07-19 |  | 1 | Mill Creek tributary | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Thru plant major spill for exceeding weekly effluent BOD. No oral notification given - District Office recognized spill during July 2016 DMR review. BOD exceedance likely due to algae die off and facility personnel spraying for duckweed in the previous month. | PNs done on 7/20/2016 (TV, Radio, Print media and Health Dept.). Stream monitoring initiated 7/19/2016. PN ran in legal organ on 7/23/2016. PN posted at outfall location - there are no downstream public access use areas per the facility and there are no known surface water withdrawals within 20 miles downstream of WPCP that are used for drinking water intake/treatment purposes. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2016-08-23 | 1 | 1 | 1 | 1 | 0 | 0 | James Rhodes |  | CITY OF ROCHELLE (SOUTHEAST WPCP) | [8 empty] | 89
2016-08-13 | 2016-08-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 761 Woodward Way, NW | 968 | fax received 8/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 8/14/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-16 | 2018-05-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3812 McElroy Road, Doraville GA 30340 | 300 | manhole 18-320-s071 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Contractor |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/17/2018 1:24:00 PM | Ocmulgee | 5/16/2018 12:00:00 AM |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractors are relining the main (Company Layne I Liner) the pump was not enough to keep up with flow, causing the sewer to come out of the cone of the manhole. | Contractor brought in a bigger pump |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Cobb County MS4 | Cobb |  | 787 Stone Harbor Parkway | 330 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of infiltration in 8" Clay main causing the manhole to overflow into a tributary of Nickajack Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-23 | 2015-01-24 |  | Lowndes | Valdosta | 700 Block of Cypress Street | 9000 | Email notification from the City received 1/24/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Storm Drain |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/24/2015 12:00:00 AM |  |  |  |  | 1 | Storm drain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-09-11 | 2017-09-14 | Saint Marys, City of (Point Peter WPCP) | Camden | St. Mary's | Multiple lift stations throughout the city of St. Mary's. | 400000 | Mr. Broxton sent in a spill report, received on 9/18/2017. Spill was initially called in to emergency spill line. See CTS # 84047 for additional information. | Raw Sewage | Coastal District | GA0039047 | Lift Station | Ground, Stream | Stream | Natural Disaster |  | ADMINTEST ADMINTEST | Brett Berry | Brett Berry | 9/11/2017 12:00:00 AM | Saint Mary's | 9/12/2017 12:00:00 AM | 2017-09-12 | 2018-09-12 | 1 | Saint Mary's River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Power failures from trees falling due to Hurricane Irma. | N/A | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-25 | 1 | 1 | 0 | 0 | 0 | 0
2015-04-08 | 2015-04-09 |  | Franklin | Royston | 310 Spring Street Extension, Royston, Georgia | 250000 | Notification received on April 20, 2015. | Treated Effluent | Wastewater Regulatory Program |  | WWTP | Stream |  | Operator error |  |  | Hsin Yeh | Hsin Yeh | 4/16/2015 12:00:00 AM |  |  |  |  | 0 | Hannah Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | On April 7, 2015, City crews removed accumulated solids from the pump station near Royston LLC, which is part of the City's collection sewerage system. The pump station needed repairs and to facilitate this work, about 500 gallons of solids were pumped out of the wetwell. The solids removed from the pump station were brought to the City's Sewage Treatment Plant (STP) for treatment and disposal. The solids were placed in the bar screen, which is the first step of treatment at the facility. On April 8, 2015, Butch Watson, Superintendent for the City, noticed that the treatment plant was upset and the biological matter in the lagoons appeared to have died. The effluent flow at the discharge of the facility was sampled April 8 & 9. The effluent flow was approximately 250,000 gallons per day. The results were available on April 16th which showed that the BOD was 70 mg/L. This is more than 150% over the weekly permitted value of 45 mg/L. The NPDES permit defines this as a major spill | City staff took immediate actin to secure new biological matter from the City of Hartwell to reseed the treatment plant. This was completed and the plant is returning to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-21 | 2018-01-21 | Columbia County (Little River WPCP) | Columbia | Evans | 3503 Lost Tree Lane - Evans | 2800 | Fax sent 2018-01-22; received 2018-03-13 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 1/22/2018 12:00:00 AM |  | 1/21/2018 12:00:00 AM |  |  | 1 | Reed Creek ( Private Pond) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Unclogged sewer main with high pressure jet machine. Cleaned up spill area. Posted signs. Planned follow up to remove roots, camera line. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-28 | 2016-08-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3312 Stonecrest Court, Chamblee | 13680 | Notification received on August 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/28/2016 12:00:00 AM |  |  |  |  | 0 | Warren Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 12:44 hours when the crew pressure washed the overflowing manhole 350ft, cleared blockage of grease at 340ft and restored service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-01 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-10 | 2017-05-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1461 Woodbine Ave. SE - ATL | 1950 | Fax received 2017-05-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/11/2017 12:00:00 AM |  | 5/10/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | Crew repaired the by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-19 | 2017-07-19 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1259 Augusta West Parkway - Augusta | 9000 | Email received 2017-07-20 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/20/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Sewer gravity main was augered to open the line. The Sewer main will be videoed to assess pipe structure and information will be reviewed to determine next course of action. On the property, 4” – 6” of dirt was removed from the top layer of the affected area. Lime was spread in the area and covered with fresh dirt. Hard surface areas were washed and vacuumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 142500 | Notification received on November 4, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/2/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 16:50 hours when the storm event passed, the water receded, the manhole stopped spilling and resumed to regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-04 | 2017-01-04 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 298 Imperial Ct. - Cumming | 500 | Fax received 2017-01-04 | Raw Sewage | Wastewater Regulatory Program | GA0046019 |  | Stream | Stream | Grease |  |  | Alys Hannum | Hsin Yeh | 1/4/2017 12:00:00 AM |  | 1/4/2017 12:00:00 AM |  |  | 1 | Big Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was the result of grease and rags partially blocking the sewer line. | Blockage jetted and cleared, lime applied. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 485 Charter Oak Dr. SW - ATL | 50 | Fax received 2017-04-05. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4175 Bakers Ferry Road, SW | 6084 | fax received 4/02/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-26 | 2018-01-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1550 Peachtree St. NE - ATL | 1350 | Fax sent 2018-01-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 1/27/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-21 | 2016-02-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 451 Sawtell Avenue, SE | 75 | fax received 2/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/22/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-11 | 2015-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Woodbine Circle, SE | 10 | fax received 9/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 9/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-12 | 2017-12-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall St. SE - ATL | 230 | Fax sent 2017-12-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 12/12/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | RM Clayton WRF Outfall - ATL | 157920000 | Notification received 2017-04-06. 5-day letter received 2017-04-14. | Undisinfected Primary Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to severe storm events resulted in a passive bypass of the sand filters. | The event ended when influent flow rates substantially declined. City of Atlanta is currently implementing a $56 million capital improvement project at the RM Clayton Headworks to help reduce the amount of influent solids from the wastewater collection system. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-13 | 2017-12-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 5420 Riverdale Road, College Park Manhole - 2205616 | 3000 | Fax received on 12/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/13/2017 12:00:00 AM | Flint |  |  |  | 1 | Sullivan Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-18 | 0 | 1 | 1 | 0 | 0 | 0 | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2016-03-01 | 2016-03-02 | Thomaston, City of | Upson | Thomaston | 511 Whittle Row | 50 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2016 12:00:00 AM | Flint |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots | Debris was removed from the surrounding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-08 | 2018-02-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2461 Metropolitan Pkwy SW - ATL | 1350 | Fax sent 2018-02-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/9/2018 12:00:00 AM |  | 2/8/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-24 | 2018-01-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 145 E. Lake Dr. SE - ATL | 720 | Fax sent 2018-01-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/25/2018 12:00:00 AM |  | 1/24/2018 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1942 East Starmount Way, Decatur | 23100 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 18:02 hours, when the rain subsided and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-02 | 2015-12-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 363 Fielding Lane, SW | 3600 | fax received 12/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/2/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-07 | 2016-06-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 4422 Northeast Expressway, Doraville | 344 | Notification received on June 8, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/7/2016 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment | The problem was corrected at 17:01 hours, when a crew used a full circle clamp around the steel pipe to seal the crack, stopped the leak and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-13 | 2018-01-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 9860 Chappell Lane - Jonesboro | 2500 | Fax sent 2018-01-13 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Paul Moisan | 1/13/2018 12:00:00 AM |  |  |  |  | 1 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 4102 Trenton Way | 7200 | fax received 12/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/28/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wash out of sewer main | Replaced clay sewer main with PVC pipe. Temporarily shored pipe with 4x4 post and straps. Planning permanent repair |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-11-10 | 2015-11-10 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrencevile | 155 Meadow Brook Drive | 6300 | ERT notified 11/10/2015. CTS No. 78284 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Pew Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 700 Block of Cypress Street | 29500 | Verbal/Email notification received 2/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-09-02 | 2016-09-02 | Tifton, City of (New River WPCP) | Tift | Tifton | 80 Old Brookfield Road, Tifton | 90540 | Email received on 09/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 9/3/2016 12:00:00 AM |  |  | 2016-09-03 |  | 1 | New River Basin | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole was surcharged due to inflow from the storm. | Hydrated lime was spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-09-07 | 0 | 1 | 1 | 1 | 0 | 0
2015-12-11 | 2015-12-11 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2772 Portland Place, (GM ID 4526 | 3660 | Email received on 12/11/2015, and a follow-up on 12/15/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 12/11/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Walnut Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was a broken sewer main. | A point repair was made to the section of sewer main pipe that was broken. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-17 | 1 | 1 | 0 | 0 | 0 | 0
2015-09-20 | 2015-09-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1903 Sunbury Place, NW | 990 | fax received 9/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/21/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-05 | 2015-08-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5987 Magnolia Ridge, Stone Mountain | 1500 | Notification received on August 6, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/5/2015 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:08 hours when a crew pressure washed the sewer main 475 ft, clearing the grease blockage 225 ft and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-07 | 2018-03-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2886 3rd Ave. SW - Atlanta | 30 | Fax sent 2018-03-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-04 | 2017-08-04 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2862 Dixie Road - Fort Benning | 572 | Telephone call received on 08/04, and fax received on 08/05. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | 3rd party contractor |  | Paul Moisan | Paul Lamarre | Paul Moisan | 8/4/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Laundry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fort Benning contractor bored a hole in 20" sanitary sewer line. | Sanitary sewer pipe was repaired and overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 950af5dc-8813-11e1-9b1d-12313d2b7a91 | 2017-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 651 14th Street, NW | 25 | fax received 10/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/12/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-28 | 2016-07-28 |  | Henry | Stockbridge | 678 Fairhaven Blvd | 1400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/15/2016 12:00:00 AM |  |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1300 Block of N. Lee Street | 279330 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2016-07-19 | 2016-07-19 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Fishing Creek Lift Station | 850 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Lift Station | Ground |  | Equipment failure |  |  | Dagny Pariani | Dagny Pariani | 7/20/2016 12:00:00 AM | Oconee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical pump malfunction at Fishing Creek Lift Station | Repaired pump and monitored manholes in the area |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2015-07-12 | 2015-07-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 976 Margaret Place, NW | 71 | fax received 7/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/13/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-05 | 2018-01-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2103 Defoors Ferry Rd. NW - ATL | 765 | Fax sent 2018-01-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  | Alys Hannum | Alys Hannum | Alys Hannum | 1/6/2018 12:00:00 AM |  | 1/5/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Thomaston, City of (Town Branch WPCP) | Pulaski | Thomaston | 98 Third Street | 980 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/18/2015 12:00:00 AM | Upper Ocmulgee | 8/18/2015 12:00:00 AM |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to a grease blocage which caused a gravity sewer line to backup. | The blockage was cleared and the gravity sewer line was immediately placed back in service. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-21 | 2017-02-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3645 Waldrop Road, Decatur | 5100 | Notification received on February 22, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/21/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:00 hours when a crew pressure washed the 8" sewer main 250ft removed the blockage at 150ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-16 | 2016-08-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3155 Delmar Lane, NW | 1050 | fax received 8/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/17/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-11 | 2016-10-11 | Savannah, City of (President Street WRF) | Chatham | Savannah | Lift Station 12 - 1356 Lavon Ave. | 3240 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Stream | Stream | Power failure |  | David Lyle | Hailey Harden | Hailey Harden | 10/11/2016 12:00:00 AM |  | 10/11/2016 12:00:00 AM |  |  | 0 | Hayner's Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  | 0 | Hurricane Matthew cause power outages at lift station 12, overflowing man holes | repaired generator and cleaned up area with City of Savannah Vehicles and Staff. Spill notification markers were placed at the spill site and at Halcyon Bluff Boat Ramp | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0
2018-01-17 | 2018-01-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4049 Northstrand Drive, Decatur GA 30035 | 2920 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Lift Station | Storm Drain |  | Contractor |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/17/2018 8:41:00 PM | Ocmulgee | 1/17/2018 12:00:00 AM |  |  | 1 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | asphalt blockage near manhole 15-157-s066 | Rodded 8" main to clear blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-19 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Devin Olawumi |  | Dekalb Co Dept. Watershed Management
2015-07-31 | 2015-07-31 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawerenceville | 564 Gwinnett Drive | 9600 | fax receive 8/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/3/2015 12:00:00 AM |  |  |  |  | 1 | Fairground Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-09-08 | 2015-09-08 | Newton County (Yellow River WPCP) | Newton |  | 765 Lakeside Circle | 6800 | fax received 9/09/2015 | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/9/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Beaverdam Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Jetted the lines to remove blockage and hired contractor to heavy duty jet sewer lines. Camera lines and vacuumed up grease and toilet paper from around spill site. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | NEWTON COUNTY
2017-07-04 | 2017-07-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3649 Highway, Atlanta | 3080 | Notification received on July 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/4/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:40 hours when a crew pressure washed the sewer main 144 ft, removed the blockage at 130 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-10 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Cobb County Water System | Cobb |  | 1855 Hurt Road | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-28 | 2016-03-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 7334 Conkle Road, Jonesboro MH #2201174 | 800 | Fax received on 03/29/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 3/29/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Reeves Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2800 Martin L King Jr Dr SW - ATL | 26250 | Fax received on 01/17/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/17/2017 12:00:00 AM |  |  | 2017-01-17 | 2018-02-07 | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-18 | 0 | 0 | 0 | 1 | 1 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-07-02 | 2015-07-02 | Villa Rica, City of (Tallapoosa West WPCP) | Carroll | Villa Rica | 154 Millwheel Drive, Villa Rica off of Poole Road | 2000 | Notification received on July 26, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0027162 | WWTP | Stream |  | Roots |  |  |  | Hsin Yeh | 7/2/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary of Crawfish Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root growth in manhole, trapping grease, and blocking discharge line. | Remove roots and grease. Will cut down and remove trees around manhole and sewer lines once an easement is established. |  | d80f500b-2416-4653-adb7-23760952ef3b |  | 2015-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1320 Regency Center Drive | 227250 | CTS No. 78653 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/29/2015 12:00:00 AM |  |  | 2015-12-29 | 2017-01-19 | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Collapsed line |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-29 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-15 | 2015-11-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Cleveland Avenue, SE / Jonesboro Road, SE | 720 | fax received 11/16/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 11/16/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-27 | 2016-07-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 3547 Buford Highway, Brookhaven | 2280 | Notification received on July 28, 2016 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/27/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 10:50 hours when the crew rodded the overflowing manhole, cleqred blockage of grease and tissue at 3ft and restored service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-28 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 555 Fortson Rd., Athens | 13165 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Oconee | 12/30/2015 12:00:00 AM | 2016-01-02 |  | 1 | un-named tributary to Middle Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole overflowed during flood event. | Cleaned area. Sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2016-01-06 | 2016-01-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 750735 | Due to communication issues, this event was not reported/clarified to EPD until 1/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/20/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain event |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-30 | 2015-10-30 | QUIGG BRANCH WATER POLLUTION CONTROL PLANT | Rockdale |  | 1455 Rock Hill Dr. | 990 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/9/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bricks and Debris | Removed Bricks and Debris | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-09 | 0 | 0 | 0 | 0 | 0 | 0 | Charman Griffits | 770-278-7500 | Rockdale Water Resources
2016-09-08 | 2016-09-08 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn |  | At the intersection of Hamilton Road & Sea Island Road (SSI). | 10000 |  | Raw Sewage | Coastal District | GA0021521 | Force Main | Ditch | Ditch | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/8/2016 9:45:00 AM | Satilla | 9/9/2016 12:00:00 AM | 2016-09-08 |  | 1 | Frederica River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Spill believed to have been caused when a contractor was widening Hamilton Road and installed the bulkhead/culvert at the tidal drainage ditch. The construction activity may have damaged the 4" force main causing the spill. | The associated lift station was temporarily shut down and crews repaired and rerouted the force main and return the lift station (#2051) back into operation. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-09-15 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-09 | 2016-02-09 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 2281 Midway Road, Douglasville MH 10889 | 450 | Telephone call on 02/09/2016; fax received on 02/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Roots |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/9/2016 12:00:00 AM | Chattahoochee | 2/9/2016 12:00:00 AM |  |  | 1 | Tributary D to Little Anneewakee Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in line. | VacCon crews were dispatched, and a jet truck was used to clean the line and clear blockage. Repair of the line is scheduled. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-16 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-24 | 2016-06-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1033 Hollywood Road, NW | 2850 | fax received 6/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/25/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-21 | 2015-05-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 945 Silverwood Dr. | 2400 | REC FAX 5/22/2015. Not delivered to program until 5/27/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System |  |  | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/22/2015 12:00:00 AM | Flint |  |  |  | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease | Cleared blockage. Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated to determine cause. Follow-up: Televise. Lines will be televised and root cut and if problem is located it will be repaired. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-27 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 770-960-5205
2015-11-30 | 2015-11-30 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1406 Marvin Griffin Road | 3000 | fax received 12/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 12/3/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical issues with the bypass pump | A backup bypass pump was set up and placed in service. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-12-10 | 2017-12-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3940 Ashford Lake Court, Atlanta GA 30319 | 1800 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/10/2017 7:05:00 PM | Ocmulgee | 12/10/2017 12:00:00 AM |  |  | 1 | Nan | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | According to Torrance Jones, during pressure washing process an unknown blockage was hit. Caused spill into creek | Restored flow by pressure washing |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-11 | 0 | 1 | 0 | 0 | 0 | 0 | Torrence Jones |  | Dekalb County Department of Watershed Management
2018-01-05 | 2018-01-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4675 Bryn Mawr Cir. NW - ATL | 3 | Fax sent 2018-01-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/6/2018 12:00:00 AM |  | 1/5/2018 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-12 | 2016-08-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 56 Westminster Drive, NE | 994 | fax received 8/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 8/15/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-03 | 2015-08-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Avondale | 260 Northern Avenue, Avondale. | 3150 | Notification received on August 6, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/3/2015 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:51 hours when a crew pressure washed the 15" sewer main downstream 225 ft, clearing the grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-14 | 2015-11-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1146 Spring Valley Lane, NE | 150 | fax received 11/15/2015` | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 11/15/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-30 | 2018-08-30 | Patterson, City of (Patterson WPCP) | Pierce | Patterson | Manhole located on Dallas St. & Hwy. 32, Williams St. and Echols St. | 500 |  | Raw Sewage | Coastal District | GA0037206 | Collection System | Stream | Ditch | Wet weather |  | Brett Berry | Brett Berry | Brett Berry | 8/31/2018 9:00:00 AM | Satilla | 8/31/2018 12:00:00 AM |  |  | 1 | Patterson Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred following heavy rainfall of 2.9 inches in less than forty-five minutes. | Signage has been placed at the location of the spill site. Local health department and local media were notified. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-09-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-07 | 2015-05-07 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 445 Cleveland Avenue, SE | 530 | fax received 5/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/7/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-09 | 2015-08-09 | Cobb County MS4 | Cobb |  | 2896 Macedonia RD | 2896 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | 3rd party contractor |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in the 8 in DI sewer main | Cleaned area and spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-14 | 2016-06-14 | Thomaston, City of | Upson | Thomaston | 855 N. Center Street Wal-Mart Lift Station | 3021 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/14/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The Cause of this major spill is a broken sewer main. | The affected area was clean and disinfected. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-20 | 2017-05-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 15 Crooked Creek Drive - Lawrenceville | 4295 | Fax received 2017-05-20 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Andrea Kemberling | 5/22/2017 12:00:00 AM |  | 5/20/2017 12:00:00 AM |  |  | 1 | Lee Daniel Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and other products | Raked area and spread lime and placed signs at spill and waterway. |  | 49e1c9c4-eb6e-11e0-b8d8-000c29971acc | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-09 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | 3781 Wylly Avenue, Brunswick | 1000 |  | Raw Sewage | Coastal District | GA0025313 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2016 9:00:00 AM | Satilla | 10/27/2016 12:00:00 AM |  |  | 1 | Academy Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift Station (#4005) power failure due to Hurricane Matthew. | Restarted diesel bypass pump, water in fuel shutdown, bad wire to sensor, repair made and bypass pump restarted again until permanent power was restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-31 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-09 | 2017-04-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1970 Rena Cir. SW - ATL | 7590 | Fax received 2017-04-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/10/2017 12:00:00 AM |  | 4/9/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew made repairs to the mainline to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-16 | 2015-04-16 |  | Wilkes | Washington | Rocky Creek Wastewater Treatment Plant | 110000 | Notification received on April 17, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/17/2015 12:00:00 AM |  |  |  |  | 0 | Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical equipment failure | Repairs were made to the pump and controls and two additional alarms were installed in the event this should occur again. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-06 | 2017-06-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 138 West Paces Ferry Rd. NW - ATL | 450 | Email received 2017-06-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 6/7/2017 12:00:00 AM |  | 6/6/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-13 | 2017-10-13 | Savannah, City of (President Street WRF) | Chatham | Savannah | 313 East River Street, Savannah, GA | 245 | Initial notification and full report received 10/13/17 | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain, Stream | Stream | Grease |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 10/13/2017 12:00:00 AM | Savannah | 10/13/2017 12:00:00 AM |  |  | 1 | Savannah River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage in line | Cleared blockage and washed area down. Will investigate cause. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-10-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6584
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2418 Howell Mill Rd. NW - ATL | 3060 | Fax received 2017-04-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/26/2017 12:00:00 AM |  | 4/25/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris and roots in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-24 | 2017-05-24 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1283 Rev. JL Mills Sr. Way, Macon MH ID 56754 | 21250 | Email received on 05/25/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ground, Storm Drain | Ditch | Pipe failure |  |  | Paul Moisan | Paul Moisan | 5/25/2017 12:00:00 AM | Ocmulgee | 5/25/2017 12:00:00 AM | 2017-05-25 |  | 0 | Bay Street/Downtown | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was a broken sewer main. | Debris was removed from the area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-25 | 0 | 1 | 0 | 1 | 0 | 0
2017-06-30 | 2017-06-30 | Cobb County Water System | Cobb |  | 3950 Mars Hill Road | 680 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/30/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of inflow causing it to overflow into Lake Acworth. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3151 Macon Road, Columbus | 22728 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Lindsay Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-14 | 2016-04-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3700 Roswell Road, NE | 20 | Fax received 4/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/15/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-09 | 2015-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 83 Bates Avenue, NE | 20 | fax received 10/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/11/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to remove the blockage from the mainline |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-26 | 2015-01-26 | Cobb County MS4 | Cobb |  | 1307 Pebble Creek Road | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/26/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped the overflow at 4:00 P.M. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-18 | 2017-12-18 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2621 Washington Road - Augusta | 600 | Email sent 2017-12-20 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 12/20/2017 12:00:00 AM |  |  |  |  | 1 | Rock Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage in the sewer gravity main | Sanitary sewer main was augered to break up the grease in the line. The are around the manhole was cleaned up and lime was spread. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-19 | 2018-05-23 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Approx. 100 feet south of Oglethorpe Blvd Bridge | 855000 | City reported to the GA emergency response team by 5/21/2018, and 6/7/2018 sent spill report to WRP. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Juan Robles | 5/21/2018 12:00:00 AM |  |  |  |  | 0 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Lift Station Equipment Failure/Manhole Overflow | Failed pumps were pulled from the station and have been sent off for repairs. The pump rendered inoperable by the broken valve (#4) has been relocated to another position (#3). The station controls have been gutted and replaced with new starters and control relays which replace a failed PLC. Replacement of all station valves is currently in the process of purchasing. A permanent tap of the force main for future bypass pumping is also in the planning stage and should be accomplished by 7/7/2018. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | d80f500b-2416-4653-adb7-23760952ef3b | 2018-06-27 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-10 | 2015-11-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 616 East Paces Ferry Road, NE | 50 | fax received 11/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Operator error |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by the city crew jet rodding the service lateral. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-30 | 2016-03-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2886 Sandpiper Circle, SW | 2100 | fax received 3/31/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/31/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-04 | 2016-02-04 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Westover Blvd., Albany | 390000 | An email was sent on 02/04/2016, and a report was received on 02/17/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Ditch | Shoreline |  |  |  | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/5/2016 12:00:00 AM | 2016-02-05 |  | 1 | Canal at S. Westover Blvd. | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Line was blocked, and a jet vac was used to clear the line. | Lime was used to disinfect the area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-20 | 2015-04-20 |  | DeKalb | Decatur | 2505 Columbia Drive, Decatur | 1280 | Notification received on April 28, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/20/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary to Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blocakge | The problem was corrected at 11:38 hours when a crew pressure washed the 8" sewer main upstream 387ft, cleared the grease blockage, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-10 | 2016-07-10 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 2344 Stancrest Lane | 1854 | fax received 7/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/11/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Place signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-01-22 | 2017-01-22 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | 300 Richey Lane into Indian Creek | 36000 |  | Raw Sewage | Coastal District | GA0024431 | Lift Station | Stream | Stream | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 1/23/2017 9:00:00 AM | Satilla | 1/23/2017 12:00:00 AM | 2017-01-23 |  | 1 | Indian Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Lift station power failure due to down power line. | Power was restored within two hours and spill was stopped. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-01-31 | 1 | 1 | 0 | 0 | 0 | 0
2017-07-25 | 2017-07-25 | Pembroke, City of (Pembroke WPCP) | Bryan | Pembroke |  | 7000 | On July 25, 2017, the City of Pembroke experienced a raw sewage spill of approximately 7,000 gallons from Lift Station #1 located at 144 West Industrial Boulevard in Pembroke, Ga.. The spill entered an unnamed tributary of Mill Creek in the Ogeechee River Basin. | Raw Sewage | Coastal District |  | Lift Station | Ditch | Ditch | Equipment failure |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 7/26/2017 8:30:00 AM | Ogeechee | 7/26/2017 12:00:00 AM |  |  | 0 | Mill Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was a result of inflow from heavy rain that overwhelmed the lift stations pumping capacity. | Upon discovery of the overflow, the lift station was monitored until the pumps caught up with the flow. The City will start conducting sewer main smoke testing as soon as possible to identify and correct any breaches in the sewer system. | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-07-26 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1600 Block of James P. Rogers Drive - Valdosta | 57500 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/22/2017 12:00:00 AM | 2017-01-22 |  | 1 | Mud Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Large amounts of rainfall in excess of 6 inches within a 24-hour period. | Cleanup and disinfecting at overflow location and stream discharge points. Began monitoring and testing the area.The location has been added to the city's list for rehabilitation. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 60800 | fax received 12/24/2015. CTS No. 78623 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-02 | 2017-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2067 Manchester St. NE - ATL | 5 | EDIT 2018-02-20: This is a private spill, not a city spill. Fax received 2017-08-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/3/2017 12:00:00 AM |  | 8/2/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | EDIT 2018-02-20: This is a private spill, not a city spill. Debris in the mainline | EDIT 2018-02-20: This is a private spill, not a city spill. Self-contained |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 |  | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is day three of an ongoing outfall spill. Reported TSS = 41 mg/L. Volume = 86,600,000 gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-19 | 2017-06-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3479 Hickory Walk Lane, Ellenwood | 2025 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/19/2017 12:00:00 AM |  |  |  |  | 0 | Clarks Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Malfunction pump | The problem was corrected at 07:36 hours when the technician recognized the issue and shut the pump down to contain the spill, made the repairs and resumed normal service at the lift station. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-12 | 2015-01-16 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville | Bldg 1340 located off of West 18th Street on Fort Stewart at Lift station #899. | 600 | A heavy rain event occurred during the time of the spill and flushed the stormwater collection system and spill. | Raw Sewage | Coastal District | GA0047180 | WWTP | Ground, Stream |  | Equipment failure |  | John Kalp | John Kalp | John Kalp | 1/12/2015 12:46:00 PM | Ogeechee | 1/12/2015 12:00:00 AM |  |  | 0 | Mill Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Yes | 0 | See "Documents" Section |  | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2015-01-12 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Creekside Subdivision. | 7020 | Fax received on 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Dixie Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy I/I caused by recent rainfall events. | Parked vehicles with tire on top of two MH covers to minimize the overflow. Investigations to located I/I sources |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-02 | 2015-12-02 | Rome, City of (Rome WRF) | Floyd |  | Bells Ferry Road Lift Station | 28000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Equipment failure |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/3/2015 12:00:00 AM | Coosa |  |  |  | 0 | Dozier Creek Tributary of Oostanaula | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ruptured Force Main | Fixed main see report dated 12/3/2015 | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4560 | CITY OF ROME
2015-11-18 | 2015-11-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 1290 | fax received 11/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/18/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-21 | 2015-03-21 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 780 Sydney Marcus Blvd, NE | 20 | fax received 3/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Contractor |  |  | Kim Hembree | Kim Hembree | 3/22/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Private contractor damaged the mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-28 | 2017-02-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 241 Daniel Ave. SE - ATL | 50 | Fax received 2017-08-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-19 | 2017-06-28 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 160 Parkway Drive | 8670 | No Fish Kill spotted. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Line Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Rags | Jet0Vac the City sewer main | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-08 | 2015-03-09 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | Lower Poplar WWTP. | 0 | REC CALL 3/10/2015. REC EMAIL 3/11/2015. REC STREAM MONITORING 3/23/2015. | Treated Effluent | Wastewater Regulatory Program | GA0024538 | WWTP | Stream | Stream |  |  | Emily Wingo | Emily Wingo | Emily Wingo | 3/10/2015 12:00:00 AM | Ocmulgee | 3/10/2015 12:00:00 AM | 2015-03-11 |  | 1 | Ocmulgee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The blanket level in one of the final clarifiers got too high and solids pushed through a weak spot in the effluent trough, making their way into the plant effluent. | The blanket level in one of the final clarifiers got too high and solids pushed through a weak spot in the effluent trough, making their way into the plant effluent. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-10 | 0 | 1 | 0 | 1 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5680 |  |  | 77 mg/L
2015-04-15 | 2015-04-15 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 29.6 mg/L on 04/15/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-10 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | Manhole 417 at Hwy 82 and Don Foster Rd | 48960 | This sewer line/manhole overflowing is a recurring issue. | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 2/4/2016 12:00:00 AM | Flint | 2/4/2016 12:00:00 AM | 2016-02-04 |  | 1 | Brantley Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 4 inches of rain on already saturated ground. | Clean and lime area as needed. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-11 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | City of Dawson
2015-02-03 | 2015-02-03 |  | Richmond | Augusta | 3627 Bermuda Circle | 600 | fax received 2/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/4/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2016-06-07 | 2016-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1695 Pryor Road, SW | 1500 | fax received 6/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/8/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-02 | 2016-06-06 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 0 | Stream monitoring initiated 6/3/16. Public notification posted at City Hall on 6/2/16. Notification to the Burke Co. Health Department completed on 6/16/16; and notification published in the July 6, 2016 edition of The True Citizen newspaper. Stream monitoring ceased for the June 2nd major effluent spill upon the facility initiating stream monitoring for the June 21st major spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream | Other |  | Delaine Scott | Delaine Scott | Delaine Scott | 6/13/2016 12:00:00 AM | Savannah | 6/2/2016 12:00:00 AM | 2016-06-03 | 2016-06-22 | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. |  | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-06-20 | 1 | 1 | 0 | 1 | 0 | 0 | Jonathan Tindall | 912-449-0999 | Tindall Enterprises, Inc.
2018-08-06 | 2018-08-06 | Blackshear, City of | Pierce | Blackshear | Manhole located at Hwy. 84 and Carraway | 1000 |  | Raw Sewage | Coastal District | GAJ020001 | Collection System | Storm Drain | Ditch | Other |  | Brett Berry | Brett Berry | Brett Berry | 8/6/2018 11:00:00 AM | Satilla | 8/6/2018 12:00:00 AM |  |  | 0 | Albaha River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravity flow sewer line partially clogged. | Sewer clog was cleared, signage placed at the discharge point, area was cleaned and local health department and local media were notified. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-08-07 | 1 | 1 | 0 | 0 | 0 | 0
2015-08-31 | 2015-08-31 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 1953 Crescent Center Blvd, Tucker | 8840 | Notification received on September 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/1/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:42 hours, when the clean-up crew, pressure washed the 8" sewer main 275 ft, cleared the grease blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 596 Peyton Rd. SW - ATL | 200 | Fax received 2014-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3262 W Roxboro Rd. NE - ATL | 7110 | Fax received 2017-03-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/28/2017 12:00:00 AM |  | 3/27/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 530 Bay Creek Road (Outfall) | 16800 | CTS No. 78628 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/26/2015 12:00:00 AM |  |  | 2015-12-25 | 2017-01-15 | 1 | Big Flat Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rain. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF LOGANVILLE
2016-03-29 | 2016-03-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2886 Sandpiper Circle, SW | 1000 | Fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/30/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-02 | 2015-07-02 | Tifton, City of (New River WPCP) | Tift | Tifton | Influent manhole prior to pump station at WWTP | 1500 | REC CALL 7/3/2015. REC WRITTEN REPORT 7/8/2015. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Stream | Equipment failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 7/3/2015 8:42:00 AM | Suwannee | 7/3/2015 12:00:00 AM |  |  | 1 | New River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lighting strike damaged influent pump and temporarily interrupted power to the pump controls | Damage pump sent off for repair and temporary pump installed in place of damaged pump | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-07-06 | 0 | 1 | 0 | 0 | 0 | 0 | Scott Murphy | (912) 281-4186 | ESG Operations, Inc. | [5 empty] | CITY OF TIFTON | 229-391-3937
2016-08-26 | 2016-08-29 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 160 Lenox Parkway | 3750 | fax received 8/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Other |  |  | Kim Hembree | Kim Hembree | 8/29/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Stream bank erosion | Jetted sewer main, repaired break in sewer pipe, performed temporary stream bank stabilization, posted signs |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2018-01-16 | 2018-01-16 | East Point (City of)- Sewers | Fulton | East Point | 8-inch Sanitary Sewer; Under Headwall GDOT Box Culvert Stream crossing; Interstate I-285; between Exit 1 and 2 West Side. | 9000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mimms Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Damage GDOT drainage flume |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | 5th St and 4th Ave SW, Moultrie | 500 | Using CCTV, dye, and smoke testing to search for additional I/I issues. | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System |  |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall impacted the area causing sewer surcharging | Monitoring site. Area limed. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2016-03-09 | 2016-03-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1266 Simpson Road, NW | 1302 | Fax received 3/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/10/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3207 Meadowbrook/East Lindsay Drive, Columbus, GA | 6851 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Lindsay Creek. | Once the rain subsided, flow returned to normal, and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-21 | 2015-04-21 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 29.2 mg/L on 04/21/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-20 | 2015-10-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2914 Collier Drive, NW | 30 | 10/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Kim Hembree | Kim Hembree | 10/21/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-29 | 2015-06-29 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 7/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 60.4 mg/L on 06/29/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-14 | 2018-09-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 618 North Indian Creek Drive Clarkston GA 30021 | 1380 | manhole 18-044-s021 | Raw Sewage |  | GA0024147 | Collection System | Storm Drain |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/15/2018 12:17:00 AM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-10 | 2017-10-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 280 Murray Hill Ave. NE - ATL | 80 | Fax sent 2018-02-20 after discrepancies noted in semi-annual report. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-27 | 2017-11-27 | Cobb County Water System | Cobb |  | 2081 Tweleve Oaks Cir | 640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/30/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Crew stopped the spill at 11:30 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | Stephem McCullers |  | Cobb County Water System
2015-10-11 | 2015-10-11 | Paulding County (Coppermine Road WPCP) | Paulding |  | Outfall line Sunnerhill Road | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 10/11/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tribute to Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/Grease | Jetted & Cleared lines of grease and debris | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-10-21 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey |  | PAULDING COUNTY - COPPERMINE WRF
2018-04-27 | 2018-04-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1138 St. Louis Pl. NE - Atlanta | 50 | Fax sent 2018-04-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/28/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-04 | 2017-12-04 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 6917 Biscayne Blvd., Rex Manhole: 2200699 | 7200 | Fax received on 12/05/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/5/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-06 | 0 | 1 | 1 | 0 | 0 | 0 | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2017-10-18 | 2017-10-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2015 Detroit Ave. NW - ATL | 1090 | Email sent 2017-10-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 10/19/2017 12:00:00 AM |  | 10/18/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-12 | 2017-07-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1622 Wellswood Dr. SE - ATL | 3340 | Fax received 2017-07-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/13/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-02 | 2015-01-02 | Cobb County MS4 | Cobb |  | 1936 Wicksridge Lane | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Wicks Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of gravel in sewer main causing the manhole to overflow into a tributary of Wicks Lake. | The spill was stopped at 1:18 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 644 Wesley Dr. NW - ATL | 149128 | Fax received 2017-04-06. Update received 2017-04-010. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM | 2017-04-12 | 2018-04-27 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 1 | 1 | 0
2018-05-31 | 2018-05-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1725 Bolton Rd. NW - Atlanta | 2550 | Fax sent 2018-06-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 6/1/2018 12:00:00 AM |  | 5/31/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause unknown | Crew made mechanical repairs to the by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-20 | 2017-04-20 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 1245 Parkmont Drive | 3400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Big Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Spilled stopped | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-19 | 2017-10-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2568 Echo Drive, Atlanta | 10 | Notification received on October 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh |  | 10/19/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fallen tree limb causing a 4-inch sewer lateral broken. | The problem was corrected at 14:45 hours when the first responder crew replaced and upsized the 4-inch to a 6-inch sewer lateral, made the connection to the 8-inch sewer crossing, and restored normal flow. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-28 | 2016-06-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8329 Magnolia Drive, Jonesboro Manhole 2211197 | 54000 | Telephone call received on 06/28/2016. Fax received on 06/29/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 6/28/2016 12:00:00 AM | Flint |  | 2016-06-29 |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Sudden intense rain event caused the gravity lines to surcharge and the construction bypass pumps could not keep up with additional flow causing the discharge. | Lines upstream of the discharge site will be inspected by Clayton County crews to determine possible locations of inflow. Any problems located will be repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-08 | 0 | 1 | 1 | 1 | 0 | 0 |  |  |  |  | Jennifer Brandon | 770-302-3462 | CLAYTON COUNTY WATER AUTHORITY
2017-07-23 | 2017-09-07 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Under sidewalk across from 2449 Towne Lake Parkway across the street from the Towne Lake Square Shopping Center | 19576 | Pumps shut off when hole developed due to drop in pressure at pump station | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/23/2017 12:00:00 AM | Coosa |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 2 inch hole developed on the 12 inch force main line at the air valve | Construction switched over to 8 inch force main on July 23, 2017 until construction fixed the air valve on July 24, 2017 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 3134 Brians Creek Drive | 5833 | This spill is a result of Hurricane Irma. | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Power failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 9/12/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Snapping Shoals Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of Electrical Power | Restored Power and stopped the spill | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-27 | 2016-06-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1770 Richmond Avenue, SE | 1280 | fax received 6/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/28/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-09-16 | 2018-09-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 990 Redan Trace Stone Mountain GA 30088 | 335 | manhole 16-034-s037 | Raw Sewage |  | GA0024147 |  | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 9/17/2018 8:06:00 AM | Ocmulgee |  |  |  | 1 | Barbashela Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-29 | 2017-09-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2164 Faulkner Rd. NE - ATL | 4085 | Fax sent 2017-09-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/30/2017 12:00:00 AM |  | 9/30/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a bypass pump to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-12 | 2017-02-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 4000 | Fax received 2017-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Paul Moisan | 2/13/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | Crew repaired the by-pass pump hose to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Donalsonville, City of (Donalsonville WPCP) | Seminole | Donalsonville | The effected manholes were located at Plain and Tennille Street, Tennille and Second Street, and Newcombe Avenue. | 9309 | Mr. Davis called on 4/4/2016 at 08:45 to report that 3 manholes associated with the city's sewerage collection system started overflowing between 16:30 and 16:40 on April 1st. 2016 and stopped sometime between 09:45 and 10:00 on April 2nd 2016. | Raw Sewage | Southwest District | GA0026123 | WWTP | Storm Drain | N/A | Wet weather |  | Jay Howell | Linda Stevens | Jay Howell | 4/4/2016 8:45:00 AM | Flint | 4/2/2016 12:00:00 AM |  |  | 1 | Fish Pond Drain | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The facility received between 5" and 8" of heavy rainfall within the past twenty-four (24) hours leading up to this event, which caused a surge of inflow and infiltration of ground and surface waters within the collection system. | The city will The city is making every effort to eliminate the problem of infiltration and inflow. They have implemented a video program and other methods of locating and repairing sections of the collection system where significant infiltration is occurring. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-05-27 | 1 | 1 | 0 | 0 | 0 | 1 | Kevin Davis |  | City of Donalsonville WPCP
2016-08-28 | 2016-08-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4047 Lindsey Drive, Decatur | 2000 | Notification received on August 31, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 8/29/2016 12:00:00 AM |  |  |  |  | 0 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The spill was contained at 18:24 hours when a crew pressure washed the 8" main 150ft to remove the root blockage at 51ft, which then restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-01 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-06 | 2017-04-06 | Temple, City of (Temple WPCP) | Carroll | Temple | Center Point Road, Temple | 36000 |  | Raw Sewage | Wastewater Regulatory Program | GAJ020134 | WWTP | Stream |  | Natural Disaster |  |  | Hsin Yeh | Hsin Yeh | 4/10/2017 12:00:00 AM |  |  |  |  | 0 | Morgan Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wind and lighting knocking out the lift station. | Call contractor and repair the pump. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-22 | 2015-10-22 | Paulding County (Coppermine Road WPCP) | Paulding |  | Hooters outfall line/Highway 278 Hiram | 1500 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 10/23/2015 12:00:00 AM | Coosa |  |  |  | 0 | Branch of Rakestraw Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/Grease | Jetted/Cleared line of blockage | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey | 770-655-8342 | PAULDING COUNTY - COPPERMINE WRF
2016-12-31 | 2016-12-31 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3441 Comet Circle, Decatur | 5035 | Notification received on January 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh |  | 12/31/2016 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:57 hours, when a crew pressure washed the 8" sewer main 42ft, clearing the grease blockage ata 6ft and restoring normal flow. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-18 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-17 | 2017-03-17 | Cobb County MS4 | Cobb |  | 4475 Beech Haven Trl/ Cumberland Pkwy | 230 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 10 inch Clay Main | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-04 | 2017-01-04 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 1383 Cambridge Drive | 8640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/24/2017 12:00:00 AM | Ocmulgee | 1/3/2017 12:00:00 AM |  |  | 0 | Big Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage release occurred due to inflow and infiltration. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-21 | 2015-11-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1331 Memorial Drive, SE | 600 | fax received 11/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/22/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-20 | 2018-05-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 6943 Nottingham Road, Jonesboro | 3850 | Fax received on 05/20/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 5/20/2018 12:00:00 AM |  |  |  |  | 0 | Jester Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-21 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-07 | 2015-08-07 |  | DeKalb | Dunwoody | 1506 Rochelle Drive, Dunwoody | 100 | Notification received on August 10, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/7/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | A temporary repair was made by using hydraulic concrete to seal the hole at the creek crossing bank and restored regular services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-31 | 2018-01-31 | Forsyth County (Fowler & Shakerag WRF) | Forsyth |  | 405 Peachtree Pkwy. | 1500 | Email sent 2018-01-31 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 1/31/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease from outlet stores | Vac'ed to stop overflow, then jetted blockage and limed area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-24 | 2016-01-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | Verbal notification received 1/25/2016 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outfall spill due to TSS violation: Reported Daily TSS = 59 mg/L. Volume = 48,780,000 gallons |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-19 | 2015-11-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1576 Nantahalla Court, Atlanta | 5 | Notification received on November 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/19/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek crossing leaking | The problem was corrected at 13:47 hours when a crew placed a five gallon bucket under the 8" aerial crossing to contain the spill, called in a repair request and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-07 | Rochelle, City of (Northwest WPCP) | Wilcox | Rochelle | Manhole in roadway adjacent to the Sook Road Lift Station in Rochelle, GA. | 8624 | Received written documentation stating the local health dept and Cordele Dispatch were notified on January 5, 2015. | Raw Sewage | Southwest District | GA0024244 | Collection System | Ground, Stream | Ditch | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 1/5/2015 10:26:00 AM | Suwannee |  |  |  | 1 | Mill Creek tributary | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Apparent inflow and infiltrations issues within City's Sanitary Sewerage Collection System. Received heavy rainfalls in area prior to spill event. | Implementing Public Notification reporting requirements as required by Part II.A.11. of the Permit. In addition, facility is currently in the process of upgrading the collection system within the effected area and installing a new lift station. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-01-06 | 1 | 1 | 0 | 0 | 0 | 0
2018-01-28 | 2018-01-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 9600 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/29/2018 8:12:00 AM | Ocmulgee |  |  |  | 1 | South River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event and heavy infiltration caused vault 30-5012 to spill into South River | Check vault when storm event was over to find sewer succeeded and spill stopped |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-29 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-29 | 2016-02-29 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 3979 Woodward Mill Road | 6861 | EPD notification received 2/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/29/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Place signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-02-03 | 2016-02-03 | Tifton, City of (New River WPCP) | Tift | Tifton | manhole located at 1439 Sutton Circle, Tifton, GA | 1000 | Voice mail received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | New River Basin | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | Mitigated by removing debris and washing down the road. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-29 | 2017-08-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2364 Lilia Cir. SW - ATL | 350 | Fax sent 2017-08-31; received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/31/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Tifton, City of (New River WPCP) | Tift | Tifton | 26th and Ridge Ave. Lift Station, Tifton | 100 | Emails received on 01/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Pump Station | Stream | Shoreline | Power failure |  |  |  | Paul Moisan | 1/20/2017 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The pump motor shorted out at the lift station, and that knocked out the transformer that supplied the lift station power. | Power was restored, and the lift station restarted. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-03-02 | 0 | 1 | 0 | 0 | 0 | 0 | Andrew Marzen | 229-392-0660 | ESG Operations, Inc.
2017-09-25 | 2017-09-25 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 471 East Campbellton Street, Fairburn | 9021 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/25/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Whitewater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4" diameter oak tree fell on and broke an 8" diamter aerial crossing, gravity sewer main. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-18 | 2016-11-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Woods St., NW, ATL | 103 | Fax received on 11/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 11/19/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. Dry Land Spill. | A temporary repair was made to the by-pass pump, and it was placed on a periodic inspection schedule. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-25 | 2016-01-25 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Yellow Jacket Pumping Station, LaGrange. | 75600 | Fax received 01/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Pump Station | Reservoir |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 1/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | West Point Lake | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | RTU failed/all pumps tripped out due to overheating as pumps did not shut off when wet well was pumped dry. Possible glitch in PLC program. | Overflow stopped after pumps were started back up by WPC maintenance personnel. Cause of RTU failure investigated by city forces. Reason for pumps tripping out also being investigated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-11-10 | 2017-11-10 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 1128 Forest Vale Lane - Norcross | 5719 | Fax sent 2017-11-10 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 11/10/2017 12:00:00 AM |  | 11/10/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Rakes area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Vidalia (South WPCP) | Toombs | Vidalia | 468 Hugh Taylor Road, Vidalia, Georgia 30475 | 460000 | Memo received by the EPD office on September 14, 2017 from Robbie Akins states that they have begun the process of public notifications. | Raw Sewage | Coastal District | GAJ020100 | Lift Station | Stream | Stream | Natural Disaster |  | Bill Hawthorne | Brett Berry | Brett Berry | 9/12/2017 12:00:00 AM | Altamaha | 9/15/2017 12:00:00 AM | 2017-09-15 | 2018-09-15 | 1 | Rocky Creek | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Lift station power outage caused by Hurricane Irma. | N/A | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-19 | 1 | 0 | 0 | 0 | 0 | 1
2015-12-17 | 2015-12-17 |  | Brooks | Quitman | West Battle St. and South Walker St. | 1500 |  | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Ditch |  | Power failure |  |  | Dagny Pariani |  | 12/17/2015 12:00:00 AM | Suwannee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station power failure during rain event. | Reset power. Electrical company scheduled to check panel. Cleaned and limed area. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-16 | 2018-05-16 | Cobb County Water System | Cobb |  | 489 Hawkins Store Rd/Noonday Park | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Stopped spill and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-13 | 2015-12-13 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 3312 Country Club Apartments | 2540 | fax received 12/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/13/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Shot line with Hydro Jet and restored flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-02-09 | 2018-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3032 Wanda Cir. SW - ATL | 40 | Fax sent 2018-02-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 2/10/2018 12:00:00 AM |  | 2/9/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the main line | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-04 | 2018-08-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2098 Campbellton Rd. SW - Atlanta | 50 | Fax sent 2018-08-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Operator error |  |  | Alys Hannum | Alys Hannum | 8/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was caused by city crew jet rodding the service lateral. | Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-14 | 2017-04-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3360 Mountain Drive, Decautur | 45675 | Notification received on April 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/14/2017 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected on April 14, 2017 at 05:10 hours when a crew built a berm around the cracked joint, contain the spill and perform an emergency point repair on the 12" sewer main to restore normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-15 | 2017-05-15 | Cobb County Water System | Cobb |  | 32 Sheraton Way | 510 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Milan Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crews stopped the spill at 1224. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2351 Adams Dr. NW - ATL | 9925 | Fax sent 2018-02-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 2/5/2018 12:00:00 AM |  | 2/4/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain-induced | Unknown |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-27 | 2016-03-28 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 0 | Initial call 3/29, full report received 3/31 | Treated Effluent | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Hydraulic Overload |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 3/29/2016 12:00:00 AM | Ochlockonee | 3/28/2016 12:00:00 AM | 2016-03-28 |  | 1 | Parker's Mill Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Spill of partially treated effluent due to extremely wet weather. Flow volume = 36,000 gals. Flow, Weekly Average (MGD): permit = 3.75, reported = 5.39 |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-30 | 0 | 1 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025
2015-04-14 | 2015-04-14 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 8 Peachtree Battle Avenue, NW | 1730 | fax received 4/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/15/2014 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-16 | 2018-03-16 | Fulton County (Big Creek WPCP) | Fulton | College Park | 2819 Windsor Forrest Ct. College Park, GA 30349 | 12400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Re-flush sewer line using grease control. Apply enzymes and lime to affected area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-19 | 2017-12-19 | Cobb County Water System | Cobb |  | 2395 New Macland Rd. | 460 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud and Nose Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Crews stopped the spill and spread lime and cleaned the area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur GA 30032 | 16000 | Complaint ID 85246 reported that 16,000 gallons have initially been estimated | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/4/2018 6:35:00 PM | Ocmulgee | 2/4/2018 12:00:00 AM |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Rain induced event | Wait for rain event to end to stop manhole 15-184-s004 from spilling |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-31 | 2018-01-31 | Clayton County (Northeast WPCP) | Clayton | Forest Park | 1375 Rock Cut Road - Forest Park | 3000 | Fax sent 2018-02-01 | Raw Sewage |  | GA0020575 | Collection System | Stream |  | Grease |  |  |  | Paul Moisan | 2/1/2018 12:00:00 AM |  |  |  |  | 1 | Conley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Line will be televised and de-greaser applied. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2018-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-24 | 2017-08-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill St. NW - ATL | 6860 | Fax received 2017-08-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/25/2017 12:00:00 AM |  | 8/24/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-30 | 2018-04-30 | Jackson, City of (Yellow Water Creek WPCP) | Butts | Jackson | Jackson Square Lift Station | 0 | Email sent 2018-05-01 | Raw Sewage | Wastewater Regulatory Program | GA0021831 | Pump Station | Ground |  | Rags |  |  | Alys Hannum | Alys Hannum | 5/1/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags got caught in pump. | Pumps were removed and cleaned. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-03 | 2015-06-03 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 7/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the TSS effluent to rise to 31.0 mg/L on 06/01/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6023 Landover Circle, Marrow | 4980 | Fax received on 3/14/2018. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Paul Moisan | 3/14/2018 12:00:00 AM |  |  |  |  | 1 | Tar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure | Performed a point repair on the collapsed section of pipe. Work orders generated for any further work that might be needed in the future. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-14 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 |  | Barrow | Winder | Glenwood Pump Station | 6750 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Storm Drain |  | Power failure |  |  | Kim Hembree | Kim Hembree | 2/17/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Beech Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An ice storm downed trees which resulted in power failure to the pump station. | Bypass pump installed. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER
2015-09-16 | 2015-09-16 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Land adjecent to 515 Grant Street, Clarkesville | 720 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Other |  | Brian Koehler | Kathy Lewis | Brian Koehler | 9/16/2015 12:00:00 AM | Chattahoochee |  | 2015-09-22 |  | 0 | Rocky Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fell and broke the creek crossing | We are going to case this line incase this were to happen again | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | Jeremy Garmon | 706-754-5075 | City of Clarkesville
2015-04-20 | 2015-04-20 |  | DeKalb | Brookhaven | 3892 Buford Hwy, Brookhaven | 1340 | Notification received on April 27, 2015. | Raw Sewage | Wastewater Regulatory Program |  |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/20/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:40 hours when a crew rodded and pressure washed the 8" sewer main upstream 400ft, cleared the grease blockage, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-06 | 2017-11-07 | Marietta (City of)- Sewers | Cobb | marietta | 20 Northcutt St. | 8350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/7/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Ward Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A root blockage caused a sewer main to back up and leak into a creek culvert running under the roadway at this location. | Marietta Water personnel were able to relieve the blockage by hydrojetting the sewer main. Surrounding lines are being cleaned and examined by CCTV to assess the root intrusion and make sure all have been removed. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-19 | 2015-01-19 | Cobb County MS4 | Cobb |  | 1841 Silver Leaf Court | 540 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Olley Creek. | The Water System was notified at 7:15 a.m. and the flow was stopped at 11:45 a.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 600 Block of Scott Drive | 167475 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-09-11 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | 3rd Ave/ Andrews Street Lift Station in McRae-Helena | 5000 | Isolated spill. | Raw Sewage | Southwest District | GA0048674 | Lift Station |  |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma | Dirt was placed around lift station to control spill. Contents were help in place within a few feet of the lift station and were returned to manhole when power resumed. Area was cleaned and lime applied liberally. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2016-09-14 | 2016-09-14 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Deadend of Jackson Springs Road West, Macon GM ID 76031 | 2280 | Email received on 09/16/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 9/16/2016 12:00:00 AM | Upper Ocmulgee | 9/15/2016 12:00:00 AM |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sewer main. | The repair was made, and debris was removed and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-09-19 | 0 | 1 | 0 | 0 | 0 | 0 | Heather Veal |  | MACON WATER AUTHORITY
2017-05-23 | 2017-05-23 | Fayetteville, City of (Fayetteville WPCP) | Fayette | Fayetteville | Heritage Lake Subdivision, Fayetteville | 7500 |  | Raw Sewage | Wastewater Regulatory Program | GA0035807 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/23/2017 12:00:00 AM |  |  |  |  | 0 | Gingercake Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Jet line and cleaned |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-29 | 2015-07-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 999 Braemar Avenue SW | 890 | fax received 7/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/30/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-28 | 2015-02-28 | Cobb County MS4 | Cobb |  | 2332 Milstead Cir NE | 310 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/28/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morgan Farm Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" ductile iron main | The crews stopped the spill at 19:15 Hrs. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-13 | 2018-04-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3135 Rilman Rd. NW - Atlanta | 1320 | Fax sent 2018-04-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/14/2018 12:00:00 AM |  | 4/13/2018 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Creek crossing at Waldrop Ave. | 3600 |  | Raw Sewage | Coastal District | GA0024431 | Collection System |  | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/2/2016 10:30:00 AM | Satilla | 4/2/2016 12:00:00 AM |  |  | 1 | Unnamed Tributary to Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was caused by I&I during a heavy rain event | Spill subsided by 6:00 PM when flow returned closer to normal. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-04-07 | 1 | 1 | 0 | 0 | 0 | 0
2018-07-19 | 2018-07-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1735 Bolton Rd. NW - Atlanta UPDATE- PRIVATE | 100 | Fax/email sent 2018-07-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | UPDATE- PRIVATE Pump failure | UPDATE- PRIVATE Crew made mechanical repairs to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-16 | 2018-04-16 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | Near 3580 Corporate Drive at a Dalton Utilities lift station. | 1200 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Contractor |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/17/2018 12:00:00 AM | Coosa |  |  |  | 1 | Tributary of Swamp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor working on behalf of Dalton Utilities hit an unmarked 2" force main while excavation was being performed. Line was not known to exist. | Dalton Utilities excavated a retention pond on-site to capture wastewater. 1200 gallons was released before Dalton Utilities could get a portable pump to pump remainder back into lift station. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-24 | 1 | 0 | 0 | 0 | 0 | 0
2015-06-01 | 2015-06-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 675 Hutchens Road, SE | 10 | fax recievd 6/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/2/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-22 | 2017-10-22 | Cobb County Water System | Cobb |  | 3720 Austell Road | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 9:46 p.m. and our crew stopped the overflow at 11:38 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-07 | 2018-05-07 | Rome, City of (Rome WRF) | Floyd |  | Directly behind 18 Westwood Circle | 300 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 5/8/2018 12:00:00 AM | Coosa |  |  |  | 1 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and rags in the sewer main | Sewer main was thoroughly cleaned. Spill site was cleaned and lime applied. Sewage was vacuumed out of the unnamed tributary as much as possible. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-10 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8890 Roberts Road, Jonesboro MH 2216314 | 4125 | Telephone call received on 02/04/2016; fax received on 02/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Capacity during rainfall event. | Area was cleaned and signs posted. Sanitary sewer tangents upstream will be inspected for signs of inflow and infiltration, and repairs will be performed if needed. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 |  | DeKalb | Chamblee | 5260 Peachtree Industrial Boulevard, Chamblee | 17930 | Notification received on February 29, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/27/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Crek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken joint | The problem was corrected at 15:13 hours, when a crew built a berm around the broken 12" main to contain the spill, restored normal flow until the repair is made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-29 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 4000 Henderson Park Road, Tucker | 1250 | Notification received on April 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/27/2017 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 8:30 hours when a crew rodded between manholes 60ft, cleared the blockage at 3ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-05 | 2016-04-05 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | 313 East Griffin Street | 1200 |  | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Rags |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 4/6/2016 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags | Jetted line, flushed main | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-14 | 2016-10-14 | Savannah, City of (President Street WRF) | Chatham | Savannah | West Gwinnett St., Savannah, GA | 85 |  | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Natural Disaster |  |  | Dagny Pariani |  | 10/14/2016 12:00:00 AM | Savannah | 10/14/2016 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flood waters from Hurricane Matthew undermined sewer manhole. | Plugged the main and set up bypass. Contractor will repair manhole. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-14 | 2016-10-14 | Savannah, City of (President Street WRF) | Chatham | Savannah | West Gwinnett St., Savannah, GA | 85 |  | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Natural Disaster |  |  | Dagny Pariani |  | 10/14/2016 12:00:00 AM | Savannah | 10/14/2016 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flood waters from Hurricane Matthew undermined sewer manhole. | Plugged the main and set up bypass. Contractor will repair manhole. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 | Cobb County MS4 | Cobb |  | 4255 Eade Green Rd. | 830 |  | Raw Sewage | Wastewater Regulatory Program |  |  | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/17/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Lake Legency | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8 in Ductile Iron Main | Cleaned and spread lime at spill area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-09 | 2016-02-09 | Savannah, City of (Travis Field WPCP) | Chatham | Savannah | Mikell Avenue– east – Dean Forest Road | 1200 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Other |  | Steve Fox | Steve Fox | Steve Fox | 2/9/2016 12:00:00 AM | Savannah | 2/10/2016 12:00:00 AM |  |  | 1 | Pipemakers Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Directional Drilling contractor bored into sewer force main | Lift Station was shut off and flow in ditch was contained. A by-pass pump was set up which pumped the storm and sewage mix back into City Sewer Collection System. Force main was repaired by City staff and contractor. Spill site was cleaned and mitigated and the force main will be located and marked. Notifications were placed at the spill site, at Pipe-maker’s Canal and at Pipe-maker’s Canal at State Route 21. All agencies (i.e. Health Department, State EPD, and the City of Savannah Public Information Office (who will issue the Public News Release)) were notified as required by State Guidelines. Spill Notifications were placed at spill site and on Pipe-Maker’s Canal | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-02-17 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2335 Adams Drive, NW. | 4500 | fax received 2/04/2016. COA Service Request No. 7518899 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-21 | 2015-10-21 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 11/9/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 34.6 mg/L on 10/21/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-16 | 2017-11-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | S Inner Loop Rd. SW - ATL | 2500 | Fax sent 2017-11-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Pump Station | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 11/16/2017 12:00:00 AM |  | 11/16/2017 12:00:00 AM |  |  | 1 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A malfunction at the Flint River pumping station caused the mainline to back up onto Hartsfield-Jackson airport property. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-07 | 2017-12-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3880 Oakcliff Industrial Court, Doraville, GA 30340 | 50 | Manhole 18-316-s024 4 postings | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Contractor |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/7/2017 7:29:00 PM | Ocmulgee | 12/7/2017 12:00:00 AM |  |  | 1 | N. Fork Peachtree creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractors are relaying sewer main. The man hole with the plug caused the manhole to spill into the creek. | Contractor removed the plug and the manhole stop overflowing. |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-08 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Brandon Hollingsworth |  | Dekalb County Department of Watershed Management
2017-03-05 | 2017-03-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2598 Lake Erin Drive, Tucker | 4600 | Notification received on March 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/5/2017 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:24 hours when a crew rodded the 8" sewer main downstream 75ft, removed the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-17 | 2017-04-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1235 Chattahoochee Ave. NW - ATL | 3350 | Fax received 2017-04-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/18/2017 12:00:00 AM |  | 4/17/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill at |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-30 | 2017-01-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Lovejoy | 11590 SLR Blvd, Lovejoy Manhole 2217393 | 7200 | Fax received on 01/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Vandalism |  |  | Paul Moisan | Paul Moisan | 1/31/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the blockage was vandalism | Blockage was cleared and the flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1454 Cherokee @ Poplar, Columbus | 35819 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-01-26 | 2016-01-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 555 8th Street, NW | 50 | fax received 1/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/27/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-18 | 2016-07-18 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 3200 Lake Colony Drive | 2487 | fax recieved 7/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/19/2016 12:00:00 AM |  |  |  |  | 1 | Tributary of Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-12-24 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | verbal and electronic notification received 12/29/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/29/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill due to high TSS. Date sample taken: 12/25/2015. Reported TSS = 50 mg/l; Permit Limit = 15 mg/L/ Flow volume = 182.19 MG, entire day (12am – 12am). |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-11 | 2016-03-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2833 Glenlocke Circle, NW | 640 | fax received 3/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/12/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-22 | 2016-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 154000 | Email notification received 1/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/22/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-30 | 2015-11-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 311 Scott Street, SW | 2106 | fax received 12/01/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/1/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-15 | 2017-05-15 | Emerson, City of (Henry Jordan WPCP) | Bartow |  | 280 Allatoona Dam Road Cartersville Lift Station 1 | 5000 | Did not reach state waters | Raw Sewage | Mountain District - Cartersville | GA0026115 | WWTP | Stream |  | Equipment failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 5/16/2017 12:00:00 AM | Coosa |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Level float failure | Inspection, Cleaning | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-24 | 2017-05-24 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3067 Wheeler Rd. Dr. - Augusta | 900 | Email received 2017-05-25 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/25/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Debris. | Sewer gravity main was augered to open the line. Will be videoed to assess pipe structure. Lime will be spread in the area after the rain stops. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-21 | 2016-03-23 | Thomaston, City of | Upson | Thomaston | 801 W. Gordon Street | 300 | The spill was contained and did not appear to have reached surface waters. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Other |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/21/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was due to an air filter fault which caused the pump to shut down until thewarning was physically acknowledged. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 |  | Chatham | Savannah | 3 Waite Dr., Savannah, GA | 2000 | Initial notification via CTS on 9/12/17. Follow up phone call and email on 9/15/17. | Raw Sewage | Coastal District |  | Collection System | Ground, Storm Drain, Stream | Ditch | Debris |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/12/2017 12:00:00 AM | Savannah | 9/12/2017 12:00:00 AM |  |  | 1 | Herb Creek | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in sewer line caused by collapsed, paved over manhole. | Jetted and cleaned several manholes and connecting sewer pipes. Ongoing rehab/replacement of collapsed manhole occurring. Restricted access to affected area, cleaned and spread lime. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-09-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Water Utility Management | 912-352-9339
2017-08-09 | 2017-08-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2804 Millwood Way, Decatur | 26550 | Notification received on August 14, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 8/9/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 10:44 hours when the storm event subsided and the flow return to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-04 | 2017-01-06 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 25000 | Stream monitoring ceased after 3rd month and initiated under the 2/28/17 - 3/1/17 major spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP |  | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/13/2017 12:00:00 AM | Savannah |  | 2017-01-09 | 2017-03-29 | 1 | Tributary to Chandler's Branch | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. | Stream monitoring initiated. Public notification posted at City Hall. Notification to the Burke Co. Health Department; and notification was published in the Burke County True Citizen newspaper in the January 18, 2017 edition. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2017-01-19 | 1 | 1 | 0 | 1 | 1 | 0 | Jon Tindall | 912-449-0999 | Tindall Enterprises, Inc.
2016-07-27 | 2016-07-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 3200 Lake Colony Drive | 2758 | fax received 7/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/27/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and flushables | Removed all deposited solids; placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-10-08 | 2015-10-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 1130 | fax received 10/09/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/9/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-14 | 2016-11-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1488 Metropolitan Pkwy, SW, Atlanta | 17030 | Fax received on 11/16/2016. Correction to the spill that occurred on 11/14/2016 - The correct address should be 1488 Metropolitan Pkwy, SW; a point repair was made to contain the spill at 4:30 p.m. on 11/15/2016; and the cause of the spill was a collapsed mainline. The estimate of spillage is 17,030 gallons.. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 11/16/2016 12:00:00 AM |  |  | 2016-11-15 | 2017-12-05 | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed mainline. | The crew made a repair to the collapsed mainline. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 1 | 0 | 1 | 1 | 0
2016-01-27 | 2016-01-27 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 4687 Columbia Road | 1000 | fax received 1/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Operator error |  |  | Kim Hembree | Kim Hembree | 1/28/2016 12:00:00 AM |  |  |  |  | 1 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Stream bank erosion | replaced pipe, restored creek bank |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2016-12-08 | 2016-12-13 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd. | 350000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2016 12:00:00 AM | Ocmulgee |  | 2016-12-08 |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 7.5 inches of rainfall in a 24 hour period. | The facility were able to get the spill stopped. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-29 | 2018-05-29 | Norman Park (Norman Park WPCP) | Colquitt | Norman Park | Manhole outside WPCP and discharge from permitted outfall bulking solids into Reedy Creek per operator. | 0 | Manhole overflow likely in excess of 10,000 gallons and treated as a major spill by operator. | Primary Effuent | Southwest District | GA0033600 | WWTP | Stream | Stream | Hydraulic Overload |  | Jay Howell | Jay Howell | Jenna Detar | 7/17/2018 4:00:00 PM | Suwannee | 5/29/2018 12:00:00 AM | 2018-05-29 |  | 1 | Reedy Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  | 0 | Rising sludge blanket in secondary clarifier discharged from the WPCP due to hydraulic overload. A manhole next to the WPCP also overflowed (untreated effluent).Caused by inflow and infiltration in the sewer collection system and hydraulic overload in the WPCP; resulting from heavy rainfall from Subtropical Storm Alberto. | City is working with engineer to address I & I. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2018-07-17 | 1 | 1 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2556 Defoors Ferry Rd. NW - ATL | 1520 | Email received 2017-06-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  | 6/20/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-28 | 2015-04-28 | Thomasville, City of (Oquina Creek WPCP) | Thomas | Thomasville | 15000 Block of US 19 South | 10000 | REC CALL 4/29/2015. REC EMAIL 4/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024082 | Collection System | Stream | Stream | Debris |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/29/2015 12:00:00 AM | Ochlockonee | 4/29/2015 12:00:00 AM |  |  | 1 | branch to Good Water Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags | Remove blockage and cleaned site | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF THOMASVILLE | 229-227-3275
2015-09-02 | 2015-09-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 672 Quaker Street, SW | 100 | This is a spill from a private lateral. This spill does not belong to the City of Atlanta | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Kim Hembree | Kim Hembree | 10/23/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-11 | 2016-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3136 Martin L. King Jr. Drive, SW | 10350 | fax received 1/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/12/2016 12:00:00 AM |  |  | 2016-01-12 | 2017-02-02 | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-13 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-10 | 2017-02-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1794 Alvarado Ter. SW - ATL | 50 | Fax received Saturday 2017-02-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/11/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Spill was self-contained. The process to clean and disinfect the site has been initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-09 | 2016-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1277 Niles Avenue, NW | 957 | fax received 2/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 2/10/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | The crew replaced the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-23 | 2017-02-23 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 3312 County Club Village Lane - Norcross | 4137 | Fax received 2017-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 2/23/2017 12:00:00 AM |  | 2/23/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Bromolow Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-24 | 2015-10-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 855 | fax received 10/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/24/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-12 | 2018-02-12 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 294 Hammond Drive Sandy Springs | 10800 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/12/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-12 | 2016-08-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1881 Myrtle Drive, SW | 960 | fax received 8/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/15/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-16 | 2016-09-16 |  | DeKalb | Brookhaven | 3946 Duncannon Court, Brookhaven | 1460 | Notification received on September 19, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/16/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected on September 16, 2016 at 12:11 hours when a crew made a temporary repair, built a dirt berm, installed a 6" PVC pipe with two Fernco couplings, disinfected the creek bank and called in a work order to make a permanent repair. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-04 | 2016-05-03 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2301 Old Salem Road (Old Salem Lift Station) | 22500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/4/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Sanpping Shoals Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease build up interfering with pump controls | Relocated level instrument, repaired air release valve. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Savannah, City of (President Street WRF) | Chatham | Savannah | 7100 block of Concord Rd., Savannah, GA | 6300 |  | Raw Sewage | Coastal District | GA0025348 | Force Main | Storm Drain, Stream | Stream | Contractor |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM | Savannah | 10/9/2016 12:00:00 AM |  |  | 1 | Betz Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Utility contractor damaged a buried force main while straightening a damaged utility pole. | Repaired force main. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-21 | 2016-03-21 | Cobb County Water System | Cobb |  | 240 The Bluffs NW | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in the 10 inch sewer main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-11 | 2017-02-11 | Cobb County Water System | Cobb |  | 54 Vinings Lake Drive | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-09 | 2018-03-09 | Columbus Water Works (South WRF) | Muscogee | Columbus | 5226 Grady Drive, Columbus | 1355 | Fax sent 3/10/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Paul Moisan | 3/10/2018 12:00:00 AM |  |  |  |  | 0 | Flatrock Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | An 8" sewer main broke due to bank erosion causing a discharge. The broken line was plugged and a pump around was initiated until repairs could be made. The basin is Flatrock Creek Basin. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-13 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-16 | 2016-03-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1990 Alison Court, SW | 255 | This is a private spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  |  |  |  | Kim Hembree | Kim Hembree | 4/12/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Private spill. | N/A. Private spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-06 | 2015-07-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1398 Boulevard Lorraine, SW | 865 | fax received 7/06/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/6/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-28 | 2015-04-28 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2950 Martin Luther King, Jr. Drive, SW | 1040 | fax received 4/29/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/28/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-07 |  | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo | 9000 | Dryland | Other | Wastewater Regulatory Program |  | Collection System |  |  | Wet weather |  | Alan Leake | Reginald Williamson | Reginald Williamson | 5/4/2017 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | heavy rains |  | 644f35d6-83cf-4c2c-b251-beda6cfdc258 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-24 | 2017-03-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1033 Hollywood Rd. NW - ATL | 50 | Fax received Saturday 2017-03-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 3/25/2017 12:00:00 AM |  | 3/24/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-12 | 2016-09-16 | Canton, City of (Canton WPCP) | Cherokee |  | Forcemain in the river bank downstream of the Canton WTP near Heritage Park | 37500 | Being handled by EECO | Raw Sewage | Mountain District - Cartersville | GA0025674 | WWTP | Stream | Stream | Pipe failure |  | Ebony Johnson | Kathy Lewis | Eric Dykes | 9/14/2016 12:00:00 AM | Coosa | 9/14/2016 12:00:00 AM | 2016-09-16 |  | 1 | Etowah River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken force main caused by flooding and erosion of the river bank |  | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 |  | Lowndes | Valdosta | 2426 Meadowbrooke | 45750 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-08-28 | 2017-08-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1044 Hubbard St. SW - ATL | 5 | Fax received 2017-08-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/29/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-07 | 2016-01-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1030 Beechcrest Road, SW | 300 | fax received 1/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/8/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-13 | 2016-03-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 801 Gresham Avenue, SE | 380 | fax received 3/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-09 | 2018-07-19 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Lift Station 4110 at 549 Harry Driggers Boulevard. | 100 |  | Raw Sewage | Coastal District | GA0025313 | Pump Station | Canal | Canal | Pipe failure |  | Bill Hawthorne |  | Bill Hawthorne | 7/10/2018 12:15:00 PM | Altamaha | 7/10/2018 12:00:00 AM |  |  | 1 | Altamaha Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by a by-pass hose failure which caused 400 gal. of sewage to flow on the ground and approx. 100 gal. spilled into the Altamaha Canal. No fish kill reported. | Incident Time Line: 7/9/2018 @ 4:45 pm Frank Clark was contacted by Thomas Grimes lift station crew member that a by-pass pump hose had broken and sewer was on the ground but that he had shut the pump off so the sewer had stopped spilling from the hose. The JWSC Sewer Collection System Crew were able to collect 400 gal. by use of a Vac-truck. A new by-pass hose was installed. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc |  | 2018-07-19 | 1 | 1 | 0 | 0 | 0 | 0
2017-11-06 | 2017-11-06 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 228 East Midlake Parkway - Swainsboro | 300 | Call received 2017-11-06 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Pump Station | Ground |  | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 11/6/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power loss at the lift station caused a backup. | Power was restored. Solids removed and area limed. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-11 | 2016-12-11 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6744 Standing Boy Road, Columbus | 73 | Call received on 12/11/2016; Fax received on 12/12/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System |  |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/12/2016 12:00:00 AM |  |  |  |  | 1 | Standing Boy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. | Once the debris was cleared from the main, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornet |  | COLUMBUS WATER WORKS
2015-05-14 | 2015-05-14 |  | Forsyth | Cumming | 2274 Chamblee Gap Road | 1500 | verbal and fax notification received 5/14/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/14/2015 12:00:00 AM |  |  |  |  | 1 | Cheatham Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flush-able wipes | The blockage was jetted and the line was cleared. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CUMMING
2017-11-22 | 2017-11-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3557 Waldrop Trail, Decatur GA 30034 | 3380 | Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | N/A | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/22/2017 2:35:00 PM | Ocmulgee |  |  |  | 1 | South River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole 15-071-s015 spilling into n-named tributary to the South River | Pressure washed 100ft and cleared grease blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-27 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Sylvester West |  | Dekalb Co Dept. Watershed Management
2017-04-12 | 2017-04-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton |  | 1263 Richland Rd. SW - ATL | 8080 | Fax received 2017-04-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/13/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-17 |  |  | Cobb |  | 70 Rhodes Dr. | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  |  |  | Reginald Williamson | 12/17/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" Main | Limed Area |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-20 | 2018-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2392 Pryor Rd. SW - ATL | 1935 | Fax sent 2017-01-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-02 | 2017-03-02 | Cobb County Water System | Cobb |  | 391 Pine Valley Rd | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-10 | 2018-01-10 | Columbia County (Crawford Creek WPCP) | Columbia | Grovetown | 700 Horizon South Parkway - Grovetown | 840 | Fax sent 2018-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Debris |  |  |  | Alys Hannum | 1/10/2018 12:00:00 AM |  |  |  |  | 1 | Millbranch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Dirt and debris | Unstopped sewer main with high pressure jet machine. Vacuumed. Spread lime. Planned follow up video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-20 | 2016-06-21 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 60000 | Stream monitoring ceased for the June 21st major effluent spill upon the facility initiating stream monitoring for the December 27th major spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 6/30/2016 12:00:00 AM | Savannah | 6/30/2016 12:00:00 AM | 2016-06-30 |  | 1 | Tributary to Chandler's Branch | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. | Stream monitoring initiated 6/30/16. Public notification posted at City Hall on 7/5/16 to 8/5/16. Notification to the Burke Co. Health Department completed on 7/5/16; and notification published in the True Citizen newspaper in the November 16, 2016 edition. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-10-26 | 1 | 1 | 0 | 1 | 0 | 0
2018-04-10 | 2018-04-10 | Newton County (Yellow River WPCP) | Newton | Covington | Turkey Creek Outfall - Covington | 540 | Email sent 2018-04-10 | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/10/2018 12:00:00 AM |  | 4/11/2018 12:00:00 AM |  |  | 1 | Turkey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Jetted lines to free blockage and removed debris. Lime spread on affected area. Signs will be posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-12 | 2015-05-12 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 196 Montgomery Ferry Drive, NE | 1170 | fax received 5/13/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/13/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 |  | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-10 | 2018-03-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 2523 Brittany Park Cove, Ellenwood GA 30294 | 5000 | Manhole 15-023-s011 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/11/2018 8:48:00 AM | Ocmulgee | 3/10/2018 12:00:00 AM |  |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rocks in invert | Rodded manhole |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-13 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-03 | 2018-05-03 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 1900 Buford Hwy - Duluth | 6248 | Fax sent 2018-05-03 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/3/2018 12:00:00 AM |  | 5/3/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Suwanee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products | Removed all deposited solids, placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-24 | 2017-10-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 675 Metropolitan Pkwy SW - ATL | 815 | Fax sent 2017-10-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/25/2017 12:00:00 AM |  | 10/24/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-08 | 2018-08-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4008 Princeton Lakes Way SW - Atlanta | 6180 | Fax sent 2018-08-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/9/2018 12:00:00 AM |  | 8/8/2018 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-17 |  |  | DeKalb |  | 4309 Memorial Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown cause, believed to be associated with work going on in area |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-07 | 2015-03-07 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1277 Niles Avenue, NW | 147 | fax received 3/08/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/7/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-14 | 2015-04-14 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2424 Grand Harbor Court | 475 | REC VOICE MAIL 4/15/2015. REC EMAIL 4/16/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain | Ditch | Equipment failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/16/2015 2:51:00 PM | Ocmulgee | 4/16/2015 12:00:00 AM |  |  | 1 | Lake Tobesofkee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was a busted hose on a by-pass pump. | Debris has been removed and the affected area is being disinfected with lime. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-16 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2017-09-11 | 2017-09-11 | Brunswick-Glynn County JWSC (Exit 29 WPCP) | Glynn |  | 106 Southwinds Drive - (Hurricane Irma) | 25 |  | Raw Sewage | Coastal District | GA0038938 | Collection System | Ditch | Ditch | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/19/2017 1:04:00 PM | Satilla | 9/11/2017 12:00:00 AM |  |  | 1 | Little Satilla River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewage in sinkhole in front yard. (Hurricane Irma) | Pipe repaired | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-27 | 1 | 1 | 0 | 0 | 0 | 0
2018-03-20 | 2018-03-20 | Rochelle, City of (Northwest WPCP) | Wilcox | Rochelle | Waste overflowed from the lift station onto the ground. No waste left the lift station property. | 360 | Public notice was posted at the lift station gate. | Raw Sewage | Southwest District | GA0024244 | Lift Station | Ground |  | Rags |  | Jay Howell | Jenna Detar | Jenna Detar | 3/20/2018 8:00:00 AM |  | 3/20/2018 12:00:00 AM |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pumps clogged from rags. waste did not leave lift station property. | Submersible pumps were pulled and cleared, pumper truck pumped out the wet-well. Sand bags were put down to contain the overflow and lime was applied to surrounding area to neutralize waste water. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2018-04-10 | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Chip Shaddix |  | CITY OF ROCHELLE-NORTHWEST WPCP
2016-08-05 | 2016-08-05 | Dekalb County (Snapfinger Creek WPCP) |  | Decatur | 4347 Flats Shoals Parkway, Decatur | 400 | Notification received on August 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Pipe failure |  |  | Hsin Yeh | Hsin Yeh | 8/5/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing sewer ling leaking | The problem was corrected at 14:06 hours when the crew used concrete to seal the leak and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-09 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Sweetgum Lane Lift Station in McRae-Helena | 200 | Isolated spill. | Raw Sewage | Southwest District | GA0048674 | Lift Station |  |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma. | Isolated spill and cleaned ares. Lime applied liberally. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2015-11-10 | 2015-11-11 | Cobb County Water System | Cobb |  | 3535 Clubland Drive | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  |  | Reginald Williamson | Reginald Williamson | 11/11/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-02 | 2016-10-02 | Cobb County Water System | Cobb |  | 2216 Wakita Drive | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-03 | 2015-12-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1053 Cascade Circle, SW | 100 | fax received 12/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/4/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-27 | 2015-02-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1776 Johnson Road, NW | 50 | fax received 2/28/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/27/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-15 | 2016-03-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2145 Lawrenceville Hwy, Decatur | 1920 | Notification received on March 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/17/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | The problem was corrected at 12:30 hours, when a crew pressure washed the sewer main 400ft upstream clearing the blockage at 275ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1280 Oakland Dr. SW - ATL (Spill #2) | 750 | Fax received 2017-04-26. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/27/2017 12:00:00 AM |  | 4/26/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-22 | 2018-02-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 380 Ardmore Cir. NW - ATL | 210 | Fax sent 2018-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/23/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-31 | 2016-01-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 187 Whiteford Avenue, SE | 3255 | fax received 2/01/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/1/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-06 | 2018-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1160 Peachtree Battle Ave. NW - ATL | 2900 | Fax sent 2018-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/7/2018 12:00:00 AM |  | 2/6/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | Crew used a hydraulic pressure cleaner and a mechanical rod to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-15 | 2018-07-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 395 Bishop St. NW - Atlanta | 7500 | Missed 24 hour notification; received 5 day notification in mail. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/25/2018 12:00:00 AM |  | 7/15/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew used a bypass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-27 | 2016-08-28 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn |  | Corner of 5514 Frederica Road and South Harrington Road, St. Simons Island. | 12000 |  | Raw Sewage | Coastal District | GA0021521 | Force Main | Ground, Storm Drain | Ditch | Equipment failure |  | Michelle Cortes | Bill Hawthorne | Bill Hawthorne | 8/28/2016 2:23:00 AM | Satilla | 8/28/2016 12:00:00 AM | 2016-08-29 |  | 1 | Tributary of Harrington Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 |  | 0 | 4" line air relief valve failure | Closed isolation valve to stop the spill. | db6b2c02-fb34-11e0-9fd5-12313b0cb679 | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-09-06 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Manhole No. 1134, near Ronthor Drive and Fairplay Drive | 39600 | fax received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 1 | Tributary of Mean's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain - 3.9" |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-04-01 | 2016-04-03 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | manhole near the Carlton Woods Lift Station, Moultrie | 486000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/1/2016 12:00:00 AM | Ochlockonee | 4/1/2016 12:00:00 AM | 2016-04-01 |  | 1 | Ochlockonee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Heavy rainfall caused an influx of inflow and infiltration to the collection system resulting in surcharging. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2016-06-28 | 2016-06-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 546 Maggie Lane, Jonesboro Manhole 2207387 | 72000 | Telephone call received on 06/28/2016. Fax received on 06/29/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 6/28/2016 12:00:00 AM | Flint |  | 2016-06-29 |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 0 | Heavy rain event caused the gravity lines to surcharge and the construction bypass pumps could not keep up with the additional flow causing the discharge. | Lines upstream of the discharge site will be inspected by Clayton County crews to determine possible locations of inflow. Any problems located will be repaired. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-08 | 0 | 1 | 1 | 0 | 0 | 0
2018-04-03 | 2018-04-03 | Hall County (Spout Springs WRF) | Hall | Flowery Branch | Just outside plant - location to follow | 7608 | Call received 2018-04-03; email sent 2018-04-03 | Raw Sewage | Wastewater Regulatory Program | GA0050214 | Force Main | Stream |  | 3rd party contractor |  |  |  | Alys Hannum | 4/3/2018 12:00:00 AM |  |  | 2018-04-03 |  | 1 | Lollis Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "...a result of a contractor hitting our forcemain." | " The damage was reported to us within minutes of it occurring and we quickly turned the pump station off to minimize the impact. Also, there was an empty storm water retention pond down grade of the leaking main that crews were able to divert the flow into. After the repair was completed the contractor hired septic haulers to vac out the storm water pond and is now stabilizing the area." |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-18 | 2017-05-18 | Cobb County Water System | Cobb |  | 2977 Cynthia ct. | 1840 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/18/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sewell Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Strural Failure of 8" Ductile iron creek crossing |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-27 | 2015-04-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 4900 | The crew used a hydraulic pressure cleaner to contain the spill. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/28/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-11 | 2015-08-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, N.W. | 1060 | Fax received on 08/12/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/12/2015 12:00:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Hydraulic pressure cleaner was used to contain spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-10 | 2016-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2730 Peyton Springs Circle, SW | 2191 | fax received 8/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 |  | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/11/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-07 | 2015-11-07 | Atlanta, City of (West Area CSO) | Fulton | Atlanta | West Area WQCF | 1720000 |  | Primary Effuent | Wastewater Regulatory Program | GA0038644 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/8/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-19 | 2015-07-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2914 3rd Avenue, SW | 144 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 7/20/2015 12:00:00 AM |  |  |  |  | 0 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-09 | 2016-10-09 | Richmond Hill, City of (Sterling Creek WRF) | Bryan | Richmond Hill |  | 2000 |  | Raw Sewage | Coastal District | GA0037648 | Collection System | Basin | Ditch | Power failure |  | Cliff Swiger | Cliff Swiger | Cliff Swiger | 10/9/2016 2:30:00 PM | Ogeechee | 10/9/2016 12:00:00 AM | 2016-10-09 |  | 0 | Ogeechee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Matthew caused power outage. |  | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-10 | 2015-12-10 | Cobb County MS4 | Cobb |  | 341 Huntsman Way | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in the sewer causing the manhole to overflow into a tributary of Sope creek | The overflow was stopped at 8:25 a.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 | Cobb County MS4 | Cobb |  | 4255 Wade Green Rd. | 660 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/17/2015 12:00:00 AM | Chattahoochee | 2/17/2015 12:00:00 AM |  |  | 0 | Lake Legency | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8 in Ductile Iron Main | Cleaned and spread lime at spill area | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 240 Flint River Road, Jonesboro MH# 2216228 | 99000 | Fax received on 02/08/2016; telephone call received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM | Flint |  |  |  | 1 | Kendrick Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | The cause of the overflow was capacity. | Multiple lines will be inspected for source of inflow and infiltration to solve capacity issues. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-08 | 0 | 1 | 1 | 0 | 0 | 0
2016-10-17 | 2016-10-17 | Marietta (City of)- Sewers | Cobb | Marietta | 851 Cannongate Xing | 2100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/17/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Ward Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-09 | 2017-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3596 N Stratford Rd. NE - ATL | 1065 | Fax sent 2017-10-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/10/2017 12:00:00 AM |  | 10/9/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-08 | 2015-10-08 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 4370 Satellite Blvd | 5400 | fax received 10/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 10/8/2015 12:00:00 AM |  |  |  |  | 1 | Bromolow Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed the main to restore the flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-03-02 | 2016-03-02 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2546 Sheraton | 3500 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-12-05 | 2017-12-05 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3022 Mistletoe Avenue - Augusta | 2756 | Email received 2017-12-06 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 12/6/2017 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The sanitary sewer main was jet washed to break up the grease in the line. The mainline was also sawed to cut the grease away from the pipe while the Vactor truck removed the floating grease from the downstream manhole. The area around the manhole was cleaned up and washed down. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-11 | 2018-02-12 | Adairsville, City of (North WPCP) | Bartow |  | 106 Cass Street | 155000 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Hydraulic Overload |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/12/2018 12:00:00 AM | Coosa |  |  |  | 0 | Oothkalooga Creek Tributary to the Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Major inflow and infiltration problems | Physically inspect every sewer manhole within the city sewer system and document the following conditions on the city's GIS sewer mapping software. Begin manhole surveys in the low lying areas. As defective manholes are found repair them. Compile an accurate sewer map accessible through the city's GIS. Continue with the flow monitoring effort to isolate the problem areas. When suspect sewer zones are identified, employ smoke testing to locate specific sources of inflow. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-24 | 2016-07-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 81 | fax received 7/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/25/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crews made repairs to the mainline to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-12 | 2015-06-12 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 551 Northport Parkway Savannah GA 31407 | 430 |  | Raw Sewage | Coastal District |  | WWTP | Other | Shoreline | Equipment failure |  | Cliff Swiger | Steve Fox | Steve Fox | 6/12/2015 12:00:00 AM | Savannah | 6/12/2015 12:00:00 AM |  |  | 1 | Savannah River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | y | 0 | Force main air release failure | Repaired air release valve. City staff will increase inspections and have put lime on the affected area. Spill notifications will be put at spill site and at Houlihan Bridge boat ramp. All entities (Georgia Environmental Protection Division, Health Dept. and City Public Information Office will send out a news release to the media) were contacted. | 67692807-818f-496b-9fb6-018f0decdb42 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-07-13 | 1 | 1 | 1 | 0 | 0 | 0
2015-08-28 | 2015-08-29 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2400 Block of Meadowbrook Drive | 48000 | CTS Nos. 77716 and 77714 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 8/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-06-19 | 2018-06-19 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 7180 South Lake Pkwy. | 3600 | Lines will be televised and De-greaser applied to sewer main and if problem is located it will be repaired. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Grease |  |  | Juan Robles | Juan Robles | 6/20/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Probable Cause of Spill: Grease | Cleared Blockage. Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-29 | 2015-10-29 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Dacula | Balley Road Pump Station | 7500 | fax received 10/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/29/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Break in force main | Repaired force main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-08-17 | 2015-08-17 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 820 Harrington Dr. | 3850 | Emergency Response Team was notified on 08/18/2015; Complaint Tracking System No: 77613 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Rags |  |  | Kim Hembree | Kim Hembree | 8/18/2015 12:00:00 AM |  |  |  |  | 1 | Fishing Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE | 478-414-4059
2018-04-20 | 2018-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 645 Bolton Rd. NW - Atlanta | 2 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 4/21/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown; this is not a city problem. | None; this is not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-29 | 2015-01-29 | Columbus Water Works (South WRF) | Muscogee | Columbus | Cross Gates St. at Teresa St. | 326 | REC INITIAL CALL 1/29/2015. REC EMAIL 2/2/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Roots |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/29/2015 12:00:00 AM | Chattahoochee | 1/29/2015 12:00:00 AM |  |  | 1 | Mill Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A stopup due to debris caused an 8 inch pipe to leak where roots had penetrated the pipe. The basin is Mill Branch | Once the debris was cleared and flow returned to normal, the overflow stopped. Roots will be cleared and repairs made on the pipe. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2017-01-27 | 2017-01-27 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd. | 950000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/27/2017 12:00:00 AM | Suwannee |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet Weather |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-27 | 2017-01-27 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd. | 950000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/27/2017 12:00:00 AM | Suwannee |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet Weather |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-24 | 2016-01-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 50 Mount Zion Road, SE | 2235 | fax received 1/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/25/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-25 | 2015-02-26 | Rochelle, City of (Northwest WPCP) | Wilcox | Rochelle | manhole on Jackson Road in Rochelle, GA. | 120 |  | Raw Sewage | Southwest District | GA0024244 | Collection System | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 2/26/2015 9:48:00 AM | Suwannee | 2/26/2015 12:00:00 AM |  |  | 1 | Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall event and I & I in collection system. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-03-03 | 1 | 1 | 0 | 0 | 0 | 0
2018-02-05 | 2018-02-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 4800 Buford Highway, Chamblee GA 30341 | 8580 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/5/2018 4:08:00 PM |  |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | brocken main | pressured washed manhole 18-280-s062 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-28 | 2015-04-28 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 30.2 mg/L on 04/28/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-18 | 2018-04-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 526 Peyton Rd. SW - Atlanta | 700 | Fax sent 2018-04-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/19/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-07 | 2016-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1025 Fulton Industrial Blvd, NW | 2950 | fax received 6/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/8/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-12 | 2018-03-12 | Cobb County Water System | Cobb |  | 4667 Patrick Dr. | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/12/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-14 | 2017-06-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1000 Peachtree St. - ATL | 750 | Email received 2017-06-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/15/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-16 | 2016-02-16 | Cobb County Water System | Cobb |  | 2395 New MacLand Road | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/24/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | WIld Horse Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravell in sewer main causing the manhole to overflow into a tributarty of Wild Horse Creek |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-04 | 2015-10-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Alpine Lift Station | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 10/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Fork of Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Torrential Rains |  | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-894-3085 | CITY OF CORNELIA WPCP
2018-08-02 | 2018-08-07 | Waycross, City of (Waycross WPCP) | Ware | Waycross | Intersection of Sycamore St. and Pendergast St. in Waycross, GA | 15000 | Spill letter and paperwork was received at the EPD coastal district office on 8/7/2018 which included a copy of the posted notification and a map of the discharge point and sampling sites. | Raw Sewage | Coastal District | GA0020966 | Collection System | Canal | Canal | Debris |  | Bill Hawthorne | Brett Berry | Brett Berry | 8/2/2018 8:00:00 PM | Satilla | 8/3/2018 12:00:00 AM | 2018-08-03 | 2019-08-03 | 1 | Tributary A1 Waycross Drainage Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Spill occurred following a 2 inch afternoon rainfall. A blockage in the main was located at Byrd Street and Wilkerson Street. | Blockage was cleared by the use of a Jetter Trailer. Signs were posted at the spill site as well as downstream and upstream sampling locations. The area of the spill was cleaned following the incident. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-08-07 | 1 | 1 | 0 | 0 | 0 | 0
2017-12-18 | 2017-12-18 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | 827 South Herod Road, Dawson, Georgia, 31742 | 1500 | Spill has not reached waterway. Assured that the spill was contained and will not enter enter water | Digester Sludge | Wastewater Regulatory Program | GA0021326 |  | Ground |  | Operator error |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/18/2017 12:00:00 AM | Flint |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Overflow of digester | Sludge will be removed when it has dried | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | Jon Bergozza |  | City of Dawson
2016-02-03 |  |  | DeKalb |  | 4422 Oakleaf Cove | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-19 | 2016-02-19 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6930 Hilltop Court, Columbus (Manhole) | 1049 | Voice mail, and email received on 02/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Rags |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/19/2016 12:00:00 AM | Chattahoochee | 2/19/2016 12:00:00 AM |  |  | 1 | Standing Boy Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 12 inch main was clogged with rags, causing a manhole to overflow. | Once the obstruction was cleared, flow returned to normal and the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-22 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-04 | 2016-03-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3371 Lake Valley Road, NW | 8550 | fax received 3/07/2016 Spill volume updated 2017-06-06 based on correspondence from November 2016 that states the spill was non-major with 8550 gallons total spilled. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/7/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-04 | 2017-05-04 | Fulton County (Camp Creek WPCP) | Fulton |  | 615 Stonehill Dr. Atlanta, GA 30336 | 17700 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/4/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fallen tree broke sewer pipe. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-01 | 2016-08-01 |  | Rockdale |  | 1364 Old Milstead Road | 600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/1/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | Removed Roots and Debris from the manhole. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-24 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | City of Social Circle Little River WPCP | 1050012 | ERT contacted 1/24/2016. CTS No. 78862 | Treated Effluent | Wastewater Regulatory Program | GA0026107 | WWRF | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 1/24/2016 12:00:00 AM |  |  |  |  | 1 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2015-05-19 | 2015-05-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 196 Montgomery Ferry Road, NE | 2310 | fax received 5/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/20/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-23 | 2017-05-23 | Athens-Clarke County (North Oconee WPCP) |  | athens | 165 Hiawassee | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/23/2017 12:00:00 AM | Oconee |  |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | paper towels clogged sewer |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-25 | 2017-01-25 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville | Victory Division Drive | 50 |  | Raw Sewage | Coastal District | GA0047180 | WWTP | Stream | Stream | Rags |  | John Kalp | John Kalp | John Kalp | 1/25/2017 3:00:00 PM | Ogeechee | 1/25/2017 12:00:00 AM |  |  | 1 | Taylor Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Yes | 0 | See documentation section. | See documentation section. | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2017-01-26 | 1 | 1 | 0 | 0 | 0 | 0
2016-12-27 | 2016-12-27 | Greensboro, City of (South WPCP) | Greene | Greensboro | Adrian Circle | 8900 | Spill report received by fax. | Raw Sewage | Wastewater Regulatory Program | GA0021351 | WWTP | Stream |  | Pipe failure |  |  | Hsin Yeh | Hsin Yeh | 12/27/2016 12:00:00 AM |  |  |  |  | 0 | Town Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure | Jetted the sewer main and wash down the area and put lim on the area that had raw sewage. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-01 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-21 | 2015-01-21 |  | DeKalb | Lithonia | 3148 Meadow Glade Court, Lithonia | 1960 | Notification received on January 22, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/22/2015 12:00:00 AM |  |  |  |  | 0 | Sanpfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:55 hours when a crew pressure washed the 8" sewer main 226ft downstream, removed the grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-30 | 2015-05-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4329 Kimball Road, SW | 200 | fax received 5/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/31/2015 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-20 | 2016-12-20 | Rome, City of (Rome WRF) | Floyd |  | Green Acres Community | 8750 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 12/20/2016 12:00:00 AM | Coosa |  |  |  | 0 | Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease and roots in the sewer main | The sewer main was thoroughly cleaned. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-12 | 2018-05-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1257 McLynn Avenue Atlanta GA 30306 | 3960 | manhole 15-055-s069 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/13/2018 10:54:00 AM | Ocmulgee |  |  |  | 1 | South Fork Peachtree Creek & unnamed tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Rodded sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-10 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 2986 Wilson Circle | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow and pressure washed to clean main |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-14 | 2017-06-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 795 Lullwater Rd. NE - ATL | 75 | Email received 2017-06-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/15/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-04 | 2017-03-04 | Cobb County Water System | Cobb |  | 3371 Johnson Ferry Road | 300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/4/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Chimney | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Lee Street | 8000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Sam Buckles | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cornelia Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain |  | 455ebb3c-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-490-4613 | CITY OF CORNELIA
2018-06-27 | 2018-06-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 934 Kingway Drive, Lithonia GA 30058 | 600 | manhole 16-095-s001 spilling | Raw Sewage |  | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/28/2018 9:07:00 AM | Ocmulgee |  |  |  | 0 | North Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 720 Berkeley Ave NW - ATL | 500 | Fax received on 01/22/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | T%he cause of the spill was debris in the mainline. | The process to clean and disinfect the site was initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2018-02-03 | 2018-02-03 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 6269 Allison Rd. - Cumming | 50 | Email sent 2018-02-04 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 2/4/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Malfunctioning air release valve | Repaired |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-04 | 2015-09-04 | Columbus Water Works CSO | Muscogee | Columbus | Forrest Road & Lamore Street | 365 | Received fax on September 4, 2015 | Raw Sewage | Wastewater Regulatory Program | GA0036838 | Collection System | Basin |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Bull Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer Crews responded to a leak on an 18" line caused by leak in bell. | Columbus Water Works initiated sewer pump around to stop the leak and will further investigate to either repair line or reroute line. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-17 | 2017-03-17 | Fulton County (Big Creek WPCP) | Fulton |  | 1165 Perimeter Center West | 77400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debis |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 800 Branch of Gornto Road - Valdosta | 9725 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/22/2017 12:00:00 AM | 2017-01-22 |  | 1 | Two Mile Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Large amounts of rainfall in excess of 6 inches within a 24-hour period. | Cleanup and disinfecting at overflow location and stream discharge points. Began monitoring and testing the area.The location has been added to the city's list for rehabilitation. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-11 | 2015-11-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 550 | fax received 11/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 11/12/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-03 | 2016-07-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 15 Barksdale Drive, SE | 30 | fax received 7/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-15 | 2018-03-15 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 173 Highland Drive - Winder | 96 | Email sent 2018-03-16 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Grease Interceptor | Stream | Stream | Roots |  | Alys Hannum | Alys Hannum | Alys Hannum | 3/16/2018 12:00:00 AM |  | 3/15/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Beech Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots protruding into a manhole and sewer main. | Root growth removed, line jetted. Area sanitized. Roots cuts. CCTVed. New manhole set. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-07 | 2018-09-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 166 Meadow Park Ln. SW - Atlanta | 13 | Fax sent 2018-09-08 | Raw Sewage |  | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 9/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-21 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | Bell Creek | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/2/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The rainfall caused flows to elevate at the Bell Creek WPCP. | Process adustments were made by operations staff to minimize the amount of the release and further research is being conducted to eliminate a future occurence. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-17 | 2015-09-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2920 Martin L King Jr Drive, SW | 798 | fax received 9/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Unknown |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/20/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-07 | 2016-02-07 | Marietta (City of)- Sewers | Cobb | Marietta | 814 Sandtown Rd. | 4400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A sewer main blockage caused a sewer manhole to overflow in the street and discharge to a nearby storm drain. Marietta Water personnel quickly relieved the blockage by hydro jetting the main thus restoring normal service. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-27 | 2018-07-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 24730000 | This spill is also entered as a violation. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Wet weather |  | Alys Hannum | Alys Hannum | Alys Hannum | 8/2/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | South River Major TSS Spill From midnight July 27 to midnight July 28, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. July 28 TSS - 31 mg/L Permit Limit = 15 mg/L | Seeking landfill options for the removal of excess solids. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1011 Hilburn DR SE - ATL | 1110 | Fax received on 01/21/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2015-11-17 | 2015-11-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall Street, SE | 860 | fax received 11/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/18/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-20 | 2015-02-20 |  | Hancock | Sparta | Hancock State Prison | 10000 | ERT contacted 2/20/2015 - CTS No. 76003. Verbal and email notification received 2/20/2015 | Raw Sewage | Wastewater Regulatory Program |  | N/A | Storm Drain |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/20/2015 12:00:00 AM |  |  |  |  | 1 | Pinkston Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Broken Pipe | Pipe is being excavated and replaced. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Georgia Department of Corrections (GA DOC)
2016-10-04 | 2016-10-04 | HARTSFIELD-JACKSON ATLANTA INTERNATIONAL AIRPORT | Fulton | Atlanta | Atlanta Hartsfield-Jackson Airport | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | [5 empty] | Kim Hembree | Kim Hembree | 10/4/2016 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Hartsfield-Jackson Atlanta International Airport
2015-03-24 | 2015-03-24 | Paulding County (Coppermine Road WPCP) | Paulding |  | Summer Hill Road | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 3/25/2015 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | Jetted and cleaned all lines | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey | 678-224-4077 | PAULDING COUNTY - COPPERMINE WRF
2016-07-22 | 2016-07-22 | Thomaston, City of | Upson | Thomaston | Moore's Crossing Lift Station | 8960 |  | Raw Sewage |  |  | Collection System |  | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/26/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary Delray Rd. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to a power outage within the service area. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-13 | 2015-08-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 437 W. Ontario Ave. S.W. | 5 | Fax was received on 08/14/2015. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/14/2015 12:00:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-04 | 2016-01-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1071 Dunbarton Trace, Brookhaven | 3840 | Notification received on January 5, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 1/4/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 12:10 hours, when a crew pressure washed the 8" sewer main 800ft, cleared the blockage and restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-05 | 2017-01-11 | Cobb County MS4 | Cobb |  | 2352 Goodwood Dr. | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2352 Goodwood Dr. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-11 | 2018-01-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3045 Wadsworth Mill Place Decatur GA 30032 | 3000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/11/2018 6:22:00 PM | Ocmulgee | 1/11/2018 12:00:00 AM |  |  | 1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure washed m/h 15-153-s096 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-12 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Devin Olawumi |  | Dekalb Co Dept. Watershed Management
2018-06-29 | 2018-06-29 | Cobb County Water System | Cobb |  | 3340 Bryan Way | 260 | Spill report attached. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson |  | Reginald Williamson | 6/29/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel | The spill stopped at 10:30 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-03 | 2015-11-03 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 12/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise as high as 30.0 mg/L on 11/03/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-28 | 2016-10-28 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Pumping Station Rd., Milledgeville | 4500 | Initial call 10/28 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Power failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 10/28/2016 12:00:00 AM | Oconee |  |  |  | 1 | Fishing Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump failure caused pressure to build in the sewer line, resulting in 5 manholes weeping | Restarted pumps. Cleaned and limed area. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE | 478-414-4059
2017-03-27 | 2017-03-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1700 Chantilly Drive, Atlanta | 6240 | Notification received on March 29, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 3/27/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage | The problem was corrected at 13:47 hours when a crew root-cut between manholes, cleared the blockage at 6ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 616 Mitchell Bridge Rd., Athens | 10251 | Initial email 11/9, full report faxed 11/10 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/9/2015 12:00:00 AM | Oconee | 11/7/2015 12:00:00 AM | 2015-11-07 |  | 1 | tributary to Middle Oconee | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | manhole overflow caused by flooding during a major rain event | sewer upgrade is under design |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-10 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-12-28 | 2015-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1430 Country Squire Drive, Decatur | 995 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/29/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected on December 29, 2015 at 02:25 hours, when the rain subsides and returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-17 | 2015-12-17 | Atlanta, City of (East Area CSO) | Fulton | Atlanta | Custer Avenue WQCF | 139000 | CTS No. 78548 and 78549. This is an "overflow" of partially treated effluent. | Primary Effuent | Wastewater Regulatory Program | GA0037168 | WWRF | Stream |  | Equipment failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/17/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This is an "overflow" of partially treated effluent. Total volume = 139,000 gallons This overflow also experienced a release of sodium hypochlorite that resulted in a fish kill. Overflow was a result of de-chlorination equipment failing to start. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-12 | 2015-01-12 |  | Lowndes | Valdosta | 1834 Remer Lane | 3400 | fax received 1/13/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/13/2015 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | I&I from heavy rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-04-23 | 2018-04-23 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 2840 Pierce Drive S | 5200 |  | Raw Sewage | Wastewater Regulatory Program | GA0024538 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/26/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Bowman Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Debris has been removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-23 | 2018-04-23 | Macon Water Authority (Lower Poplar WRF) | Bibb | macon | 2840 Pierce Drive S | 5200 |  | Raw Sewage | Wastewater Regulatory Program | GA0024538 | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/26/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Bowman Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Debris has been removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-13 | 2018-03-13 | Fulton County (Big Creek WPCP) | Fulton | Roswell | Behind 1970 six Branches Lane Roswell, 30076 | 5400 | SSO Report uploaded. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/13/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. The area impacted by the spill is in the process of being cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-07 | 2017-03-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3254 Northside Pky. NW - ATL | 1920 | Fax received 2017-03-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 3/8/2017 12:00:00 AM |  | 3/7/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-10 | 2016-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 262 Rumson Road, NE | 475 | fax receive 6/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/13/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew excavated and repaired the mainline |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-12 | 2016-05-12 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Sugar Hill | 988 Pine Acre Drive | 9903 | fax received 5/12/2016. This was upgraded to a major spill due to violation of fecal water quality standards. | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/12/2016 12:00:00 AM |  |  | 2016-05-13 | 2017-05-23 | 1 | Unnamed Tributary to Level Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rags and other flushables. This was upgraded to a major spill due to a violation of the fecal coliform water quality standards. | Raked area and spread lime. Placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-16 | 0 | 1 | 0 | 1 | 1 | 0 | [8 empty] | GWINNETT COUNTY
2016-09-12 | 2016-09-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 640 Aline Drive, NW | 690 | fax received 9/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/13/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-17 | 2018-04-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2717 Cascade Rd. SW - Atlanta | 2795 | Fax sent 2018-04-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/14/2018 12:00:00 AM |  | 4/13/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew performed a point repair |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Chandler Haulk Lift Station | 7800 | email notification received 11/09/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Little Haynes Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2016-10-11 | 2016-10-11 | Savannah, City of (President Street WRF) | Chatham | Savannah | 54 Litchfield Driver | 530 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Stream | Stream | Power failure |  | David Lyle | Hailey Harden | Hailey Harden | 10/11/2016 12:00:00 AM | Ogeechee | 10/11/2016 12:00:00 AM |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |  | 0 | Hurricane Matthew cause a power outage allowing an overflow of a manhole | Pumped and hauled sewage from station wet-well. Portable generator was sent to the site. cleaned up area with City of Savannah Jet Vacuum truck. Spill notifications were placed at the spill site, drainage pond, and the kings ferry landing boat ramp. | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0
2018-06-08 | 2018-06-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2301 Mountain Industrial Boulevard Tucker GA 30084 | 4120 | manhole 18-215-s221 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/8/2018 8:29:00 PM | Ocmulgee |  |  |  | 1 | Camp Creak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rag debris blockage | vacuum manhole to stop sewer spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-19 | 2016-09-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2353 Burroughs Avenue, SE | 295 | fax received 9/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/20/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-11 | 2017-04-11 | Monroe, City of (Jack's Creek WPCP) | Walton | Monroe | 942 Harvest Lane - Montor | 2400 | Email received 2017-04-11 | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 4/11/2017 12:00:00 AM |  |  |  |  | 1 | Tribe to MT. CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease buildup and rags. | Cleaned up location and spread lime out. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-24 | 2017-02-24 | Fulton County (Big Creek WPCP) | Fulton |  | 128 Webb Street Roswell | 3560 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/24/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Failure | THE SEWER SYSTEM IMMEDIATELY UPSTREAM AND DOWNSTREAM HAS BEEN CLEANED. THE FAILED PIPE LINE HAS A TEMPORARY REPAIR AND WE ARE IN THE PROCESS OF CLEARING THE EASEMENT FOR PERMAMENT REPAIRS. INHIBITORS HAVE BEEN APPLIED TO MINIMIZE ODORS. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-06 | 2015-11-06 | Commerce, City of (Northside WPCP) | Jackson | Commerce | Waterworks Lift Station | 2500 |  | Raw Sewage | Wastewater Regulatory Program | GA0026247 | Collection System | Stream |  | Contractor |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/6/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-31 | 2017-03-31 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 106 Morehead Dr. - Martinez | 1000 | Fax received Saturday, 2017-04-01 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/1/2017 12:00:00 AM |  | 3/31/2017 12:00:00 AM |  |  | 1 | Mystery Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Unstopped main with high pressure jet machine. Cleaned up overflow and posted signs. Follow up inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-19 | 2017-02-19 | Cobb County Water System | Cobb |  | 2226 Courts Dr | 280 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sewell Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-25 | 2017-01-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Rd, SW - ATL | 3600 | Fax received on 01/26/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 1/26/2017 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-11-04 | 2016-11-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 420 New Jersey Ave., NW, Atlanta | 88 | Fax recieved on 11/05/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Paul Moisan | Paul Moisan | 11/5/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown at this time. | A televised inspection of the mainline has been scheduled. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-15 | 0 | 1 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2015-01-04 | 2015-01-04 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 444 Branham Circle | 1200 | fax received 1/05/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM |  |  |  |  | 1 | Tributary of Stroud's Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The jet machine was used to clear the grease blockage. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2015-02-09 | 2015-02-10 |  | Lincoln | Lincolnton | N.E. of lift station #4 at TB1.A.3 manhole | 18000 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 2/12/2015 12:00:00 AM |  |  |  |  | 0 | Town Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This spill was caused by clogging due to roots, grease and debris. | The City of Lincolnton has started all necessary procedures to carry out the guidelines for handling major spills according to their permit. Such guidelines include sampling for Fecal, measuring pH, DO and taking the temperature of the water. Line was unclogged February 10, 2015 at 09:30 hours. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-20 | 2016-01-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Lovejoy | 10851 South Shore Ct., Lovejoy MH #2212554 | 1575 | Fax received on 01/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/20/2016 12:00:00 AM | Flint |  |  |  | 1 | Hurricane Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Lines will be televised and roots cut if a problem is located. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-21 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-13 | 2017-07-13 | Habersham on Lanier WPCP | Forsyth |  | 1950 Buford Dam Road | 1200 |  | Raw Sewage | Mountain District - Cartersville | GA0030261 | WWTP | Stream |  | Equipment failure |  | Mick Smith | Kathy Lewis | Eric Dykes | 7/13/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Lake Lanier | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump Station failure at Habersham #2 Pump Station | Pump was replaced with a new pump | 4265e0af-00af-4b96-982e-53f807bc3994 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2324 Adams Dr. NW - ATL | 20 | Fax sent 2018-02-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 2/5/2018 12:00:00 AM |  | 2/5/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain induced | Unknown |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-04 | 2017-05-04 | Thomaston, City of | Upson | Thomaston | 107 Avenue | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/4/2017 12:00:00 AM | Flint |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Debris was removed | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-17 | 2015-08-17 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 439 Shenandoah Court | 9432 | fax received 8/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/18/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Beech Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Split in the sewer force main from Clay Howard Sewer Pump Station | Replaced pipe | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER | 770-868-0863
2017-01-02 | 2017-01-03 | Columbia County (Little River WPCP) | Columbia | Evans | 4000 Blanchard Woods Drive - Evans | 10001 | Received 2017-01-12 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/6/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM |  |  | 1 | Euchee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Surcharging from excessive rainfall. | Monitored area, searched for inflow, spread lime over the affected area, planned sampling of creek and posting signs. Follow-up inspections, sampling, and reporting will continue as required. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 1 | 1 | 0
2015-12-24 | 2015-12-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1430 Country Squire Drive, Decatur | 86280 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected on December 25th, at 11:00 hours, when the rain subsided and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-27 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 619 Pierce Ave., Macon MH #71261 | 675750 | Email and fax received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/26/2015 12:00:00 AM | 2015-12-29 | 2016-11-29 | 1 | Bowman Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The spill was hydraulic overload. The MWA service are received 5.78 inches of rainfall from December 21-26. | Debris will be removed from the area and the affected area will be disinfected with lime. The MWA will continue its search for I/I into its sewer system through CCTV and flow monitoring investigations and will develop rehabilitation projects based on this information and contractor conducted sewer evaluations. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-10-23 | 2016-10-26 | Thomasville, City of (Oquina Creek WPCP) | Thomas | Thomasville | Robin Hood Rd. and Friar Tuck, Thomasville | 148000 | Phone call and email received on 10/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024082 | Lift Station | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/24/2016 12:00:00 AM | Suwannee |  | 2016-10-26 |  | 1 | Olive Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Broken force main. | Force main repaired. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-24 | 0 | 1 | 0 | 1 | 0 | 0
2015-07-17 | 2015-07-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 102 Rogers Street, SE | 1995 | fax received 7/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/19/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disjointed pipe | The crew used hydraulic mix to repair the pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-24 | 2018-04-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 2250 | Vault 30-5012 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/25/2018 11:52:00 AM | Ocmulgee | 4/24/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | Wait until Storm ended |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-04 | 2016-04-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 150 Warren Street, NE | 1 | fax received 4/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/5/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-06 | 2016-10-06 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | Southeast WPCP located at 622 Iron Road in Douglas. | 18360 |  | Raw Sewage | Coastal District | GA0024431 | Lift Station | Ditch | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/6/2016 9:30:00 AM | Satilla | 10/6/2016 12:00:00 AM | 2016-10-06 |  | 1 | Unnamed tributary of the Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Submersible pump failure that resulted in a manhole overflowing inside the Southeast WPCP property. | A by-pass pump was utilized until the submersible pump was repaired and brought back online. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-17 | 1 | 1 | 0 | 0 | 0 | 0
2015-03-05 | 2015-03-05 |  | DeKalb | Clarkston | 3589 Indian Creek Way, Clarkston | 4680 | Notification received on March 6, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/6/2015 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and large sticks blockage | The problem was corrected at 15:35 hours when a crew removed the large sticks and debris out of the mouth of the manhole, pressure washed the sewer main 215ft; removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-10 | 2015-06-10 | Rome, City of (Rome WRF) | Floyd |  | 268 Old Lindale Road | 8400 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 6/11/2015 12:00:00 AM | Coosa |  |  |  | 0 | Silver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was result of a blockage due to grease and a collapsed sewer main | The sewer main was repaired and thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2017-04-22 | 2017-05-02 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 706 North Jefferson Street - Dublin | 750 | Email received 2017-04-24. | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/24/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Restriction in the sewer main caused by concrete rubble that was not removed by the contractor. | Crew used a Vac Truck with a high pressure jetter to clean that section of sewer. To further investigate, Dublin will run a camera to video all the sections of the sewer along the paving project and remove any foreign debris as found. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-16 | 2016-02-16 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | A spill was not recognized to have occurred until the facility received a copy of its lab results. Weekly average effluent BOD was greater than 50% the permit limit for two days, 2/16 and 2/17: BOD, weekly average concentration (mg/L): permit = 12, reported = 26.8. Daily flow was 0.855MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 3/16/2016 12:00:00 AM | Ogeechee | 3/16/2016 12:00:00 AM | 2016-03-16 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Outfall spill caused by an imbalance in the loadings of the facility due to heavy rainfall. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-21 | 0 | 1 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 26.8
2015-05-29 | 2015-05-29 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1304 Hunt Avenue | 1949 | REC EMAIL 5/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Pipe failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/29/2015 4:44:00 PM | Chattahoochee | 5/29/2015 12:00:00 AM |  |  | 1 | Mill Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A leaking bell was discovered discharging into Mill Branch Creek | The leaking bell was repaired and the discharge was stopped . | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-10 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2016-01-15 | 2016-01-15 | Cobb County MS4 | Cobb |  | 26020 Owens Ave. | 650 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/15/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8 in pvc main | washed down road | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-10 | 2015-10-10 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 624 Clubland Circle | 2600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/10/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | McClane Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Removed Grease | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-20 | 2016-11-26 | Rochelle, City of (Southeast WPCP) | Wilcox | Rochelle | Permitted outfall at Mill Creek for WWTP. | 230000 | Day 1-Day 7 stream monitoring received on 01/04/2017. | Treated Effluent | Southwest District | GA0024236 | WWTP | Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 12/13/2016 6:16:00 PM | Suwannee |  | 2016-12-14 | 2018-01-03 | 1 | Mill Creek tributary | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 20000 | 0 | Wet weather and hydraulic overloading of WWTP resulted in through plant major spill for weekly BOD loading (reported 12.2 kg/day). | Comply with emergency action requirements. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-01-05 | 1 | 1 | 0 | 1 | 1 | 0 | [11 empty] | 12.2 kg/day
2016-12-19 | 2016-12-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 324 E Paces Ferry Rd, NE, ATL | 415 | Fax received on 12/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/20/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-21 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-12-01 | 2015-12-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5361 Vernon Lake Drive, Dunwoody | 515 | Notification received on December 7, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 12/2/2015 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected at 22:00 hours when a crew pressure washed the 8" sewer main 222ft upstream, clearing the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-03 | 2016-04-09 | Ochlocknee, Town of (Ochlocknee WPCP) | Thomas | Ochlocknee | Pine Creek in the Ochlocknee River Basin | 77000 | Major Spill as defined in permit. The avg. weekly concentration for TTS was reported as 13.7 kg/day, the limits set in the permit are 6.8 kg/day. | Treated Effluent | Southwest District | GA0046370 | WWTP | Stream | Stream | Wet weather |  |  | Linda Stevens | Jay Howell | 5/20/2016 12:00:00 AM | Ochlockonee | 5/22/2016 12:00:00 AM | 2016-05-23 | 2017-05-24 | 1 | Pine Creek | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall and I&I resulting in hydraulic overload of the treatment plant. | Continue to fix and repair I&I issues as they are discovered. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-05-23 | 0 | 1 | 1 | 1 | 1 | 0 | [8 empty] | City of Ochlocknee |  |  |  | 13.7 kg/day
2016-04-03 | 2016-04-09 | Ochlocknee, Town of (Ochlocknee WPCP) | Thomas | Ochlocknee | Pine Creek in the Ochlocknee River Basin | 77000 | Major Spill as defined in permit. The avg. weekly concentration for TTS was reported as 13.7 kg/day, the limits set in the permit are 6.8 kg/day. | Treated Effluent | Southwest District | GA0046370 | WWTP | Stream | Stream | Wet weather |  |  | Linda Stevens | Jay Howell | 5/20/2016 12:00:00 AM | Ochlockonee | 5/22/2016 12:00:00 AM | 2016-05-23 | 2017-05-24 | 1 | Pine Creek | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall and I&I resulting in hydraulic overload of the treatment plant. | Continue to fix and repair I&I issues as they are discovered. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 72b89952-7fed-43ef-a49d-acceca69b62c | 2016-05-23 | 0 | 1 | 1 | 1 | 1 | 0 | [8 empty] | City of Ochlocknee |  |  |  | 13.7 kg/day
2017-04-05 | 2017-04-05 | Marietta (City of)- Sewers | Cobb | Marietta | 627 N Marietta Pkwy | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet Weather I/I |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-23 | 2017-03-23 | Monroe, City of (Jack's Creek WPCP) | Walton | Monroe | Vine Street Pump Station - Monroe | 6000 | Email received 2017-03-23 | Raw Sewage | Wastewater Regulatory Program | GA0047171 | Pump Station | Stream |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 3/23/2017 12:00:00 AM |  |  |  |  | 0 | Tributary to Hard Labor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical issues. | Cleaned up location and spread lime out. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-20 | 2018-08-20 | Macon Water Authority (Rocky Creek WPCP) | Macon | Macon | 722 Old Lundy Road, MH ID 67045 | 405 |  | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Juan Robles | Juan Robles | 8/22/2018 12:00:00 AM |  |  |  |  | 0 | Sabbath Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. | Debris was removed and area was disinfected with lime. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-08-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-21 | 2015-02-21 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2914 Collier Drive, NW | 100 | fax received 2/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/22/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-09 | 2015-11-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Woodbine Circle, SE | 75 | fax received 11/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-28 | 2017-03-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3181 Midway Road, Decatur | 10050 | Notification received on March 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/28/2017 12:00:00 AM |  |  |  |  | 1 | Cobb Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:51 hours when a crew pressure washed between manholes 600ft, cleared the blockage at 300ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1621 Hasty Place, NW | 30 | fax received 12/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain induced |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-22 | 2016-02-22 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 260 St. George Dr., Athens | 14 | Initial email 2/22, full report faxed 2/23 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Roots |  |  | Dagny Pariani | Dagny Pariani | 2/22/2016 12:00:00 AM | Oconee | 2/22/2016 12:00:00 AM |  |  | 1 | un-named tributary to Middle Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and rags blocked flow in sewer line | Rodded and flushed the line |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-08-30 | 2015-08-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2217 Cascade Road, SW | 343 | fax received 8/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 8/31/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and vandalism to bypass pump | Repairs made to bypass pump, debris removed. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-07 | 2017-01-07 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1820 Doug Barnard Pkwy - Augusta | 373620 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System |  |  | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/7/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The wastewater collection system was still recovering from 7-inch rain event earlier in the week. | Projects to remove rainwater from the wastewater collection system are in various stages of design and implementation. Begun monitoring of Butler Creek as requested by the EPD. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 4557 Meadow Creek Path, Lithonia | 89700 | Notification received on January 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 10:02 hours on January 24, 2017 when the rain stopped and the sewer flow return to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-03 | 2017-03-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2535 Friar Lane - Augusta | 100 | Email received Sunday, 2017-03-05. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 3/5/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, rags and debris | Sewer gravity main was cleaned and the downstream storm pipe was flushed and vacuumed out. Further investigation regarding sewer gravity main structural inspection and origin of grease are ongoing. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-06 | 2018-03-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 61 Delmoor Dr. NW - Atlanta | 10 | Fax sent 2018-03-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/7/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-25 | 2017-10-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4949 Memorial Drive, Stone Mountain | 1260 | Notification received on October 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWRF | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/25/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:13 hours when the first responder crew pressure washed the 8-inch sewer main 365-ft, cleared the blockage and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-30 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-25 | 2016-05-30 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 0 | Stream monitoring initiated 6/3/16. Public notification posted at City Hall on 6/3/16. Notification to the Burke Co. Health Department completed on 6/6/16; and notification published in the June 8th edition of The True Citizen. Stream monitoring ceased prior to the Week 3 sampling event since the facility experienced another effluent major spill on June 2nd. Stream monitoring to be conducted under the June 2nd spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream | Other |  | Delaine Scott | Delaine Scott | Delaine Scott | 6/3/2016 12:00:00 AM | Savannah | 6/2/2016 12:00:00 AM | 2016-06-01 | 2016-06-22 | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility's routine effluent monitoring revealed that the BOD weekly max had been exceeded by more than 50%. |  | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-06-03 | 1 | 1 | 0 | 1 | 0 | 0 | Jonathan Tindall | 912-449-0999 | Tindall Enterprises, Inc.
2017-01-05 | 2017-01-05 |  | Cobb |  | 2352 Goodwood Drive | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The Water System was notified at 11:01 a.m. and the crew stopped the overflow at 11:50. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Marietta (City of)- Sewers | Cobb | Marietta | 721 Smithstone Rd | 675 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Marietta Water personnel quickly sealed the pipe defect with hydro cement thus restoring normal service. This line is currently under contrac for 2017 relay due to recurring problems and pipe defects. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-29 | 2016-03-01 | Augusta, City of (Spirit Creek WPCP) | Richmond | Augusta | Spirit Creek WPCP | 0 | Verbal notification received 3/07/2016 | Treated Effluent | Wastewater Regulatory Program | GA0047147 | WWTP | Stream |  | Unknown |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/7/2016 12:00:00 AM |  |  |  |  | 1 | Spirit Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill for BOD. Reported BOD = 72 mg/L. Total Volume = 1.17 million |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-12-26 | 2015-12-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2351 Armand Road, NE | 2410 | Spill report received 1/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/18/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-02 | 2018-08-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 231 Atlanta Ave. SE - Atlanta | 15 | Fax sent 2018-08-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 8/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown. Not a city problem. | None. Not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2017-06-23 | Cobb County Water System | Cobb |  | 2195 Cobb Pkwy SE | 710 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Poplar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in 8" Truss Pipe | Stopped spill and spread lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-05 | 2015-11-05 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5978 Reynolds Road (Manhole No. 2203053). | 2400 | Fax was received on 11/06/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 11/6/2015 12:00:00 AM | Flint |  |  |  | 1 | Angel Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Probable cause of spill - roots. | Blockage was cleared and flow was returned to normal. Site was cleaned and work orders generated for additional work to determine cause. Lines will be televised and roots will be cut if a problem is located. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-06 | 0 | 1 | 1 | 0 | 0 | 0
2015-05-22 | 2015-05-22 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Dacula | 1846 Alcovy Trail | 4777 | fax received 2015-05-22 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/22/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Alcovy River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Clogged ARV | Changed out clogged ARV |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY | 678.376.6700
2015-11-29 | 2015-11-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 536 Hollydale Court, NW | 3280 | fax receviced 11/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/29/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-05 | 2017-09-05 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 725 Glenairy Drive | 9720 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-07 | 2017-10-07 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Lift Station #9 King Circle Drive - Swainsboro | 5000 | Call made 2017-10-10. Letter received 2017-10-18. | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Lift Station | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 10/10/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line blockage | Blockage was cleared and line damage was repaired. Lime was applied to the spill site. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-10 | Jesup, City of (Jesup WPCP) | Wayne | Jesup | East Plum Street Lift Station | 8640 |  | Raw Sewage | Coastal District | GA0026000 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/10/2016 9:00:00 AM | Altamaha | 10/9/2016 12:00:00 AM |  |  | 1 | Upper Penholloway Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power at the lift station | Utilized a by-pass diesel pump until power was restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-26 | 1 | 1 | 1 | 0 | 0 | 0
2015-02-16 | 2015-02-16 |  | Lowndes | Valdosta | 1110 Old Statenville Road (Park Chase Apartments) | 375 | Voice mail from Russ Norman received 2/16/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/16/2015 12:00:00 AM |  |  |  |  | 1 | Dukes Bay Canal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags | Cleaned and limed the area | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-07-24 | 2017-07-24 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 819 Barrett Lane - Augusta | 3600 | Email received 2017-07-24 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/24/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, debris and heavy rainfall. | The sewer gravity main was augered to open the line. The Sewer gravity main assessment was reviewed and action is being taken to replace an area with root infiltration. Sewer gravity main will continue to be treated and monitored in the area. The affected area was spread with lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-28 | 2015-10-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1327 Fairview Road, NE | 1128 | fax received 10/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/28/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-13 | 2017-12-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1560 Memorial Dr. SE - ATL | 768 | Fax sent 2017-12-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 12/14/2017 12:00:00 AM |  | 12/14/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 342 Armour Drive, NE | 780 | Notification of this spill was not received until the 5 Day Follow Report was received in EPD's office on 1/12/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/12/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-26 | 2015-09-26 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Big Flat Creek WPCP Influent Pump Station | 2400 | email received 9/28/2015. CTS number 99736 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | WWTP | Stream |  | Power failure |  |  | Kim Hembree | Kim Hembree | 9/28/2015 12:00:00 AM |  |  |  |  | 1 | Big Flat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at the Big Flat Creek WPCP influent pump station. | Restored power |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2015-10-08 | 2015-10-08 | Columbia County (Crawford Creek WPCP) | Columbia |  | 422 Columbia Industrial Blvd | 7300 | fax received 10-08-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/8/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Concrete chunk in pipe | Unclogged main with high pressure jet machine. Removed obstruction from manhole... |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY | 706-863-6928
2018-01-22 | 2018-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton - ATL | 19660000 | TSS - 169 mg/L. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 1/23/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | From shortly before midnight on January 22nd to 7:00 AM January 23rd, City of Atlanta experienced a major spill for TSS due to equipment failure caused by freezing temperatures. This spill is also entered as a violation. | Self-corrected | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-11 | 2018-02-12 | Cairo, City of (Cairo WPCP) | Grady | Cairo |  | 46200 |  | Raw Sewage | Wastewater Regulatory Program | GA0025771 | WWTP |  |  | Wet weather |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/12/2018 12:00:00 AM | Ochlockonee |  | 2018-02-12 |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | wet weather |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-13 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 506 South McDonough Street, Decatur | 32900 | Notification received on January 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 18:07 hours when the heavy rain passed and the sewer flow return to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-23 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3308 Matilda Lane, Columbus | 1169 | Fax sent 5/23/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Paul Moisan | 5/23/2018 12:00:00 AM |  |  |  |  | 0 | Bull Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rains | Once the rain subsided and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 1171 Ga Hwy 100 Tallapoosa, Carroll EMC Power Pole 35.924.015 | 9000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Other |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/7/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Gold Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lightening strike hit power pole and blew fuse, lost phase 3 power, no back up power | Power was restored, flow restored, resident notified, signs posted and sampling begun, excessive rain has limited clean up or treatment processes | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 2170 Keheley Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-03-03 | Rochelle, City of (Northwest WPCP) | Wilcox | Rochelle | manhole adjacent to Sook Road Lift Station. | 1260 |  | Raw Sewage | Southwest District | GA0024244 | Collection System | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 2/26/2015 9:48:00 AM | Suwannee | 2/26/2015 12:00:00 AM |  |  | 1 | Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall event and I & I in collection system. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-03-03 | 1 | 1 | 0 | 0 | 0 | 0
2018-06-03 | 2018-06-03 | Pembroke, City of (Pembroke WPCP) | Bryan |  |  | 5000 |  | Raw Sewage | Coastal District | GA0038377 | Collection System | Ground, Storm Drain, Stream | Ditch |  |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 6/4/2018 12:00:00 AM | Ogeechee | 5/23/2018 12:00:00 AM |  |  | 0 | tributary of ogeechee Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | I&I problem large amounts of rain | Removal of soils and disinfectant applied | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-06-06 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 14850 | Initial call received 4/4, full report received 4/6. The influent and effluent spills both occurred on April 1, 2016. Monitoring results are submitted in regards to the effluent spill. | Raw Sewage | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Hydraulic Overload |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Ochlockonee | 4/1/2016 12:00:00 AM | 2016-04-01 |  | 1 | Parker's Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 1 | Hydraulic overload at the influent side of the WWTP due to extremely heavy rainfall. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-05 | 0 | 1 | 1 | 1 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025
2017-09-19 | 2017-09-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1058 Northside Dr. NW | 755 | Fax sent 2017-09-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2269 Glendale Dr., Decatur | 3300 | Notification received on January 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:46 hours when the crew pressure washed the 8" sewer main 100 ft upstream, cleared the grease blockage at 75 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-14 | 2016-11-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2205 Northside Dr, NW, ATL | 0 | Fax received on 11/14/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Paul Moisan | Paul Moisan | 11/14/2016 12:00:00 AM |  |  |  |  | 0 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown at this time, and has not yet been contained. | More updated information on estimate of spillage and containment to follow. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 |  | Hart | Hartwell | Jailhouse Branch Lift Station | 446750 | This is one of three spills that occurred in the area on 11/2/2015. Total volume spilled = 1.478 mgd | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Ground |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Savannah | 11/3/2015 12:00:00 AM | 2015-11-03 |  | 1 | Lake Hartwell | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 |  | 0 | Extremely heavy rainfall overloaded the sewer system | After rainfall had subsided, lime was applied. City is replacing one sewer line and looking at other upgrades. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-19 |  |  | DeKalb |  | 501 Collingwood Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-09 | 2018-09-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 674 Waterford Rd. NW - Atlanta | 1800 | Fax sent 2018-09-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/10/2018 12:00:00 AM |  | 9/10/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-08 | 2017-03-08 | Marietta (City of)- Sewers | Cobb | Marietta | 335 Roseland St. | 1500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/8/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage and Debris | Marietta Water personnel quickly relieved he blockage thus restoring normal service. A private company is cleaning and sanitizing the building. Surrounding sewer mains are being cleaned and checked for additional blockages. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-06 | 2015-11-06 | Rome, City of (Rome WRF) | Floyd |  | South Rome Community at the intersection of E. 7th Street at Lee Avenue | 1500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 11/6/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This spill was the result of a blockage due to grease and roots in the sewer main. | The spill was stopped and the sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2018-07-27 | 2018-07-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3124 Parkridge Crescent Chamblee GA 30341 | 1800 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Ditch |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/28/2018 7:23:00 AM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 8" main | Made berm in drainage ditch until repairs are made |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-04 | 2017-12-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2511 Barge Rd. SW - ATL | 50 | Email sent 2017-12-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 12/5/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-04 | 2018-06-04 | Cobb County Water System | Cobb |  | 1085 Woodruff Plantation | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/9/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Terrell Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" PVC main | Limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 2607 Lenora Church Rd. - Snellville | 8895 | Fax received 2017-04-05 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/5/2017 12:00:00 AM |  | 4/5/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of No Business Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-11 | 2018-09-11 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 34 Hickory Trace Circle - Swainsboro | 250 | Call made 2018-09-12 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Ground |  | Grease |  | Alys Hannum | Alys Hannum |  | 9/12/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waterways. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Line was cleared with jet truck and lime applied to spill. Spill contained on land. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-02 | 2017-06-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1845 MacArthur Blvd. NW - ATL | 159 | ** This is not a city problem. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/3/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the service lateral. | ** This is not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-20 | 2016-02-20 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2400 Block of Gornto Road | 2175 | Verbal notification received 2/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/22/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-04-08 | 2015-04-08 |  | DeKalb | Brookhaven | 1781 Dresden Drive, Brookhaven | 4620 | Notification received on April 15, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/8/2015 12:00:00 AM |  |  |  |  | 0 | unnamed tributary to North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blocakge | The problem was corrected at 13:03 hours when a crew pressure washed the 8" sewer main 126ft upstream, cleared the grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Columbus Water Works (South WRF) | Muscogee | Columbus | Columbus Water Works, South Columbus Water Resource Facility. | 0 | Telephone call received on 01/22/2016. Fax received on 01/27/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Other |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/22/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An imbalance of flows to the final clarifiers caused the effluent TSS to go up to 53 mg/L on 01/22/2016. | Flows were corrected within 8 hours and proper balance of flows was restored. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-15 | 2015-04-15 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Rd. and Sylvia Dr. | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/15/2015 12:00:00 AM | Suwannee | 4/15/2015 12:00:00 AM |  |  | 1 | Hat Creek | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 4160 Lexington Rd., Athens | 1088 | Initial email 3/15, full report faxed 3/18 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Equipment failure |  |  | Dagny Pariani | Dagny Pariani | 3/14/2016 12:00:00 AM | Oconee | 3/14/2016 12:00:00 AM |  |  | 1 | Cedar Creek | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Private company was rodding a private sewer line when their equipment broke and blocked an Athens-Clarke County sewer line causing it to overflow | Rodded sewer, cleaned area of solids, applied lime. Also advised the private maintenance personnel to notify ACC of future events |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-08-21 | 2015-08-21 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 940 Madison Avenue | 1350 | fax received 8/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/21/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-07-15 | 2015-07-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 4108 Woodwin Court, Doraville. | 6060 | Notification received on July 23, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/15/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blocakge | the problem was corrected at 13:24 hours when the crew pressure washed the 8 inch sewer main 300 feet to remove a blockage at 155 ft from manhole 336-s024. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-07-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-05 | 2018-05-05 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 283A Canon Drive - Social Circle | 50 | Email sent 2018-05-06 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 5/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Degreaser applied to sewer line. Signs posted. Lime applied. Public agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-27 | 2016-03-28 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 600 Block of Scott Drive | 2885 | Email notification received 3/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 3/28/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-11-28 | 2015-11-28 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2244 Roiser Road | 9000 | fax received 11/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 11/30/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-849-5911
2015-12-29 | 2015-12-29 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1140 MLK Jr Dr Pkwy., Athens | 530 | Initial email and full report faxed 12/30 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Other |  | Rags |  |  | Dagny Pariani | Dagny Pariani | 12/30/2015 12:00:00 AM | Oconee | 12/29/2015 12:00:00 AM |  |  | 0 | private pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer blockage caused by rags | Rodded sewer line |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-11-09 | 2015-11-09 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Manhole TRK-0002 206 Sycamore Way | 26250 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 11/9/2015 12:00:00 AM | Chattahoochee | 11/9/2015 12:00:00 AM |  |  | 1 | Soque River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rainfall | Areas affected by spill have been cleaned up and powdered lime has been applied. City is making sure that the manholes at 206 Sycamore Way will be properly sealed to prevent a spill in the future. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | Justin Allen | 706-754-4216 | City of Clarkesville
2017-02-03 | 2017-02-03 | Forsyth County (Fowler WRF) | Forsyth | Alpharetta | 1295 Old Alpharetta Rd. | 100 | Did not reach State Waters. Fax received 2017-02-06 | Raw Sewage | Wastewater Regulatory Program | GA0038695 | Collection System | Stream |  | Roots |  |  | Alys Hannum | Alys Hannum | 2/6/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots grew in sewer line | Jetted from downstream manhole #5503 to upstream manhole #3274, spread lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-10 | 2016-07-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 191 Stanhope Circle, NW | 100 | fax received 7/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Operator error |  |  | Kim Hembree | Kim Hembree | 7/11/2016 12:00:00 AM |  |  |  |  | 0 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by the city crew jet rodding the service lateral. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-13 | 2015-11-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 18 | fax received 11-13-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 11/13/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-07 | 2015-02-07 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 1651 Flat Shoals | 2200 | REC FAX 2/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Roots |  |  | Emily Wingo | Emily Wingo | 2/10/2015 12:00:00 AM | Flint | 2/10/2015 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Cleared Blockage. Follow Up Line will be televised and any problems will be corrected if needed |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-17 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | Clayton Co Water Authority
2017-09-09 | 2017-09-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2815 Kathryn Cir. SW - ATL | 2640 | Fax sent 2017-09-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/10/2017 12:00:00 AM |  | 9/9/2017 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-18 | 2017-01-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 4185 English Oaks Drive, Doraville | 100 | Notification received on January 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 1/18/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected when the crew repaired the lateral by a point repair, which then restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-26 | 2018-06-27 | Forsyth, City of (South WPCP) | Monroe | Forsyth | 789 Montpelier Rd | 0 | Failed to report major spill, (outfall spill). Tested two days in a row at 57mg/L and 45mg/L. Major spill classified if BOD equal or greater than 45mg/L | Chlorinated Effluent | Wastewater Regulatory Program | GA0024732 | WWTP | Stream |  | Other |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/17/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Slippery Rock Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Aerator repair, mechanical failure, excessive rainfall | Repair of mechanical aeration expected to be finished 7/20/18 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-10 | 2018-02-10 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3648 Walton Way Ext. - Augusta | 350 | Email sent 2018-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Rags |  |  | Alys Hannum | Alys Hannum | 2/13/2018 12:00:00 AM |  |  |  |  | 1 | Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy amounts of rags and debris were in the line. | Used the Vac truck to jet wash the line. In between 80’ and 100’ a blockage was opened. The road was washed down and the storm drain was flushed and vacuumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-17 | 2016-05-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3488 Keswick Drive, Chamblee | 1600 | Notification received on May 20, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/17/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots | The problem was corrected at 9:40 hours, when a crew pressure washed the sewer main 69ft up stream, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-23 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-31 | 2017-07-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill St. NW | 75 | Fax received 2017-08-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 8/1/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-17 | 2016-06-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 618 Skipper Drive N.W. | 1170 | fax received 6/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/18/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-09 | 2015-02-09 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 502 Lakemont Drive, Dalton | 225 |  | Raw Sewage | Mountain District - Cartersville | GA02-056 | WWRF | Stream |  | Equipment failure |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/9/2015 12:00:00 AM | Coosa |  |  |  | 0 | Lootens Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cracked manhole base | Hydraulic cement was used to patch the crack | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | Lori McDaniel | 706-529-1032 | DALTON UTILITIES
2016-01-24 | 2016-01-24 |  | Cobb |  | 421 Monroe Way | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/10/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 1383 Cambridge Drive, Perry, GA | 54580 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Big Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage release occurred due to inflow and infiltration related to rain event beginning on December 30, 2015 with an accumulation of nearly 4" inces of rain in a 72 hour period following the large rain event of December 23, 2015. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-14 | 2017-02-14 | Rome, City of (Rome WRF) | Floyd |  | Southeast Rome Intersection of E 7th Street and Lee Avenue | 2400 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Kevin Dallmier | Kathy Lewis | Tracy Feltman | 2/15/2017 12:00:00 AM | Coosa |  |  |  | 0 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease in the sewer main | The sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-30 | 2015-03-30 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 34.0 mg/l
2017-08-15 | 2017-08-15 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 370 Wavetree Drive | 3540 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 8/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Drive | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-17 |  |  | DeKalb |  | 2190 Meadowfliff Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pump was checked and flow was restored |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-12 | 2016-11-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3188 Paces Ferry Place, NW, Atlanta | 805 | Fax received on 11/13/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/13/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the main line. | Hydraulic pressure cleaner was used to contain the spill |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-06-09 | 2017-06-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2585 Chantilly Dr. NE - ATL | 4020 | Email received 2017-06-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/12/2017 12:00:00 AM |  | 6/9/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-12 | 2018-02-12 | Adairsville, City of (North WPCP) | Bartow |  | 105 Holcomb Drive | 600 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Hydraulic Overload |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/12/2018 12:00:00 AM | Coosa |  |  |  | 0 | Oothkalooga Creek Tributary to the Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Major inflow and infiltration problems | Physically inspect every sewer manhole within the city sewer system and document the following conditions on the city's GIS sewer mapping software. Begin manhole surveys in the low lying areas. As defective manholes are found repair them. Compile an accurate sewer map accessible through the city's GIS. Continue with the flow monitoring effort to isolate the problem areas. When suspect sewer zones are identified, employ smoke testing to locate specific sources of inflow. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-23 | 2016-09-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 2404 Cragstone Court, Lithonia | 3120 | Notification received on September 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/23/2016 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected on September 23, 2016 at 17:20 hours when a crew rodded the 8" sewer main 210ft upstream, cleared the blockage at 189ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-27 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 7850 Old Covington Hwy, Lithonia | 195800 | Notification received on December 31, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | Pine Mountain Creek to Yellow River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 20:15 hours, when the rain subsided and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-03 | 2016-08-03 | Rome, City of (Rome WRF) | Floyd |  | Armuchee Community Approximately 600 ft northeast of the end of Leanna Street | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 8/4/2016 12:00:00 AM | Coosa |  |  |  | 0 | Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage caused by roots in the sewer main | The sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-02 | 2015-01-02 | Cobb County MS4 | Cobb |  | 664 Ashley cir. | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 inch PVC Main | cleaned spill area and spread lime | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-14 | 2018-08-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 815 Peachtree Battle Ave. NW - Atlanta | 1000 | Fax sent 2018-08-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Shoreline | Equipment failure |  |  | Alys Hannum | Alys Hannum | 8/15/2018 12:00:00 AM |  | 8/14/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment Failure | Crew made repairs to the by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-05 | 2017-10-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2351 South Hairston Road, Decatur | 460 | Notification received on October 9, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/5/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:49 hours by pressure washing the 8" sewer main upstream 100-ft, removing the grease blockage at 90-ft and restoring normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-17 | 2016-06-17 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Influent Lift Station | 4000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/17/2016 12:00:00 AM | Satilla |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Outage | The backup generator was startedand the pumps cleared the station. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-04 | 2017-06-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2595 Woodward Way. NW - ATL | 1500 | Email received 2017-06-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/5/2017 12:00:00 AM |  | 6/4/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was rain-induced. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-09 | 2015-01-09 | Cobb County MS4 | Cobb |  | 4351 Clairesbrook LN | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Gravel in 8 in PVC Main | The crew stopped the spill at 19:15 hrs. and washed down road. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-18 | 2017-10-18 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 528 Bridge Ave, Forest Park Manhole: 2205275 | 4800 | Fax received on 10/19/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/19/2017 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-20 | 0 | 1 | 1 | 0 | 0 | 0 | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2015-04-02 | 2015-04-02 |  | Cobb |  | 1306 Old Powder Springs Rd. | 430 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Cobb Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease in 8" Clay Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-09 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Lift Station #100, Albany. | 82200 | Email and telephone calls received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Lift Station | Stream |  | Power failure |  | Paul Moisan |  | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Flint River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The National Weather Service reported 8 - 9 tornadoes, plus straight line winds resulting in power loss to 52 storm and sanitary lift stations. | Full power to all lift stations was restored on 01/14/2017. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2016-08-09 | 2016-08-09 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | Woodridge Rd. SW near the Carlton Woods Lift Station, Moultrie | 4000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System | Ground |  | Power failure |  |  | Dagny Pariani | Dagny Pariani | 8/12/2016 12:00:00 AM | Ochlockonee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A brief power outage at the lift station resulted in a manhole overflow nearby. | Maintenance personnel reset the pumps, putting the LS back online. Spill was contained at the site, area was cleaned and limed. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | Elvira Gibson | 229-890-5432 | City of Moultrie
2016-11-13 | 2016-11-13 |  | Henry | Hampton |  | 1000 | Did not overflow to waters of the State. | Raw Sewage |  |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/13/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A six-inch service line had a break in it. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-09 | 0 | 0 | 0 | 0 | 0 | 0 | John Spraggins | 770-946-3234 | CITY OF HAMPTON
2015-03-20 | 2015-03-20 |  | Columbia |  | 3990 Dowling Drive | 7200 | fax received 3/20/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/20/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Stream bank erosion | Repaired break in sewer pipe. Performed temporary stream bank stabilization. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2017-01-23 | 2017-01-23 | Fulton County MS4 | Fulton |  | 305 Hamilton Park Drive | 4200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Stopped Spill | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-16 | 2015-11-16 | Rome, City of (Rome WRF) | Cherokee |  | City of Romes Big Dry Creek Lift Station in the 2600 Block of Hwy 27 North | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Equipment failure |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 11/17/2015 12:00:00 AM | Coosa |  |  |  | 0 | Big Dry Creek leading to the Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This spill was caused by bolts rusting out of a valve body resulting in the top separating from the valve. | The Valve was replaced | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2017-12-21 | 2017-12-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1961 Jabco Boulevard, Lithonia GA30058 | 4410 | m/h 16-123-s005 discharging into Branch Creek | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/21/2017 4:59:00 PM | Ocmulgee | 12/21/2017 12:00:00 AM |  |  | 1 | Branch Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Pressure washed | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-22 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Marcus Challenger |  | Dekalb Co Dept. Watershed Management
2017-08-02 | 2017-08-02 | Patterson, City of (Patterson WPCP) |  |  | Dallas Street | 1000 |  | Raw Sewage | Coastal District | GA0037206 | Pump Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 8/3/2017 12:00:00 AM | Satilla | 8/2/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary to Patterson Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power due to a tree falling on the power lines which supplies power to the Dallas lift station. | The tree was removed and power was restored to the lift station. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-08-10 | 1 | 1 | 0 | 0 | 0 | 0
2017-07-22 | 2017-07-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5083 Biffle Road, Stone Mountain | 289320 | Notification received on August 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  |  |  |  | Hsin Yeh | Hsin Yeh | 7/27/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:30 hours when a first responder crew pressure washed the 8 inch sewer main 300 feet, removed the grease blockage at 130 feet, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-24 | 2016-10-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4347 Flat Shoals Parkway, Decatur | 15 | Notification received on October 28, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 10/25/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Outside Contractor/Utility | The problem was corrected at 14:30 hours, when the contractor re-plugged the 30" sewer main and placed the by-pass pump at the damaged manhole to alleviate the overflow and continue the repairs. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-31 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-10 | 2016-03-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2979 Deleher Court, Atlanta | 150255 | Notification received on March 15, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/11/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 11:03 hours, on March 11, 2016 when a crew built a 5x20 berm around the broken 12" main to contain the spill, restored normal flow until the repair was completed at 19:00 hour. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-22 | 2015-10-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2717 Hedgewood Drive, NW | 58650 | fax received 10/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/23/2015 12:00:00 AM |  |  | 2015-10-23 | 2016-11-13 | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | debris and collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-09 | 2017-08-09 | Fulton County (Big Creek WPCP) | Fulton |  | 0 Whitewater Creek Road Atlanta 30327 | 76060 | Major SSO A demand letter is required as part of the CMOM Agreement. | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flash Flood of Long Creek | Ongoing I/I Reduction Program | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-21 | 2016-03-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1680 Westview Drive, SW | 3990 | fax received 3/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/22/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-01 | 2016-02-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 253 Scott Street, NW | 13950 | fax received 2/02/2016. CTS No. 78946 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/2/2016 12:00:00 AM |  |  | 2016-02-06 | 2017-02-23 | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-26 | 2018-04-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 294 pine tree circle, Decatur GA 30032 | 28960 | spilling manholes 15-260-s026 and 15-250-s022 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/27/2018 5:38:00 PM | Ocmulgee | 4/27/2018 12:00:00 AM |  |  | 1 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | grease | pressure washed from private manhole 15-250-p023 to manhole 15-250-s026 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-17 | 2017-10-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1753 Dodson Dr. SW - ATL | 2000 | Fax sent 2017-10-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/19/2017 12:00:00 AM |  | 10/17/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline. | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-27 | 2016-10-27 | Cobb County Water System | Cobb |  | 2087 Fairpot Way | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/31/2016 12:00:00 AM | Unknown |  |  |  | 0 | Sope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris (gravel) in 8" Clay Main. | Flushed and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-13 | 2016-06-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2319 Doreen Court, Atlanta | 980 | Notification received on June 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/14/2016 12:00:00 AM |  |  |  |  | 0 | North fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots | The problem was corrected at 12:10 hours, when a crew pressure washed the sewer main 187ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-16 | 2015-09-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2039 Wells Drive, SW | 7480 | fax received 9/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/17/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-18 | 2016-02-18 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Between Harrington Dr and Hancock St | 17490 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Pipe failure |  |  | Dagny Pariani | Dagny Pariani | 2/18/2016 12:00:00 AM | Oconee | 2/18/2016 12:00:00 AM | 2016-02-18 |  | 1 | Fishing Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Erosion of soil from around the pipe caused the pipe to break | Replaced the 8" pipe, built a berm, hauled off contaminated soil, spread lime, and filled in the creek bank. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-19 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2017-03-04 | 2017-03-04 | Cobb County Water System | Cobb |  | 3371 Johnson Ferry Road/Chimney Lake Drive | 300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/4/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Chimney | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Tifton, City of (New River WPCP) | Tift | Tifton | Gum Creek, Tifton 31.410309, -83.473827 | 8400 | Email received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Gum Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall event on April 1-2, 2016. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 1050000 | CTS No. 78262 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-24 | 2015-01-24 |  | DeKalb | Tucker | 3924 Roman Court, Tucker | 3080 | Notification received on January 26, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 1/25/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A broken 8" sewer main due to an uprooted tree. | The problem was corrected at 16:04 hours when a crew contained the sewer spill from getting into the creek, repaired the sewer line, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-24 | 2017-01-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1516 Northwest Dr NW - ATL | 10 | Fax received on 01/25/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan |  | 1/25/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-12-17 | 2015-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 831000 | CTS No. 78538 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/16/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Overflow from the Intrenchment Creek WRC due to hydraulic overload |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-02 | 2015-11-02 | Thomasville, City of (Oquina Creek WPCP) | Thomas | Thomasville | The overflow location was at the corner of Chatam Drive and Glenwood Drive, where the pipe crosses Oquina Creek. | 148000 | Jim Ridley (Superintendent, Thomasville Wastewater Treatment) called Paul Moisan on 11/02/2015 to advise him of the situation | Raw Sewage | Wastewater Regulatory Program | GA0024082 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/2/2015 12:00:00 AM | Ochlockonee | 10/24/2016 12:00:00 AM | 2016-10-24 | 2017-10-24 | 1 | Oquina Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | A pipe support failed under a pipe, located at Chatam Drive and Glenwood Drive. This caused a spill into Oquina Creek by the failed support, and the gravity fed raw sewage. | The line was temporarily plugged as reparis were made. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-03 | 1 | 1 | 0 | 1 | 1 | 0
2017-01-02 | 2017-01-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1908 Delowe Pl, SW, ATL | 3350 | Fax received on 01/04/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/4/2017 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the service lateral. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-03-03 | 2015-03-03 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | Hamilton Rd/Hwy 27 South Mile Marker 13 | 1460 | REC FAX 3/3/2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Force Main | Stream | Stream | Pipe failure |  |  | Emily Wingo | Sarita Banjade | 3/3/2015 12:00:00 AM | Chattahoochee | 3/3/2015 12:00:00 AM |  |  | 1 | Long Cane Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 10" force main split along bottom allowing sewer to escape. | 20' section of 10" force main replaced. |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-04 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LAGRANGE | 706.883.2010
2017-05-01 | 2017-05-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3752 Salem Springs Court, Lithonia | 11250 | Notification received on May 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Hsin Yeh | 5/1/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | The problem was corrected at 11:31 hours when a crew used the vactor truck to vacuum down the wet well to contain the spill, rewired the generator, powered up the station and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Warner Robins, City of (Sandy Run Creek WPCP) | Houston | Warner Robins | Hawaii Drive, Warner Robins | 12000 | Notification received on February 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0030325 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/9/2016 12:00:00 AM |  |  |  |  | 0 | Sandy Run Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failure of a concrete plug in the collections system. | The major sewage spill, of approximately 12,000 gallons, occurred as a result of the failure of a concrete plug in the collections system leading toa manhole hat was not in service on the afternoon of Thursday February 4, 2016. The release was discovered by a City of Warner Robins crew during routine I/I inspections at approximately 11:00 am Thursday February 4, 2016. The spill was stopped by 7:00 pm on the same day. The spill entered an unnamed tributary near the manhole. The manhole and the sewer lines leading to it were properly abandoned to prevent this from happening again the future. The area of the spill was cleaned and limed. The signs have been posted, sampling started and public notifications have been made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-11 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-10 | 2017-09-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 4198 Oak Crest Drive, Tucker | 3825 | Notification received on September 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 9/11/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 20:43 hours when a first response crew pressure washed the 10(in) sewer main 80ft and removed the debris blockage at 78(ft), which restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-27 | 2015-06-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 757 Woodward Way, NW | 3 | fax received 6/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 6/29/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-03 | 2017-04-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 584 Tarragon Ct. SW - ATL | 2200 | Fax received 2017-04-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/4/2017 12:00:00 AM |  | 4/3/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2530 17th Street., Columbus, GA | 39294 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rainfall subsided, flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-09 |  |  | DeKalb |  | 4776 Snapfinger Woods Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Cleaned out debris and grease to restore flow in manhole |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-05 | 2015-02-05 |  | DeKalb | Dunwoody | 4101 Dunwoody Club Drive, Dunwoody | 1320 | Notification received on February 6, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 2/5/2015 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 16:29 hours when a crew rodded the sewer main 30ft unblocked the sewer line and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-29 | 2016-01-29 | Columbia County (Crawford Creek WPCP) | Columbia | Evans | 709 Michaels Creek | 6000 | fax received 1/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 1/29/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Jones Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | unstopped sewer main with high pressure jet machine. Cleaned spill area, spread lime, and posted signs. Planned followup video inspection. Took sample of creek. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-12-30 | 2016-01-02 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | City of Social Circle - Little River WPCP, 167 Vine Circle | 1637295 | CTS No. 78693 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Due to hydraulic overload of the WPCP, shut down aerators and mixers at middle of aeration basin. Started diesel pump to handle flow. When flow subsided, started motors in basin. Shut down diesel pump. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-02-23 | 2016-02-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 42 Karland Drive, NW | 10 | fax received 2/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/24/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-07 | 2018-02-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1860 Childress Dr. SW | 94 | Fax sent 2018-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-26 | 2017-01-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3310 W. Roxboro Rd. NE - ATL | 3204 | Fax received on 01/27/2017. Update 8/22/17 - Location changed from 1079 W. Roxboro Dr. NE to 3310 W. Roxboro Rd NE., volume changed from 10 to 3,204 as per fax received 8/21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/27/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | The crews made repairs to the mainline to contain the spill |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 312 Cascade Court | 7441 | REC CALL 2/26/2015. REC FAX 2/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | Rags |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/27/2015 12:00:00 PM | Chattahoochee | 2/27/2015 12:00:00 AM |  |  | 1 | Chattahoochee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump station stopped up due to rags in the sewer system causing a manhole to overflow into the river. | Once the rags were cleared and the pumps back online the overflow stopped. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-02 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Columbus Water Works | 706-649-3490
2016-03-17 | 2016-03-17 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 6808 Brookwood Ct, Douglasville WSA Manhole 7977 | 450 | Fax received on 03/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 3/18/2016 12:00:00 AM | Chattahoochee | 3/17/2016 12:00:00 AM |  |  | 1 | Knollwood Branch Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks and debris in line. | VacCon crews were dispatched to the site and a jet truck was used to clean the line and clear the blockage. Crews cleaned and disinfected the area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-21 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-08 | 2015-06-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1771 Valley Ridge Drive, SW | 550 | fax received 6/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-05 | 2017-04-06 | Fulton County (Big Creek WPCP) | Fulton |  | Azalea Drive Roswell, GA 30075 | 282758 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 4/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chatthoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ongoing I/I Reduction Program |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-23 | 2017-02-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3388 Garden Mill Lane, Ellenwood | 1700 | Notification received on March 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/23/2017 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 15:00 hours when a crew pressure washed the 8" sewer main between manholes 300ft, removed the blockage at 100ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-02 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Glenwood Ave. SE - ATL | 665 | Fax sent 2018-02-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/5/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 |  | Colquitt | Moultrie | Carlton Woods Lift Station | 36000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  |  | Reginald Williamson | Reginald Williamson | 2/8/2017 12:00:00 AM | Ochlockonee |  |  |  | 0 | Ochlocknee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage at the lift station, caused by a major thunderstorm. |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-28 | 2016-08-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3593 Adkins Road, NW | 1 | fax received 8/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Operator error |  |  | Kim Hembree | Kim Hembree | 8/29/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "The spill was caused by the city crew jet rodding the mainline" |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-28 | 2017-02-28 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3637 Monmouth Rd - Augusta | 21000 | Email received after business hours 2017-02-01. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Rags |  |  | Alys Hannum | Alys Hannum | 3/1/2017 12:00:00 AM |  | 2/28/2017 12:00:00 AM | 2017-02-28 |  | 1 | Tributary to Butler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Overflow was due to large amounts of rags and debris in the line causing a blockage. | Gravity main was augered to relieve the pipe of debris. After flow stabilized, downstream segments were augered to prevent any rags and debris from causing a blocking. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-16 | 2016-06-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1265 Woodland Avenue, SE | 7200 | fax received 6/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/17/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and partially collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-21 | 2017-02-21 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1060 Scott St. | 2040 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/21/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Clean Piping | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-10 | 2016-07-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3186 Buford Hwy, Atlanta | 1325 | Notification received on July 11, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 7/10/2016 12:00:00 AM |  |  |  |  | 0 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 14:33 hours when a crew pressure washed the sewer main, cleared the blockage, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-11 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-12 | 2015-01-12 | Cobb County MS4 | Cobb |  | 4388 Clairesbrook Lane | 90 |  | Raw Sewage | Mountain District - Cartersville |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in sewer main causing the manhole to overflow. | The Water System was notfied at 2:14 p.m. and crews stopped the overflow at 3:00 P.M. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-26 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | Manhole 417 at Hwy 82 and Don Foster Rd | 5760 | Manhole weeping at this location is a recurring issue. | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 2/24/2016 12:00:00 AM | Flint | 2/24/2016 12:00:00 AM |  |  | 1 | Brantley Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3" of rain on already saturated ground caused the manhole to weep at ~2gpm for 24 hrs, followed by ~1gpm for 48 hrs. | Area cleaned and limed as needed. Creek monitoring. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Dawson
2018-05-15 | 2018-05-15 | Savannah, City of (President Street WRF) | Chatham | Savannah | 23 Wright Street, Savannah, GA | 3450 | Initial phone call and full report emailed 5/15/2018. | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain, Stream | Canal | Equipment failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 5/15/2018 12:00:00 AM | Savannah | 5/15/2018 12:00:00 AM |  |  | 1 | Dundee Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A manhole collapse upstream resulted in sand and grout plugging the gravity sewer line downstream. | Used vac truck to clean sewer line of debris. Also set up a berm to contain the spill and cleaned the site. Contractor will repair manhole. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-05-18 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-25 | 2017-05-25 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 220 King Street - Jonesboro MH - 2216134 | 1800 | Fax received on 05/26/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 5/26/2017 12:00:00 AM | Flint |  |  |  | 1 | Rum Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Once the blockage was cleared, flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-30 | 0 | 1 | 1 | 0 | 0 | 0
2017-03-03 | 2017-03-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 2836 Thornbriar oad, Doraville | 3200 | Notification received on March 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/4/2017 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:24 hours when a crew pressure washed the 8" sewer main between manhole 150ft, removed the blockage at 120ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-21 | 2017-08-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 98 Anderson Ave. NW | 206 | Fax received 2017-08-21 EDIT: This is a private spill, not public, as per fax received 2017-08-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/22/2017 12:00:00 AM |  | 8/21/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-10 | 2015-01-10 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 7 Collier Lane NW | 6 | fax received 1/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Roots |  |  | Kim Hembree | Kim Hembree | 1/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-13 | 2015-11-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3185 Panther Trail, SW | 3060 | fax received 11/14/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/14/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-11-28 | 2017-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Wy. SW - ATL | 1043 | Fax sent 2017-11-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/29/2017 12:00:00 AM |  | 11/28/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-11 | 2016-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2000 Delowe Drive, SW | 195 | fax received 1/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/12/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1331 Reynolds Street | 21600 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Mid-City | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2017-02-24 | 2017-02-24 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 128 Webb Street | 3560 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/24/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Failure | spilled stopped | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-09 | 2015-04-09 | Tifton, City of (New River WPCP) | Tift | Tifton | Central at 8th Street | 5000 | REC CALL 4/9/2015. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Storm Drain | Ditch | Debris |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/9/2015 12:00:00 AM | Suwannee | 4/9/2015 12:00:00 AM |  |  | 1 | New River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Clear blockage and clean area | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-09 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Murphy | 912-281-4186 | ESG Operations, Inc. | [5 empty] | CITY OF TIFTON
2015-06-06 | 2015-06-07 | Forsyth County (Fowler WRF) | Forsyth |  | 5890 Spring Box Drive | 300 | fax received 6/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038695 | Collection System | Ground |  | Contractor |  |  | Kim Hembree | Kim Hembree | 6/8/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor hit line | replaced pipe and couplers |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Forsyth County
2017-05-24 | 2017-05-24 | Rome, City of (Rome WRF) | Floyd |  | Bells Ferry Road Lift Station | 47000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 5/26/2017 12:00:00 AM | Coosa |  |  |  | 1 | Dozier Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Ruptured force main | Replacement of 110 feet of 16" | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2162 Montrose Ave. SW - ATL | 7 | Originally reported with "This is not a city problem." Update 8/25: This is a public city spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 2/16/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Update 8/25: Grease in the mainline | Update 8/25: Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-04 | 2015-03-04 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 3563 Meadowview Dr. | 800 | REC EMAIL 3/4/2015. REC FAX 3/6/2015. REC WRITTEN REPORT 3/13/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Force Main | Stream | Stream | Equipment failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 3/4/2015 6:18:00 PM | Chattahoochee | 3/5/2015 12:00:00 AM |  |  | 1 | Unnamed Tributary to Dry Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | failure of an air release valve on a sewer forcemain from our Meadowview Lift Station | Pump the air release valve manhole out and stop the spill by closing the isolation valve. Crews cleaned and disinfected the area around the manhole where the spill occurred. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-03-05 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Douglasville-Douglas County Water and Sewer Authority | 770-949-7617
2015-06-22 | 2015-06-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 434 Cologne Drive, SE | 5530 | fax received 6/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/23/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-25 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | Manhole 417 at Highway 82 and Don Foster | 8640 |  | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Storm Drain | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/25/2015 12:00:00 AM | Flint | 12/24/2015 12:00:00 AM | 2015-12-24 |  | 1 | Brantley Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5.25 inches of rainfall to already water saturated area | Area cleaned and limed. Creek monitoring underway. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Dawson
2018-04-15 | 2018-04-15 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 4466 Pipemaker Bluff, Douglasvillem, GA 30135 | 21600 | Email received on 04/16/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038709 |  | Stream |  | Debris |  |  | Hsin Yeh | Paul Moisan | 4/16/2018 12:00:00 AM |  |  |  |  | 0 | Anneewakee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shovel in the manhole | VacCon Crews were dispatched to the site and cleared the blockage to stop the spill. Crews cleaned and disinfected the area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-04-25 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-12 | 2017-08-12 | Cobb County Water System | Cobb |  | 4620 Hickory Run Court | 230 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/12/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clark Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-17 | 2016-02-17 |  | DeKalb | Dunwoody | 2382 Dunwoody Crossing, Dunwoody | 1135 | Notification received on February 19, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/17/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | the problem was corrected at 17:32 hours, when a crew built a dirt berm around pipe to contain the spill and restored normal flow until the repair is completed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-25 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-20 | 2017-12-21 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1214 South Dixie Hwy Dalton | 6060 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Unknown |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 12/21/2017 12:00:00 AM | Coosa |  |  |  | 0 | Tar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown blockage in collection system | Cleared line with jet truck and utilized vacuum trucks for cleanup | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-12-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-07 | 2018-03-07 | Clayton County (Northeast WPCP) | Clayton | Jonesboro | 8050 Tara Blvd, Jonesboro | 2800 | Fax sent 2018-03-08 | Raw Sewage | Wastewater Regulatory Program | GA0020575 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Paul Moisan | 3/8/2018 12:00:00 AM |  |  |  |  | 1 | Jester Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-08 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-01 | 2016-06-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1094 Stonewall Drive, SE | 570 | fax received 6/02/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/2/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-17 | 2015-03-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3581 Revere Road, SW | 150 | fax received 3/18/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/18/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-30 | 2015-01-30 |  | Fulton |  | 4655 Campbell Dr. East Point, GA | 400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. They are impacted by the spill has been cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-14 | 2016-01-14 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3155 Pio Nono Ave, Macon MH ID #56866 | 960 | Email and fax received 01/15/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/15/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. There is a commercial source of grease upstream from this location and residential grease is not regulated. | Debris was removed from the area. This line is scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly Hot Spot Inspection List. This report was forwarded to the Grease Management Program Coordinator and the commercial source upstream passed its most recent inspection. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-15 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-25 | 2016-03-25 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 1247 Candler Ct., Morrow | 800 | Fax received on 03/26/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 3/26/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-13 | 2017-07-13 | Habersham on Lanier WPCP | Forsyth |  | Habersham #2 Wastewater Pump Station 1950 Buford Dam Road Cumming | 1200 | The area that was affected by the spill has been cleaned up, lime has been applied, and signage has been posted at the affected area. | Raw Sewage | Mountain District - Cartersville | GA0030261 | WWTP | Stream |  | Equipment failure |  | Mick Smith | Kathy Lewis | Eric Dykes | 7/13/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Lake Lanier | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump Failure |  | 4265e0af-00af-4b96-982e-53f807bc3994 | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-30 | 2015-04-30 |  | DeKalb | Decatur | 1666 West Caribaea Trail, Decatur | 500 | Notification received on May 7, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/30/2015 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blocakge | The problem was corrected at 18:10 hours when a crew pressure washed the 12" sewer main upstream 75ft, cleared the blockage, dug a pit to reroute sewage to flow back into sewer main line and restored services. A full investigation revealed pipe defect/separation; repair of sewer is scheduled. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-05-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 |  | Henry | Stockbridge | 100 Stapleton Dr. Stockbridge GA 30281 | 8250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/23/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration from an alreay saturated ground Received 2 inches of rain. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 1510000 | Verbal notification received 1/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/15/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-30 | 2017-09-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2164 Faulkner Rd. NE - ATL | 255 | Email received 2017-10-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/1/2017 12:00:00 AM |  | 9/30/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a bypass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-04 | 2017-10-04 | East Point (City of)- Sewers | Fulton | East Point | 3900 N. Commerce Drive | 9150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/4/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Diapers | Details in Report | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-31 | 2018-01-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2081 Brewer Blvd. SW - ATL | 100 | Fax sent 2018-02-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/1/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-06 | 2018-02-06 | Clayton County (Northeast WPCP) | Clayton | Forest Park | Hwy 75 South, Forest Park | 8100 | Fax sent 02/07/2018. | Raw Sewage | Wastewater Regulatory Program | GA0020575 | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Paul Moisan | 2/7/2018 12:00:00 AM |  |  |  |  | 0 | Mud Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Blockage was cleared and flow returned to normal. Site was mitigated work orders generated for debris removal out of manhole. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-12 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-11 | 2015-08-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4103 Wesley club Drive, Decatur | 720 | Notification received on August 13, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/13/2015 12:00:00 AM |  |  |  |  | 0 | Cobb Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris blockage | The problem was corrected at 13:27 hours, when the clean-up crew removed the debris, rodded, pressure washed the sewer main and restored regular services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-18 | 2016-01-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 451 Sawtell Avenue, SE | 350 | fax received 1/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/19/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-14 | 2017-09-14 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Lift Station #12 @ HWY 80 and Fortune Loop - Swainsboro | 200 | Phone call received 2017-09-14 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Pump Station | Ground |  | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/15/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outages due to Hurricane Irma also caused the alarm call-out system to fail. | Emergency generator was activated. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-15 | 2016-11-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 156 Moury Ave, SE, ATL | 1005 | Fax received on 11/16/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/16/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-17 | 2017-04-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3156 East Wood Valley Rd. NW - ATL | 6 | Fax received 2017-04-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 4/18/2017 12:00:00 AM |  | 4/17/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-09 | 2018-02-09 | Cobb County Water System | Cobb | Marietta | 1000 McCollum Pkwy | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/9/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Noonday Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 1:31 p.m. and our crew stoppped the overflow at 4:25 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-27 | 2018-03-27 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1312 Peggy Lane | 200 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/27/2018 12:00:00 AM | Upper Ocmulgee |  |  |  | 0 | Travers Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Removed Roots | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-15 | 2016-02-15 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | Bemiss Road | 1450 | Verbal notification received 2/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/15/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage from cement block placed in manhole | Block removed, area cleaned and limed | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-04-17 | 2015-04-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1115 Princess Avenue, SW | 200 | The crew used a hydraulic pressure cleaner to contain the spill. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/17/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-10 | 2017-03-10 | Greenville, City of (Kennel Creek WPCP) | Meriwether |  |  | 0 |  | Raw Sewage | West Central District | GA0047813 | Lift Station | Ground | N/A | Grease |  | Stephanie Edwards | Tilden Bembry | Stephanie Edwards | 3/10/2017 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 426838fe-eb6e-11e0-b8d8-000c29971acc | 426838fe-eb6e-11e0-b8d8-000c29971acc | 488bfc66-eb6e-11e0-b8d8-000c29971acc | 2017-03-22 | 1 | 0 | 0 | 0 | 0 | 0
2017-11-07 | 2017-11-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3547 Buford Highway Atlanta GA 30329 | 5680 | Manhole 18-202-s113 overflowing and getting into the storm drain Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/7/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Fork Peachtree Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Pressure washed sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Conelius Williams |  | Dekalb County Department of Watershed Management
2018-03-14 | 2018-03-14 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 269 W Wynngate Dr. - Martinez | 9000 | Fax sent 2018-03-15 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Contractor |  |  | Alys Hannum | Alys Hannum | 3/15/2018 12:00:00 AM |  | 3/14/2018 12:00:00 AM |  |  | 1 | Boulder Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor Damage | Sewer was bypassed to limit the overflow. Once bypass was underway, the main was excavated and necessary repairs were made. Lime was spread, signs have been placed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-06 |  | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | 1171 4th St. SW Moultrie | 2000 | In the attached document, date of spill indicates February 6th, 2016 when it should be 2018 | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System | Ground |  | Equipment failure |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/6/2018 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Backed up sewer line with a hole in a joint that allowed sewage to escape | Release contained and treated with lime | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1020 Barnett Shoals Rd., Athens | 22080 | Initial call 11/3, full report faxed 11/4 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Oconee | 11/2/2015 12:00:00 AM | 2015-11-02 |  | 1 | North Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | overflow due to flooding during major rain event | sewer upgrade is under design |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-04 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1176 Garibaldi Street, SW | 465 | fax received 2/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-24 | 2016-08-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3050 Martin Luther King Jr. Drive, SW | 15 | fax received 8/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/25/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The spill was self contained. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-07 | 2018-05-07 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 5978 Reynolds Drive | 8100 | Fax received on 5/8/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 5/8/2018 12:00:00 AM |  |  |  |  | 0 | East Jester's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-14 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-25 | 2016-10-25 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Stockbridge | 437 Grove Hill Drive, Stockbridge | 9600 | Fax received on 10/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 10/25/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Big Cotton Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage, flow returned to normal. Work orders generated for additional work (CCTV, etc.). |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-05 | 0 | 0 | 0 | 0 | 0 | 0 | Billy Vondenbosch |  | CLAYTON COUNTY WATER AUTHORITY
2016-08-01 | 2016-08-01 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Hinesville |  | 6000 |  | Raw Sewage | Coastal District | GA0047180 | Force Main | Ground, Storm Drain, Stream | Ditch | Equipment failure |  | John Kalp | John Kalp | John Kalp | 8/1/2016 1:15:00 PM |  | 8/1/2016 12:00:00 AM |  |  | 1 | Tributary of Mill Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | yes | 0 | the failure of an 8-inch sanitary force main for lift station 1591 located at the intersection of Sigma St. and Crisp Ave on Fort Stewart. This caused approx. 17550 gallons of raw sewage to be released of which 6000 gallons discharged into a stormwater conveyance system that flows to a tributary of Mill Creek. See full writ-up in comments section | See comments section | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2016-08-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Savannah, City of (Georgetown WPCP) | Chatham | Savannah | 1000 Fords Point Circle, Savannah, GA | 4500 |  | Raw Sewage | Coastal District | GA0046418 | Collection System | Storm Drain, Stream | Stream | Natural Disaster |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM | Ogeechee | 10/9/2016 12:00:00 AM |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station transfer failure and power outage during Hurricane Matthew. Overflowing manhole as result. | Restored power and repaired transfer switch. Cleaned area with vac truck. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-26 | 2016-09-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2479 Abner Terrance NW | 1995 | fax received 9/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/27/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-22 | 2017-01-23 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Argonne Drive (2 Manholes) - Augusta | 4260 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County Area. | Will assess the system via flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-04 | 2015-11-04 | Fulton County (Johns Creek Environmental Campus) | Fulton |  | 5795 McClure Rd. Union City, GA 30213 | 83250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-26 | 2018-08-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2362 Dellwood Dr. NW - Atlanta | 10 | Fax sent 2018-08-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum |  | 8/27/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-11 | 2015-03-11 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1770 Richmond Avenue, SE | 1544 | Fax received 3/12/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-30 | 2018-04-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1110 Spring St. NW - Atlanta | 193 | Fax sent 2018-05-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/1/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-23 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Fort Stewart-Hinesville |  | 10500000 |  | Raw Sewage | Coastal District | GA0047180 | WWTP | Stream | Stream | Wet weather |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 1/22/2017 3:38:00 PM | Ogeechee | 1/23/2017 12:00:00 AM | 2017-01-22 | 2018-01-22 | 1 | Taylor Creek to Canoochee | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 |  | 0 | Due heavy rainfall. |  | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-01-30 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-08 | 2017-09-08 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2034 Napier Avenue, Macon MH ID 56500 | 3410 | Telephone call received on 09/12/2017; fax and email received on 09/14/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain | Shoreline | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/14/2017 12:00:00 AM | Ocmulgee | 9/8/2017 12:00:00 AM |  |  | 1 | Riverside | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Grease was removed from the area, and the area was disinfected with lime. Flow returned to normal. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-29 | 2018-04-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1540 Walnut Ridge Court, Stone Mountain GA 30083 | 660 | manghole 15-192-s259 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/29/2018 11:48:00 AM | Ocmulgee | 4/29/2018 12:00:00 AM |  |  | 1 | Snapfiger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown blockage | Presure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-17 | 2017-07-17 | Marietta (City of)- Sewers | Cobb | Marietta | 605 Commerce Park Dr. | 2100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Marietta Water personnel quickly repaired the damage pipe thus restoring normal service. This pipe is monitored regularly during our easement clearing program. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1235 Plaza Avenue, SW | 30 | fax received 2/27/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/27/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-12 | 2017-02-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2438 1st St. NW - ATL | 100 | Fax received 2017-02-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/13/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Spill was self-contained. The process to clean and disinfect the site has been initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-28 | 2017-05-11 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2840 Pierce Drive, South - Macon MH ID 64562 | 444168 | Telephone call, and Report received on 05/25/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Ditch | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 5/25/2017 12:00:00 AM | Ocmulgee | 5/24/2017 12:00:00 AM | 2017-05-22 |  | 1 | Unnamed tributary feeding Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was grease. | The maintenance department is reprogramming the SCADA system to indicate an alarm when pumps are not pumping at normal operating levels. Grease was removed, and flow returned to normal. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-07-23 | 2017-07-26 | Hinesville, City of (Peacock Creek WPCP) | Liberty | Hinesville |  | 0 | It was estimated that approximately 12,300 gallons of reuse water had backed up and flowed out of the UV station and onto the facility grounds. The motor to the second pump was replaced the next day, July 24th. No evidence was observed that would indicate this discharge left the site or entered states waters. | Undisinfected Primary Effluent | Coastal District |  | WWRF | Ground | N/A | Equipment failure |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 7/24/2017 6:30:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The operator returned to the WRF and upon arrival at approximately 1325, he immediately noticed both effluent pumps had pump fail alarms and effluent well high level alarm. | He immediately tried to reset and place the effluent pumps back in service but the pumps failed to reset directly, so he manually started rejecting flow to the reject pond. After evaluating the effluent pump problem, the operator was able to put one effluent pump back in service. | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-07-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-31 | 2017-05-31 | Newton County (Yellow River WPCP) | Newton | Oxford | Outfall beside 83 Gum Creek Trail | 7400 | Call received 2017-05-31; email received 2017-06-01 | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream | Stream | 3rd party contractor |  | Alys Hannum | Alys Hannum | Alys Hannum | 5/31/2017 12:00:00 AM |  | 6/1/2017 12:00:00 AM |  |  | 1 | Tributary to Beaverdam Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole was damaged by unknown vehicle | Jetted lines to free blockage and removed debris from damaged manhole. Manhole will be repaired. Lime will be spread on affected area. Caution signs with spill information will be placed downstream in areas of public access. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-12 | 2018-02-12 | Norman Park (Norman Park WPCP) | Colquitt | Norman Park | Treatment plant outfall into Reedy Creek. | 0 | All public notice has been received. | Treated Effluent | Southwest District | GA0033600 | WWTP | Stream | Stream | Other |  | Jay Howell | Jenna Detar | Jenna Detar | 2/12/2018 10:00:00 AM | Suwannee | 2/13/2018 12:00:00 AM | 2018-03-13 |  | 1 | Reedy Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Rising sludge in the clarifier exited the plant at the outfall into the receiving creek. | Improved sludge wasting schedule. Contacted engineer to discuss upgrading treatment plant. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2018-04-10 | 1 | 1 | 1 | 0 | 0 | 0 | Bruce Norton |  | City Norman Park | [8 empty] | 0 | 0
2016-04-02 | 2016-04-02 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Canal crossing at 1300 block of Westwood Alley, Albany. Westwood Alley & Partridge | 10000 | An email was received on 04/03/2016, and a report was received on 04/12/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 4/3/2016 12:00:00 AM |  |  |  |  | 1 | Percosin Canal Tributary to Cooleewahee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | The cause of the backup was due to a buildup of debris in the pipes. | a jet truck was used to free the blockage from the sewage pipes. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-07 | 2016-01-07 | Cobb County (South WPCP) | Cobb |  | 5520 Gravel in 8 inch Clay Main | 5520 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8 inch Clay Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-27 | 2015-04-27 | Cobb County MS4 | Cobb |  | 3295 Shadowridge Drive | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the sewer main causing the manhole to overflow into a tributary of Olley Creek. | The Water System was notified at 5:32 p.m. and our crew stopped the overflow at 6:47 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-16 | 2017-11-16 | Fulton County (Big Creek WPCP) | Fulton | sandy springs | 5385 Peachtree Dunwoody Road Sandy Springs | 4720 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/16/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | nancy creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2618 Gresham Road, Decatur | 8610 | Notification received on February 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/15/2017 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:03 hours when a crew rodded the 10" sewer main 90ft between manholes, cleared the blockage at 80ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-20 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-10 | 2017-04-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3266 Northlake Parkway, Atlanta | 13230 | Notification received on April 14, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/10/2017 12:00:00 AM |  |  |  |  | 0 | Henderson Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:49 hours when a crew pressure washed the 10" sewer amin 74ft, clearing the blockage at 60ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-07 | 2015-01-07 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 390 Stovall Street, SE | 1670 | fax received 1/08/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/8/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-22 | 2017-01-25 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 3180 Wetherington Lane - Valdosta | 2200000 | Email received 2017-01-24, update received 2017-01-26 | Other | Wastewater Regulatory Program | GA0033235 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/22/2017 12:00:00 AM |  |  | 1 | Withlacoochee River/Little River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Large amounts of rainfall in excess of 6 inches within a 24-hour period; busted seal caused a leak in the plant's 6-million gallon equalization basin. | Impact of the spill determined to be less than 0.01% on receiving rivers. Repairs began early January 25th. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-08 | 2015-08-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 38 The Prado, NE | 390 | fax received 8/09/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Kim Hembree | Kim Hembree | 8/9/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-07 | 2018-08-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 8 Edwin Pl. NW - Atlanta | 820 | Fax sent 2018-08-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/8/2018 12:00:00 AM |  | 8/7/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3114 Vultee Drive | 29086 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Linsey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, sewer main has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-20 | 2018-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1371 Kimberly Way SW - Atlanta | 3 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/21/2018 12:00:00 AM |  | 4/20/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-27 | 2015-09-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1903 Sunbury Place, NW | 250 | fax received 9/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/28/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-22 | 2016-02-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 1030 | fax received 2/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/23/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-15 | 2016-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 38988 | Email notification received 2/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 2/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload due to a severe storm event |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-05-05 | 2016-05-05 |  | DeKalb | Atlanta | 1635 Sugar Downs Court, Atlanta | 1 | Notification received on May 6, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 5/5/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure | The problem was corrected at 14:30 hours, when the crew sealed the drip with hydraulic concert and continued normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-22 | 2018-08-22 | Pepperell High School | Floyd |  | 3 Dragon Drive, Lindale, GA 30161 | 1800 |  | Raw Sewage | Mountain District - Cartersville | GAU060108 | N/A | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 9/5/2018 12:00:00 AM | Coosa |  |  |  | 1 | Silver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root mass in sewer line | Root mass was removed and pipe was reconnected | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-09-05 | 1 | 0 | 0 | 0 | 0 | 0
2016-09-21 | 2016-09-21 | Thomaston, City of (Town Branch WPCP) | Upson | Thomaston | 826 9th Avenue | 720 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Debris will be removed from the surronding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-21 | 2016-09-21 | Thomaston, City of (Town Branch WPCP) | Upson | thomaston | 826 9th Avenue | 720 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Debris will be removed from the surronding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-05 | 2016-10-11 | West Point, City of (West Point WPCP) | Troup | West Point | Chattahoochee River 1,200 feet south of East 10th St/Hwy 29 Bridge on the East Bank of the river, West Point, GA. | 2500 | Email received on 10/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0020052 | Collection System | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/5/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | There was a mechanical joint failure on six inch force main. | The city immediately shut down the pumping station feeding the force main and closed all valves from the station to the force main. The spill stopped flowing immediately. The line was excavated and the failed mechanical joint fitting was removed and replaced with new fittings. The line was repaired and back in service at 1:30 PM on October 5, 2016. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-11 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-17 | 2017-05-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 587 Tyler St. NW - ATL | 25 | EDIT 2017-10-31: This is a private spill, not a public spill. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 5/18/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was unknown. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-14 | 2018-06-16 | Albany, City of (Joshua Street WPCP) | Dougherty | City of Albany | Manhole located approximately 120 feet north of the Oglethorpe bridge adjacent to the Flint River. | 18000 |  | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System |  |  | Wet weather |  |  | Juan Robles |  | 6/18/2018 12:00:00 AM |  |  |  |  | 0 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Rain. Blockage in the discharge piping of pump number 1 in LS 25, the downstream station in addition to a blockage in a splitter box at the influent end of the wetwell. | Obstructions are going to be cleared and manhole will be repaired. |  |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-31 | 2018-03-31 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Oglethorpe Blvd. bridge | 3500 | Letter received on April 13, 2018. | Raw Sewage | Wastewater Regulatory Program | GA0037222 |  | Stream |  | Wet weather |  |  | Hsin Yeh | Paul Moisan | 4/10/2018 12:00:00 AM |  |  |  |  | 0 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rain | A jet vac was dispatched to clean up debris and wash down the area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-17 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-19 | 2018-01-19 | Grovetown, City of | Columbia | Grovetown | Man hole/Sewer trunk line at 208 Brookstone Circle, Grovetown, GA in the Ashland Commons Subdivision. | 3000 | At the time the spill was reported, personnel notified the Division that the spill had not entered State waters. Follow up correspondence from the City of Grovetown personnel confirmed that raw sewage had deposited around the nearby area; but did not enter State waters. | Raw Sewage | Northeast District - Augusta | GAJ020222 | N/A |  |  | Debris |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/22/2018 12:00:00 AM | Savannah |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the sanitary sewer line at 208 Brookstone Circle in the Ashland Commons sub division located of Harlem-Grovetown Road in Grovetown resulted in a raw sewage overflow at the manhole. The spill was reported to the City of Grovetown Public Works Department at approx. 1:00 pm. | The City of Grovetown Public Works Department responded and worked to open up the blockage within the trunk line at approximately 8:00 pm. Lime was applied to the areas that raw sewage deposited. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2018-02-22 | 1 | 0 | 0 | 0 | 0 | 0 | Raymond Fulcher | 706-860-1688 | CITY OF GROVETOWN
2018-01-19 | 2018-01-19 | Grovetown, City of | Columbia | Grovwtown | Man hole/Sewer trunk line at 208 Brookstone Circle, Grovetown, GA in the Ashland Commons Subdivision. | 3000 | At the time the spill was reported, personnel notified the Division that the spill had not entered State waters. Follow up correspondence from the City of Grovetown personnel confirmed that raw sewage had deposited around the nearby area; but did not enter State waters. | Raw Sewage | Northeast District - Augusta | GAJ020222 | N/A |  |  | Debris |  | Delaine Scott | Delaine Scott | Delaine Scott | 1/22/2018 12:00:00 AM | Savannah |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A blockage in the sanitary sewer line at 208 Brookstone Circle in the Ashland Commons sub division located of Harlem-Grovetown Road in Grovetown resulted in a raw sewage overflow at the manhole. The spill was reported to the City of Grovetown Public Works Department at approx. 1:00 pm. | The City of Grovetown Public Works Department responded and worked to open up the blockage within the trunk line at approximately 8:00 pm. Lime was applied to the areas that raw sewage deposited. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2018-02-22 | 1 | 0 | 0 | 0 | 0 | 0 | Raymond Fulcher | 706-860-1688 | CITY OF GROVETOWN
2015-03-04 | 2015-03-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 914 Ridge Avenue, NW | 3210 | fax received 3/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/5/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-13 | 2016-08-13 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1140 Martin Luther King Blvd., Athens | 842 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Other |  | Grease |  |  | Dagny Pariani | Dagny Pariani | 8/15/2016 12:00:00 AM | Oconee |  |  |  | 0 | private pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disposable wipes and grease clogged the sewer line | Rodded the sewer line to clear the blockage. Cleaned and limed the area. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-08-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-13 | 2016-06-14 | Lyons, City of (Lyons North WPCP) | Toombs |  |  | 90000 |  | Raw Sewage | Coastal District | GA0033391 | N/A | Ditch | Ditch | Rags |  | Charlotte Nevill | Charlotte Nevill | Charlotte Nevill | 6/16/2016 12:00:00 AM | Altamaha | 6/14/2016 12:00:00 AM | 2016-06-14 |  | 0 | Swift Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The spill was caused by a blockage from inmates at the local jail flushing mop heads. There was also an old manhole cover that was left in the sewer system many years ago. The city does not have a grinder for the jail. The 90,000 gallon spill lasted approximately two days from June 13-14, 2016 and flowed into an unnamed tributary to Swift Creek. The point of discharge from the manhole was being cleaned by the city and had already dried by the afternoon. There was still a small amount of sewage (grey water) flowing behind the home down the street. No dead fish were noted in this area. Further downstream was a small pool of water with very little to no flow. Sewage (grey water) had made it to this point, but no dead fish were noted. Further downstream, Swift Creek was observed to have no dead fish and no signs of sewage. The color of the creek seemed normal, brown and clear. | Signage was placed at the spill site and on Highway 152 where the road crosses over Swift Creek. The local Health Department and media were notified. Upstream and downstream monitoring was initiated on June 14, 2016. | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 778eb569-f488-4d14-a790-403523838de4 | 2016-07-22 | 1 | 1 | 1 | 0 | 0 | 0
2017-07-31 | 2017-07-31 | Cobb County Water System | Cobb |  | 1306 Powder Springs Rd | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Pine Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Jet Cleaned | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-18 | 2017-09-18 | Winder, City of (Marburg Creek WPCP) | Barrow | Winder | 4339 Monroe Highway - Winder | 480000 | 24-hour composite sample for TSS on 2017-09-18 indicated a TSS of 87 mg/L. | Treated Effluent | Wastewater Regulatory Program | GA0023191 | WWTP | Stream | Stream | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/18/2017 12:00:00 AM |  | 9/18/2017 12:00:00 AM | 2017-09-18 |  | 1 | Marbury Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The float that turns on the pump in the backwash basin malfunctioned and did not engage the discharge pumps; therefore, allowing flow from the backwash basin to backfeed into the disc filtration system via the gravity feed line from the disc filters to the basin. High turbidity conditions became present in the disc filtration system resulting in a high TSS sample. | Add a high level alarm inside the backwash basin in another location. Create SOP for inspecting effluent water quality beyond the clarifier. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-22 | 0 | 1 | 1 | 0 | 0 | 0
2018-05-23 | 2018-05-23 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 3652 Larry Mulkey Memorial Rd. - Cumming | 2160 | Email sent 2018-05-24 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/24/2018 12:00:00 AM |  | 5/23/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Sawmill Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pieces of PVC piping and flushable wipes blocking the sewer line. | Line was jetted and cleared of the blockage. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Douglas, City of (Southeast WPCP) | Coffee |  | 400 Block of West Gordon St., 608 North College Ave & 111 West Jefferson St. | 27000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ditch | Channel | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/2/2016 11:15:00 AM | Satilla | 9/2/2016 12:00:00 AM | 2016-09-03 |  | 1 | Un-named tributary of Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Hydraulic overload of the collection system from Tropical Storm Hermine. |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-09-08 | 1 | 1 | 0 | 0 | 0 | 0
2018-07-09 | 2018-07-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1100 Swathmore Dr. NW - Atlanta | 3000 | Fax sent 2018-07-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/10/2018 12:00:00 AM |  | 7/9/2018 12:00:00 AM |  |  | 1 | Long Island | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-22 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | Lift Station 158 on Crossroads Parkway | 200 | Inital email and final report received 2/23/2017. | Raw Sewage | Coastal District | GA0038326 | Lift Station | Storm Drain, Stream | Stream | Grease |  | Cliff Swiger | Dagny Pariani | Dagny Pariani | 2/23/2017 12:00:00 AM | Savannah | 2/23/2017 12:00:00 AM |  |  | 1 | St. Augustine Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease covered controls at the Lift Station causing the station not to turn on and a manhole to overflow | Manually turned on the station and cleaned controls of grease. Cleaned and mitigated spill area. Will notify FOG staff to investigate where grease was entering system. | 67692807-818f-496b-9fb6-018f0decdb42 | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2017-11-22 | 2017-11-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Campbellton Rd. SW - ATL | 1620 | Fax sent 2017-11-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 11/23/2017 12:00:00 AM |  | 11/22/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Not specified | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 800 Block of Gornto Road | 1150 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-09-11 | 2017-09-11 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 4100 Block of Bemiss Road - Valdosta | 900 | Call received 2017-09-11; email received 2017-09-12 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Pump Station | Stream | Stream | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/11/2017 12:00:00 AM |  | 9/11/2017 12:00:00 AM |  |  | 1 | Cherry Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Widespread power outages due to Tropical Storm Irma resulted in the loss of power. | Used a portable generator to restore power to the lift station and stop the spill. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-29 | 2016-07-29 | Forsyth County (Dick Creek WRF) | Forsyth |  | 4364 Orchard Lake Drive | 1000 | Fax received 7/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038563 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/29/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "plug" in line. | vacuum manhole, removed plug, and limed roadway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Forsyth County | 770.205.4504
2015-11-04 | 2015-11-04 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Spirit Creek WPCP | 26250 | fax received 11/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 11/4/2015 12:00:00 AM |  |  |  |  | 1 | Spirit Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | "Higher than normal flow to the Spirit Creek lift station and the lack of the backup pump due to failure on Monday, resulted in a high wet well level and transfer of flow to the Spirit Creek WPCP. The discharge valve at the Spirit Creek WPCP was closed resulting in the inability [to] transfer flow from the gravity line. | The valve was opened allowing the station to resume normal operation. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-12-02 | 2015-12-02 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | Intersection of West Tyler and Trammell Street | 2415 |  | Raw Sewage | Mountain District - Cartersville | GA02-056 | WWRF | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/4/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary of Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive Rainfall | Vacuum trucks were used to mitigate the spill | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | David Oxford | 706-529-1010 | Dalton Uiltities
2015-08-26 | 2015-08-26 | Rome, City of (Rome WRF) | Floyd |  | 6 Center Street West Rome | 900 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 8/27/2015 12:00:00 AM | Coosa |  |  |  | 0 | Little Dry Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease in the sewer main | The sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2017-10-02 | 2017-10-02 | Trion, Town of (Trion WPCP) |  |  | Town of Trion WPCP 15131 Hwy 27 Trion | 57000 |  | Raw Sewage | Mountain District - Cartersville | GA0025607 | WWTP | Stream |  | Equipment failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 10/3/2017 12:00:00 AM | Coosa |  |  |  | 1 | Chappel Creek | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Town of Trion WPCP influent control panel malfunctioned. | See attached report | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-10-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-05 | 2016-03-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2888 Collier Drive, NW | 168 | Fax received 3/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/6/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-02 | 2017-01-02 | BASF Corporation (Gordon) | Wilkinson |  |  | 0 |  | Primary Effuent | Wastewater Regulatory Program | GA0003271 | N/A | Stream |  | Other |  | Jill Causse | Jill Causse | Sarita Banjade | 1/2/2017 12:00:00 AM |  |  |  |  | 1 | Little Commissioner Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to pump failure coupled significant rainfall | improve reliability of the control/alarm system of pumps | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Tifton, City of (New River WPCP) | Tift | Tifton | Intersection of 26th Street East and Ridge Ave, Tifton | 6000 | Email received on 09/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Power failure |  |  | Paul Moisan | Paul Moisan | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | New River Basin | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage at lift station. | When power was restored to the lift station, flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-09-07 | 0 | 1 | 1 | 0 | 0 | 0
2015-11-30 | 2015-11-30 |  | Brooks | Quitman | West Battle St. and South Walker St. | 1000 |  | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Ditch |  | Power failure |  |  | Dagny Pariani |  | 12/16/2016 12:00:00 AM | Suwannee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lift station main breaker tripped | Reset breaker and pump programs. Electrician was called to check power source. City crew poured a lime solution and deodorizer into the ditch. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-05-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-28 | 2016-12-28 | Cobb County Water System | Cobb |  | 1623 Pintail Point | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/28/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mallard Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failed 8 inch Creek Crossing |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-17 | 2016-11-17 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 3079 Crossing Park Road, Norcross | 469 |  | Raw Sewage | Wastewater Regulatory Program | GA0026433 |  | Stream |  | Roots |  |  | Hsin Yeh | Kim Hembree | 11/17/2016 12:00:00 AM |  |  |  |  | 0 | Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-05 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-05 | 2017-01-05 | Cobb County Water System | Cobb |  | 2352 Goodwood Dr | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-02 | 2017-08-02 | Patterson, City of (Patterson WPCP) |  |  | Dallas Street | 1000 |  | Raw Sewage | Coastal District | GA0037206 | Pump Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 8/3/2017 12:00:00 AM | Satilla | 8/2/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary to Patterson Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power due to a tree falling on the power lines which supplies power to the Dallas lift station. | The tree was removed and power was restored to the lift station. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-08-10 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-05 | 2015-12-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2097 Bethel Drive, NW | 750 | fax received 12/06/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/5/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-31 | 2016-01-07 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | Manhole 417 at Hwy 82 and Don Foster | 42480 |  | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Storm Drain |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/31/2015 12:00:00 AM | Flint | 12/31/2015 12:00:00 AM | 2015-12-31 |  | 1 | Brantley Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Manhole overflow caused by excessive rain and an obstructed sewer line | Monitored and cleaned |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-08 | 1 | 1 | 0 | 0 | 0 | 0 | [8 empty] | City of Dawson
2016-01-04 | 2016-01-04 | Cobb County (RL Sutton WRF) | Cobb |  | 1919 North Landing Way | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/4/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Ruby Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 inch Clay Main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-18 | 2018-04-30 | Marshallville, City of (Marshallville WPCP) | Macon |  | Marshallville WWTP | 0 | Violation noted in facility "Violations Tab" | Treated Effluent | West Central District | GA0047431 | WWTP | Stream | Stream | Other |  | Jody Sapp | Tilden Bembry | Jody Sapp | 5/15/2018 12:00:00 AM | Flint | 4/30/2018 12:00:00 AM | 2018-05-31 |  | 1 | Spring Hill Creek trib. to Beaver Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | TSS exceedance of 183 mg/l. TSS WA limit is 70mg/l. Operator stated possible pond turnover. | discharge has been closed while undergoing corrective actions in the pond. | 43bc988a-eb6e-11e0-b8d8-000c29971acc | 43bc988a-eb6e-11e0-b8d8-000c29971acc | 488bfc66-eb6e-11e0-b8d8-000c29971acc | 2018-05-31 | 1 | 1 | 0 | 0 | 0 | 0
2016-09-07 | 2016-09-07 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 70.2 TSS, weekly average concentration (mg/L): permit = 30, reported = 100 Flow was 0.868 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 |  | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 10/3/2016 12:00:00 AM | Ogeechee |  |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Immaturity of pretreatment pond at Coastal Processing caused high BOD/TSS loadings to the WPCP | Coastal Processing installed a DAF unit, bypassing pond to allow it to biologically mature |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-625-3166 |  | 70.2 | 100
2015-12-15 | 2015-12-15 | Cobb County MS4 | Cobb |  | 51 Pheasant Drive | 300 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of roots in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The Water System was notified at 8:00 p.m and the crew stoopped the overflow at 10:00. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-22 | 2017-12-22 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 238 Colonial Drive, Woodstock | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/22/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary of Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line clogged | The clog was cleared by construction jetting the line | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-12-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2017-07-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1850 Beatrice Ct. SW - ATL | 10275 | Fax received 2017-07-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/8/2017 12:00:00 AM |  | 7/7/2017 12:00:00 AM | 2017-07-08 | 2018-07-30 | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. Process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-11 | 0 | 0 | 0 | 1 | 1 | 0
2018-05-22 | 2018-05-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1571 Willis St. NW - Atlanta | 500 | Fax sent 2018-05-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/23/2018 12:00:00 AM |  | 5/22/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-19 | 2015-02-19 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | atlanta | 3438 Stratford Road, NE | 3615 | fax received 2/20/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/20/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed line and debris | The crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-29 | 2015-04-29 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 451 Sawtell Avenue, SE | 332 | fax received 4/30/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/30/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-05 | 2015-09-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 835 Peachtree Street, NE | 550 | fax received 09-05-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/5/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-26 | 2018-01-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2522 Lake Erin Drive, Tucker GA 30084 | 5400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System |  |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/26/2018 8:27:00 PM | Ocmulgee | 1/26/2018 12:00:00 AM |  |  | 0 | Peachtree Branch Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wipe debris blockage causing manhole 18-252-s031 | Pressure washed sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | 6th Street and Lenox Ave Lift Station in McRae-Helena | 200 | Isolated spill | Raw Sewage | Southwest District | GA0048674 | Lift Station |  |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure due to Hurricane Irma | Isolated spill and cleaned area. Lime applied liberally to area. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2508 Argonne Drive | 27000 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2015-08-22 | 2015-08-22 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Lawrenceville | 155 Meadowbrook Drive | 1800 | fax received 8/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/22/2015 12:00:00 AM |  |  |  |  | 1 | Pew Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris washing up against the sewer line causing a break | Repaired broken pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-02-17 | 2015-02-17 | Paulding County (Coppermine Road WPCP) | Paulding |  | Summer Hill Road | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Cindy Nix | Kathy Lewis | Cindy Nix | 3/25/2015 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | Jetted and cleaned manhole and lines | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey | 678-224-4077 | PAULDING COUNTY - COPPERMINE WRF
2018-07-18 | 2018-07-19 | Macon Water Authority (Rocky Creek WPCP) | Macon | Macon | 1701 Walnut Street, MH ID 66937 | 4038693 |  | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Ditch | Equipment failure |  |  | Juan Robles | Juan Robles | 7/18/2018 12:00:00 AM |  | 7/19/2018 12:00:00 AM | 2018-07-19 |  | 0 | Vineville Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause is suspected to be a broken manhole lid in the manhole that is blocking the flow. | By-pass pumping is in place and sewage is no longer escaping. MWA sewer conveyance crews will be televising the sewer main in order to determine the exact cause of the blockage and the best course of action for removal. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-23 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-12 | 2018-04-12 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | MetCalf & Broad Street - Augusta | 300 | Email sent 2018-04-16 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Other |  | Rags |  |  | Alys Hannum | Alys Hannum | 4/16/2018 12:00:00 AM |  |  |  |  | 1 | Phinizy Swamp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and debris | Augered 132 feet. Area was washed down and storm drain was flushed and vacuumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 600 Block of Scott Drive | 41000 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-08-28 | 2017-08-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 2986 West Rock Quarry Rd. - Buford | 5643 | Fax received 2017-08-28 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/28/2017 12:00:00 AM |  | 8/28/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Little Mulberry Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Raked area and spread lime, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 896 Tower Road - Social Circle | 200 |  | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System |  | Ditch | Contractor |  |  | Alys Hannum | Hsin Yeh | 12/13/2016 12:00:00 AM |  | 12/6/2016 12:00:00 AM |  |  | 0 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause was due to a contractor boring through the sewer line. | Pipe dug up and replaced. Hole back-filled. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-20 |  | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 3738 Clubhouse | 0 | First Notification of Spill received on December 19, 2016 | Raw Sewage | [7 empty] | Reginald Williamson | Reginald Williamson |  | 12/20/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-25 | 2018-01-25 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 5420 Riverdale Road, College Park | 1800 | Fax received on 1/26/2018. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/26/2018 12:00:00 AM |  |  |  |  | 0 | Sullivan Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Greese | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-01 | 2018-03-01 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 251 Brookside Ct. - Martinez | 3500 | Fax sent 2018-03-01 | Raw Sewage | Wastewater Regulatory Program | GA0031992 |  | Stream | Stream | Roots |  |  |  | Alys Hannum | 3/2/2018 12:00:00 AM |  | 3/1/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. to Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debris | Used a high pressure jet to clear sewer main. Limed area, posted signs, took samples of creek, and planned video inspection of sewer main. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-01 | 2017-10-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 942 Glenwood Ave. SE - ATL | 158 | Email received 2017-10-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  | Alys Hannum | Alys Hannum | Alys Hannum | 10/2/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2017-07-03 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3292 Buford Highway, Atlanta | 100 | Notification received on July 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Rags |  |  | Hsin Yeh | Hsin Yeh | 7/3/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | The problem was corrected at 11:30 hours when a crew pressure washed the right of way cleanout 28 (ft) to clear the blockage at 15 (ft). The crew also dug down on the main, removed an obtrusive tap and corrected the lateral issue which restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-20 | 2016-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1935 Alison Court, SW | 345 | fax received 4/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/21/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-11 | 2017-07-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1508 Foote St. NE - ATL | 177 | Fax received 2017-07-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/12/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 205 North Tibbs Road | 2400 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWRF | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/25/2016 12:00:00 AM | Coosa |  |  |  | 0 | McLellan Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Inflow & infiltration from excessive rainfall | Dalton Utilities contracted pumper trucks to mitigate the release and minimize the volume of wastewater released to state waters | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-08 | 2015-10-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 3769 Salem, Lithonia | 1100 | Notification received on October 9, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/8/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary to Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:30 hours, when a crew pressure washed the sewer main 400ft upstream, cleared the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-09 | 2016-08-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3195 Panther Trail, SW | 1120 | fax received 8/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/10/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | v | 1300 Block of North Lee Street | 76500 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-05-24 | 2018-05-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4816 Milgen Road | 213987 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Cooper Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, manhole has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Richmond Hill, City of (Sterling Creek WRF) | Bryan |  | 10384 ford ave Richmond Hill, GA | 72000 |  | Raw Sewage | Coastal District | GA0037648 | Collection System | Other | Shoreline | Equipment failure |  | Steve Wurtz | Steve Wurtz | Steve Wurtz | 1/16/2018 12:00:00 AM | Ogeechee | 1/16/2018 12:00:00 AM | 2018-01-22 | 2019-01-31 | 0 | Minimal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | not detected | 0 | blockage of gravity sewer line | two pumper trucks removing recovering estimated 322000 gallons of contaminated water, 135 gallons of dechlorinated potable water used to dilute affected retention pond waters | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | e08f08ae-9859-4c14-9a81-fc17ee908cd5 | 2018-02-20 | 1 | 1 | 1 | 0 | 0 | 0
2015-08-18 | 2015-08-18 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 252 Valley Crossing, Canton | 8960 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Cindy Nix | Kathy Lewis | Ebony Johnson | 8/19/2015 12:00:00 AM | Coosa |  |  |  | 0 | Hidden Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bricks and debris blocked the sewer line. This caused the line to back up and wastewater to overflow from a manhole in the street. The wastewater entered a storm water drain that emptied into the pond at Hidden Lakes Subdivision. | A CCWSA construction crew responded immediately, jetted the line, and removed the debris. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 678-313-1947 | Cherokee County W&S Authority
2018-07-18 | 2018-07-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1725 Northwest Dr. NW - Atlanta | 800 | Email/Fax sent 2018-07-19 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/19/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | By-pass pump malfunction | Crew made repairs to the by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-05 | 2015-03-05 | Thomaston, City of | Upson | Thomaston | 855 No. Center Street | 35000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/5/2015 12:00:00 AM | Flint | 3/5/2015 12:00:00 AM |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to a broken force main. | All debris associated with the overflow has been cleaned up and the local health department has also been notified. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-30 | 2017-08-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2249 Wallingford Drive, Decatur | 2320 | Notification received on September 5, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/31/2017 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:00 hours when the crew pressure washed the 8-inch sewer main 100ft, removed the blockage at 25ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-13 | 2015-04-13 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 28 mg/L on 04/13/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-16 | 2017-07-16 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd | 60000 |  | Raw Sewage | Wastewater Regulatory Program | GA0025852 | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/16/2017 12:00:00 AM | Suwannee |  |  |  | 1 | Hat Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Wet Weather | Spilled stopped at 12:30 PM | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-22 | 2016-03-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1680 Westview Drive, SW | 26800 | fax received 3/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/22/2016 12:00:00 AM |  |  | 2016-03-23 | 2017-04-13 | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Debris and possible breached mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-05 | 2018-01-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2138 Faulkner Rd - ATL | 18750 | Call received 2018-01-05. Fax sent 2018-01-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 1/6/2018 12:00:00 AM |  | 1/5/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Unspecified | Line was bypassed for containment. Pipe repair is a work in progress. Cleanup has been scheduled. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-26 | 2018-02-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4075 Memorial Drive, Decatur GA | 40 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/26/2018 5:00:00 PM | Ocmulgee | 2/26/2018 12:00:00 AM |  |  | 1 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease and tissue debris | Pressure washed manholes |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-20 | 2017-11-20 | Folkston, City of (Folkston Pond WPCP) | Charlton | Folkston |  | 69000 |  | Secondary Effluent | Coastal District | GA0027189 |  | Stream | Stream | Unknown |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 12/1/2017 10:00:00 AM | Saint Mary's | 12/1/2017 12:00:00 AM | 2017-12-01 |  | 1 | Clay Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 1 | The City suspects that their WWTP received a "slug" of high BOD wastewater from an unknown source. | Under investigation by the City. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-12-11 | 1 | 1 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1015 Berne Street, SE | 6315 | fax received 11/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction | The crew repaired the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-22 | 2017-10-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2466 East Tupelo Street, Atlanta | 1020 | Notification received on October 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/22/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:39 hours when the first responder crew pressure washed the sewer main 320-ft upstream, cleared the grease blockage at 305-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-16 | 2018-04-16 | Cobb County Water System | Cobb |  | 240 Pine Valley Rd | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creekj | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The water system stopped the overflow at 9:30 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-29 | 2017-07-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2805 Cascade Rd. SW | 1380 | Fax received 2017-07-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/30/2017 12:00:00 AM |  | 7/29/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and a collapsed mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-16 | 2017-05-16 | Cobb County Water System | Cobb |  | 4900 Chimney Hill Court | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/16/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-08 | 2018-09-08 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Lift Station 13 - Hwy 80 & Hwy 56. | 3600 | Phone call received 2018-09-10. Email received 2018-09-11 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Pump Station | Ground |  | Pipe failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/10/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waterways. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ruptured force main | Damaged line was repaired, powdered lime was applied to spill site. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-19 | 2017-06-19 | Cobb County Water System | Cobb |  | 660 Church Road | 70 |  | Raw Sewage | Wastewater Regulatory Program |  |  | Stream |  | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 6/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Joseph Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The Cobb County crew stopped the overflow at 2:35 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-03 | 2015-01-03 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2901 Darrah Court, SW | 200 | fax received 1/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Kim Hembree |  | Kim Hembree | 1/4/2015 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 |  | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-10 | 2015-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 143 Hillsdale Drive, SW | 10 | fax received 8/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/11/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-21 | 2015-08-21 |  | Clarke | Athens | 122 Crow's Nest Court | 2360 | This spill was included on an enforcement action dated 9/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Rags |  |  | Dagny Pariani |  | 8/21/2015 12:00:00 AM | Oconee |  |  |  | 0 | Cedar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An accumulation of rags blocked the sewer line | The line was rodded and flushed. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-11 | 2017-02-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1571 Willis St. NW - ATL | 352 | Fax received Sunday 2017-02-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Paul Moisan | 2/12/2017 12:00:00 AM |  | 2/11/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-09 | 2017-05-10 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Sugar Hill | 4695 Pinecrest Drive - Sugar Hill | 584 | Fax received 2017-05-10 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Force Main | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/10/2017 12:00:00 AM |  | 5/10/2017 12:00:00 AM |  |  | 1 | Level Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cracked Pipe. | Wet soil removed, hauled off, and area backfilled. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-07 | 2017-05-07 | Cobb County Water System | Cobb |  | 70 Rhodes Dr. | 250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/7/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | sope creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease in 8" clay main | spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-23 | 2016-06-23 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Fritz-Mar Lane, Athens | 192 | Initial email 6/23, full report faxed 6/24 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 6/23/2016 12:00:00 AM | Oconee | 6/23/2016 12:00:00 AM |  |  | 1 | unnamed tributary to North Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper wipes clogged sewer line | Rodded sewer line |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-06-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2016-03-02 | 2016-03-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2575 Chantilly Drive, NE | 4250 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-02 | 2017-01-03 | Fort Valley, City of (Fort Valley WPCP) | Peach | Fort Valley | 114 Montrose Ave., Fort Valley | 14700 | Phone call received on 01/03/2017, and email received on 01/06/2017. | Raw Sewage | Wastewater Regulatory Program | GA0031046 | Collection System | Ground |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Significant rain event with more than 6" of rain. | The contracted engineering firm (Carter and Sloope) was contacted about this issue to form a plan to keep this from happening in the future. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | Keith Spillers |  | FORT VALLEY UTILITY COMMISSION
2016-10-27 | 2016-10-27 | Hinesville, City of (Fort Stewart WPCP) | Liberty | Fort Stewart | Corner of Crisp Ave and Sigma Street | 2400 |  | Raw Sewage | Coastal District | GA0047180 | Force Main | Storm Drain, Stream | Stream | Equipment failure |  | John Kalp | John Kalp | John Kalp | 10/27/2016 4:00:00 PM | Ogeechee | 10/27/2016 12:00:00 AM |  |  | 0 | Tributary of Mill Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Yes | 0 | Failure of an 8" sanitary force main for lift station 1591. See "Documents" section | Constructed berm, dug up force main and repaired it, removed approx. 7500 gallons of wastewater from stormwater collection system and then applied agriculture lime to disinfect the area. | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2016-11-01 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-16 |  |  | DeKalb |  | 4309 Memorial Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown cause, believed to be associated with the collapsed main in area |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-27 | 2016-01-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 1700 Summer Ridge Lane | 6432 | fax received 1/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/27/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Beaver Ruin Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-01-12 | 2018-01-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 207 North Decatur Road Decatur G 30030 | 600 | only 1 sign posted according to initial report | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/16/2018 9:35:00 AM | Ocmulgee |  |  |  | 1 | South Fork Peachtree Creek & unnamed tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Dale Fielder |  | Dekalb Co Dept. Watershed Management
2016-03-29 |  |  | DeKalb |  | 1599 Country Squire Court | 325 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | Cochran WPCP | Bleckley | Cochran | Lake Linda, Cochran Manhole 1438 | 25000 | Telephone call received on 02/03/2016; email received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0032107 | Collection System | Reservoir | Beach | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | Lake Linda | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Flash Flood rain event on 2/3/2016. Heavy rainfall impacted collection system through I&I with a high water table | Lake Linda will be temporarily closed from 2/4/2016 to 2/12/2016. Lake will have monitoring from 2/4/2016 to 2/12/16. Collection system will be included in Phase One of the GEFA 1.5 million dollar infrastructure repair project for the sewer collection system. Project will CIPP remaining lines around the lake, rehab manholes to include manholes lids. Project should be out for bid this year. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-06 | 2015-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | email notification recieved 11/10/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is an outfall spill. TSS Permit Limit = 15 mg/L; TSS Reported Value = 35 mg/L. Total outfall spill volume = 58.5 million gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-27 | 2015-05-27 | Columbus Water Works (South WRF) | Muscogee | Columbus | Columbus Water Works South Columbus Water Resource Facility | 0 | After review of DMR, second outfall spill was documented. REC EMAIL 6/17/2015. | Secondary Effluent | Wastewater Regulatory Program | GA0020516 | WWTP | Stream | Stream | Other |  | Emily Wingo | Emily Wingo | Emily Wingo | 6/17/2015 12:00:00 AM | Chattahoochee | 6/5/2015 12:00:00 AM |  |  | 1 | Chattahoochee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This spill was due to high Ammonia entering into the sewer. The Ammonia loading temporarily interfered with the biological activated sludge process causing increased Total Suspended Solids in the plant effluent system resulting in a discharge of 45 mg/L of suspended solids, 50% above the permitted limit. CWW continues to investigate the high result. | The influent NH3 has returned to tolerable limits and the South Columbus Water Resource Facility has returned to normal operations. CWW anticipates no adverse impact to the Chattahoochee River. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-06-17 | 0 | 1 | 1 | 1 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490 |  |  | 112
2018-02-06 | 2018-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2928 Layton Ave. NW - ATL | 25 | Fax sent 2018-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 2/7/2018 12:00:00 AM |  | 2/6/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-11 | 2015-02-11 |  | Cobb |  | 886 Branford Ct. | 530 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/11/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris in 8 in Clay Main | Cleaned and Spread Lime at Spill Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-27 | 2017-12-27 | Cobb County Water System | Cobb | Narietta | 2395 New Macland Road | 570 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Wild Horse Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped the overflow at 10:21 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-23 | 2016-02-25 | Rome, City of (Rome WRF) | Floyd |  | Behind 911 Oakland Avenue | 8500 | This section of sewer main will be inspected via CCTV for any partial blockages | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream | Stream | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 2/26/2016 12:00:00 AM | Coosa |  |  |  | 0 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather event | The spill was stopped on February 25th and the sewer main was thoroughly cleaned. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-09 | 2017-11-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1455 Fairmont Ave. NW - ATL | 905 | Fax sent 2017-11-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/10/2017 12:00:00 AM |  | 11/9/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew set up a by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 |  | Hart | Hartwell | Cedar Creek Lift Station | 279000 | this is one of three major spills that occurred in the area on 11/2/2015. Total volume of spills = 1.478 mgd | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Ground |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/3/2015 12:00:00 AM | Savannah | 11/3/2015 12:00:00 AM | 2015-11-03 |  | 1 | Lake Hartwell | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 |  | 0 | extremely heavy rainfall overloaded the sewer system | after rainfall had subsided, lime was applied. City is replacing one sewer line and looking at upgrading entire system. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-04 | 2016-01-04 | Alamo, City of (Alamo WPCP) | Wheeler |  |  | 5000 |  | Waste Activated Sludge | Northeast District - Augusta | GA0037753 | WWTP | Ground, Stream | Stream | Equipment failure |  | Joe Sills | Joe Sills | Joe Sills | 1/4/2016 1:00:00 PM | Altamaha | 1/5/2016 12:00:00 AM | 2016-01-11 |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Failure of sludge return portion of WWTP | Began in January | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 7e799d31-e731-4401-91a8-fdaf76bc3410 | 2016-05-27 | 1 | 1 | 1 | 0 | 0 | 0
2017-03-01 | 2017-03-01 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | 234 Ward Street and the corner of W. Ashley and Daughtry Streets. | 9000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ground, Storm Drain, Stream | Stream | Rags |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/1/2017 8:30:00 AM | Satilla | 3/1/2017 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill was caused by a backup of the sewer main. | Sewer main obstruction was cleared and flow was restored. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-03-21 | 1 | 1 | 0 | 0 | 0 | 0
2017-11-27 | 2017-11-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3902 memorial College Avenue, Clarkston, GA, 30021 | 4440 | Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | N/A | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/27/2017 4:46:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage caused manhole 18-043-s058 to spill into creek | Pressure washed from manhole 18-043-s202 to manhole 18-043-s058 to clear grease |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-28 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Yolanda Black |  | Dekalb Co Dept. Watershed Management
2017-07-08 | 2017-07-08 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 3519 Stone Cliff Way Woodstock | 2709 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/8/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | One inch hole in 10 inch force main coming from lift station | Construction crew fixed the main with a band and the main was put back in service. Construction is currently in the process of replacing the line. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-09 | 2018-02-09 | Columbus Water Works (South WRF) | Muscogee | Columbus | 7791 Stowers Road, Columbus | 3720 | Fax received on 2/10/2018. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 2/10/2018 12:00:00 AM |  |  |  |  | 0 | Upatoi Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" sewer main was logged with | Debris cleared, overflow stopped. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-12 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-01 | 2018-02-01 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 3065 Wyntree Dr. - Peachtree Corners | 9923 | Fax sent 2018-02-01 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/1/2018 12:00:00 AM |  |  |  |  | 1 | Unnamed Trib. of Bromolow Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and other products | Raked area and spread lime; placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-06 | 2015-05-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 10 | fax received 5/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/7/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-07 | 2017-04-07 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | 327 Linwood Rd., Savannah, GA | 3500 | Initial call and email report received 4/7. | Raw Sewage | Coastal District | GA0020443 | Force Main | Storm Drain, Stream | Stream | Contractor |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 4/7/2017 1:00:00 PM | Savannah | 4/7/2017 12:00:00 AM |  |  | 1 | Hoover Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer main was unintentionally damaged by heavy equipment operators. | Dammed canal to contain the spill. Removed sewage via vac truck. Bypass pumps in place. Repairing the main. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-04-07 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2015-04-20 | 2015-04-20 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift Station | 2500 |  | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 4/20/2015 10:24:00 AM | Ocmulgee | 4/20/2015 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Legion Drive lift station overflow. 2500 gallons, which may have entered into state waters. I & I related. | facility currently upgrading collection system. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-04-28 | 1 | 1 | 1 | 0 | 0 | 0
2016-01-21 | 2016-01-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 1754 Duffy Drive, Morrow MH # 2214563 | 2100 | Fax received on 01/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/21/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | York Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Blockage was cleared and flow returned to normal. Site will be cleaned and work orders generated for additional work to determine cause. Lines will be televised and if a problem is located, repairs will be made. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-22 | 0 | 1 | 1 | 0 | 0 | 0
2017-08-23 | 2017-08-24 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | 75 Ridge Lane off of Bo Jo Ella Drive in Douglas. | 720000 |  | Raw Sewage | Coastal District | GA0024431 | Lift Station | Other |  | Operator error |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 8/24/2017 12:38:00 PM | Satilla | 8/24/2017 12:00:00 AM | 2017-08-24 |  | 1 | Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 |  | 0 | Human error: lift station pumps found in the off position the next morning and the lift station float alarm system (SCADA) failed due to improper installation. | Lift station pumps placed back into service. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-08-28 | 1 | 1 | 1 | 0 | 0 | 1
2015-09-03 | 2015-09-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2170 Old Georgian Terrace, NW | 1670 | fax received 9/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/4/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew installed a bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-25 | 2016-02-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2190 Wallingford Drive, Decautur | 1000 | Notification received on February 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/25/2016 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | sewer main leaking | The problem was corrected at 14:15 hours, when a crew built a dirt berm around pipe to contain the spill and restored normal flow until the repair is completed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-22 | 2015-07-22 |  | Cobb |  | Laurel Canyon Golf Course | 650 |  | Raw Sewage | Mountain District - Cartersville |  | N/A | Stream |  | Operator error |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 7/23/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed creek into Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Truck turned over | Peachstate Environment cleaned up area | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | Ken Mitchell | 770-975-1133 | MBA Waste Service
2015-05-14 | 2015-05-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 666 Metropolitan Parkway, SW | 726 | fax received 5/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/27/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-18 | 2015-12-18 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 4580 Riverside Drive, Macon, GA (MH ID 65115) | 2600 | Fax and email received on 12/18/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Ditch | Grease |  |  | Paul Moisan | Paul Moisan | 12/18/2015 12:00:00 AM | Upper Ocmulgee | 12/18/2015 12:00:00 AM |  |  | 1 | Ditch feeding Beaverdam Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. There are no commercial sources of grease upstream from this location and residential grease is not regulated. | Debris has been removed from the area and the affected area has been disinfected with lime. This line is scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly "Hot Spot" inspection list. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-21 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-21 | 2017-12-21 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3001 Gordon Hwy - Augusta State Medical Prison | 8600 | Email sent 2017-12-22 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Unknown |  |  | Alys Hannum | Alys Hannum | 12/22/2017 12:00:00 AM |  |  |  |  | 1 | Uchee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "A recent project was in construct three new manholes to alleviate backups into the dormitories. Of course, this now means that a spill occurred outside the dorm and landed in a storm water ditch inside the fence." | Not specified |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-23 | 2016-03-23 | Marietta (City of)- Sewers | Cobb | Marietta | 582 Etowah Dr. Manhole in sidewalk/street in front of property | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/23/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-09 | 2017-06-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Rd. NE - ATL | 5250 | Email received 2017-06-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Alys Hannum | 6/12/2017 12:00:00 AM |  | 6/9/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was possibly vandilism to the by-pass pumps. | Crew turned the by-pass pumps back on. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-04 | 2015-05-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 3880 | verbal notification received 5/05/2015. Fax received 5/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/4/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-02 |  |  | DeKalb |  | 3625 Telstar Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh |  | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-15 | 2016-08-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3469 Rolling Green Ridge, SW | 10 | fax received 8/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/16/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-22 | 2018-05-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3478 Lakeside Dr. NE - Atlanta | 500 | Fax sent 2018-05-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/23/2018 12:00:00 AM |  | 5/22/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Conley | 4345 Abram Lane, Conley | 1080 | Notification received on December 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/6/2016 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 14:43 hours, when a crew pressure washed the 8" sewer main 160ft, cleared the grease blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-13 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 732 Knox Dr. SE - ATL | 84 | Fax sent 2018-02-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/16/2018 12:00:00 AM |  | 2/15/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-31 | 2017-08-31 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 3069 West Rock Quarry Road - Buford | 10474 | Fax received 2017-09-01 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/1/2017 12:00:00 AM |  | 8/31/2017 12:00:00 AM |  |  | 1 | Sherwood Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Debris - Rocks or Construction Material and Other | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-15 | 2017-05-15 | Richmond Hill, City of (Sterling Creek WRF) | Bryan | Richmond Hill | Mulberry Subdivision near the address of 72 Belle Grove Circle, Richmond Hill, GA, 31324. | 8925 |  | Raw Sewage | Coastal District | GA0037648 | WWTP | Canal | Lagoon | Equipment failure |  | Sarah Khorramzadeh | Sarah Khorramzadeh | Sarah Khorramzadeh | 5/15/2017 10:30:00 AM | Ogeechee | 5/16/2017 12:00:00 AM |  |  | 1 | Drainage lagoon which is contiguous to the tributary system of the Ogeechee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was the result of a faulty starter in conjunction with corrupted logic within the controller preventing a high level call out. On Friday, 05/12/2017, one of the two pumps in lift station 19 was removed and sent back to the manufacturer for warrantied repair, leaving only one pump in operation. | Minor spill protocol and broadcasted powdered hydrated lime in the potentially affected area, and in an effort to be proactive and to err on the side of caution, EOM has also taken samples in order to perform fecal, COD, and BOD5 analysis to ascertain affects if any to the ecology of the area. Placed two (2) signs in the area notifying residents of the event, and have sent the attached public notice to both the Bryan County Health Department and our local newspaper, The Bryan County Herald. | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | d71f3a29-35ed-4b3f-bb1e-03e337c876e3 | 2017-05-23 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Manhole at canal crossing Westover Blvd. at Lift Station 81, Albany | 400000 | Email notification on 02/24/2016, Telephone call received on 02/25/2016, letter received on 03/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Canal | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/25/2016 12:00:00 AM |  |  |  |  | 1 | Percosin Canal, Tributary to Cooleewahee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Rainfall (5 inches) resulted in flooding and cut the power to Lift Station 81. | Cut the power, and once the flooding subsided and the electrical components were able to be tested for integrity, pumps at the lift station were restarted and placed in automatic. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-11 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 380 Ardmore Cir. NW - ATL | 1055 | Fax sent 2018-02-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/16/2018 12:00:00 AM |  | 2/16/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-29 | 2015-05-29 | Oconee County (Calls Creek WPCP) | Oconee |  | Calls Creek plant | 7500 | Flow estimated at 7,500 gallons but becuase of the high level on uncertaincy, I requested that Oconee County handle this as a MAJOR spill. | Sludge | Northeast District - Athens | GA0050211 | WWTP | Stream | Stream | Pipe failure |  | Steve Walker | Steve Walker | Steve Walker | 5/29/2015 10:55:00 AM | Oconee | 5/29/2015 12:00:00 AM | 2015-05-29 |  | 1 | Calls Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | rupture of pipe joint along membrane feed line transporting mixed liquor. |  | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | 2015-06-01 | 1 | 0 | 0 | 0 | 0 | 0
2018-05-07 | 2018-05-07 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3536 Levy Drive | 52 | Fax sent 5/8/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Paul Moisan | 5/8/2018 12:00:00 AM |  |  |  |  | 0 | Bull Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" sewer main was clogged with debris causing an overflow. | Once the debris was cleared the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-14 | 2017-03-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 966 Yemassee Trail, Stone Mountain | 4900 | Notification received on March 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/14/2017 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defective 8" creek crossing line | The problem was corrected at 20:46 hours when a crew built a berm to contain the sewage leak, executed an emergency work order to repair the crossing, and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-16 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-28 | 2017-02-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Conley | 1915 Rock Cut Place, Conley Manhole - 2194292 | 2400 | Fax received on 03/01/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 3/1/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause was roots. | Cleared blockage, and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-01 | 0 | 1 | 1 | 0 | 0 | 0
2018-03-21 | 2018-03-21 | Savannah, City of (President Street WRF) | Chatham | Savannah | 309 West River Street, Savannah, GA | 145 | Initial phone call and emailed full report received 3/21/18. | Raw Sewage | Coastal District | GA0025348 | Collection System | Stream | Stream | Debris |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 3/21/2018 12:00:00 AM | Savannah | 3/21/2018 12:00:00 AM |  |  | 1 | Savannah River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in a gravity sewer line caused an overflow at a manhole. | Cleared blockage with vac truck and jetted sewer line. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-03-21 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-658-6973
2016-02-16 | 2016-02-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1999 Cheshire Bridge Road, NE | 40 | fax received 2/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/17/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew had to set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-18 | 2017-10-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6510 Alford Way, Lithonia | 3240 | Notification received on October 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/18/2017 12:00:00 AM |  |  |  |  | 0 | Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 19:46 hours when the first responder crew pressure washed the 8-inch sewer main 360-ft, clearing the blockage at 95-ft, stopping the spill and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-05 | 2016-11-05 | Cobb County Water System | Cobb | Marietta | 338 Rockmoor Trail | 2440 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/15/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of washed out creek crossing causing it to overflow into a tributary to Noonday Creek. | The Cobb County Crew stopped the overflow at 4:30 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 2016-03-14 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Bailey's Gym Health Club at 57 Glynn Plazas. | 2200 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Ditch | Ditch | Grease |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/14/2016 4:30:00 PM | Satilla | 3/14/2016 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage. | Grease blockage removed using a "Hot Shot" to break-up grease. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-03-21 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-22 | 2015-12-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2250 Mallard Ave., Macon MH #55952 | 10085 | Email and fax received on 12/28/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/28/2015 12:00:00 AM | Upper Ocmulgee |  | 2015-12-26 |  | 1 | Ditch feeding Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause was hydraulic overload and grease blockage. The area received 3.18 inches of rain on December 21-22. | Debris will be removed from the area and the affected area will be disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-29 | 1 | 1 | 1 | 1 | 0 | 0
2017-10-17 | 2017-10-17 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | West Martin Luther King Jr. Drive, Milledgeville | 600 | Notification received on October 19, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0030775 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/18/2017 12:00:00 AM |  |  |  |  | 0 | Tanyard Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots blockage | The Water Maintenance crew contained the spill, jetted the line, put out lime, and removed any debris. Additional preventive maintenance of checking the lines will occur. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-11 | 2018-05-11 | Fulton County (Big Creek WPCP) | Fulton |  | 625 Pine Trail Point Roswell GA 30075 | 2200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/11/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-20 | 2018-03-20 | Gwinnett County (Yellow River WPCP) | Gwinnett | Liliburn | 4985 Velva Ct. - Liliburn | 1424 | Fax sent 2018-03-20 | Raw Sewage |  | GA0047911 | Collection System |  | Stream | Debris |  |  |  | Alys Hannum | 3/20/2018 12:00:00 AM |  | 3/20/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products | Raked area and spread like; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-02 | 2018-05-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2852 Cascade Rd. SW - Atlanta | 450 | Fax sent 2018-05-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/3/2018 12:00:00 AM |  | 5/2/2018 12:00:00 AM |  |  | 1 | South Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Section of pipe was leaking from the joint. | Pipe has been repaired. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-09 | 2017-10-09 | West Point, City of (West Point WPCP) | Troup | West Point | West 8th Street, on bank of Chattahoochee River; West Point. | 1000 | Telephone call received on 10/09/2017; report emailed on 10/20/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020052 | Collection System | Stream |  | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 10/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to 6 - 6.5" of heavy rain associated with Hurricane Nate, over a 12 to 16 hour period. | Once the flood waters from the rain receded, the mainholes that were under water stopped filling, and the leaking stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-20 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-27 | 2015-02-27 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1776 Johnson Road, NE | 50 | fax received 3/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/4/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-16 | 2018-06-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1555 Lavista Road Atlanta GA 30324 | 4260 | manhole 18-106-p829 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/16/2018 11:10:00 PM | Ocmulgee |  |  |  | 1 | South Fork Peachtree Creek & unnamed tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage in county main caused private manhole to overflow | pressure washed manhole |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-20 | 2017-02-20 | Pooler, City of (Bloomingdale Regional WPCP) | Chatham | Pooler | 800 Winskie Rd., Pooler, GA, 31322 | 1300 | Initial call to Courtney Huggins on 2/20, full report emailed 2/23/17. | Waste Activated Sludge | Coastal District | GA0047066 | WWTP | Canal | Canal | Equipment failure |  | David Lyle | David Lyle | Dagny Pariani | 2/20/2017 4:00:00 PM | Savannah | 2/20/2017 12:00:00 AM |  |  | 1 | Hardin Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spoke to John Winn, City of Pooler Wastewater Superintendent. Spill was caused by malfunction in air valve at the treatment plant which caused partially treated sewage to back siphon. No visible impact to Hardin Canal at time of spill. A solenoid was replaced to repair the valve, spill location was vacuumed, and the facility is back in full operation. Mr. Winn confirmed that minor spill reporting and notifications will be completed including notice to health department, signage at the spill location, notice to local media and 5-day letter to EPD. Spill has been corrected. No further action needed. |  | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | 89352e56-9649-4d50-9761-577155a9c85b | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | 2017-02-23 | 0 | 1 | 0 | 0 | 0 | 1 | [8 empty] | CITY OF POOLER | 912-210-2673
2015-01-23 | 2015-01-24 |  | Lowndes | Valdosta | 2400 Block of Meadowbrook. | 6000 | Email notification from the City received 1/24/2015. This is NOT a duplicate of the previous spill of 6,000 gallons in the 2400 Block of Meadowbrook. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/24/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-02-03 | 2016-02-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | Silver Spring Apts., Morrow MH 2206507 | 99000 | Telephone call received on 02/04/2016; fax received on 02/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Hydraulic overload caused by rainfall event. | Lines will be inspected for source of inflow and infiltration to solve capacity issues. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-10 | 0 | 1 | 1 | 0 | 0 | 0
2018-03-05 | 2018-03-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3322 Lake Valley Rd. NW - Atlanta | 900 | Fax sent 2018-03-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 3/6/2018 12:00:00 AM |  | 3/5/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-03 | 2017-02-09 |  | Barrow | Winder | 750 Tucker Rd Winder, GA | 7800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/9/2017 12:00:00 AM | Oconee |  |  |  | 0 | Williamson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill wad due to blockage in the gravity sewer due to rags and settlement being discharged into the sewer and settling out in a low flow area thus blocking the sewer andcausing an overflowing. | The lines have been jetted to reopen to flow through the existing gravity sewer. The surrounding surface area has been raked to remove debris and lime added to area for disinfection. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-22 | 2015-09-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Road, NE | 366 | fax received 09/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/23/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-22 | 2017-03-22 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 1958 Tanglewood Drive - Snellville | 0 | Fax received 2017-03-23 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/23/2017 12:00:00 AM |  | 3/22/2017 12:00:00 AM |  |  | 1 | Watson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure - cracked | Raked are and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-07 | 2017-02-07 | Henry County Water Authority (Indian Creek WRF) | Henry |  | 844 Chase Marion Way | 1552 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/7/2017 12:00:00 AM |  |  |  |  | 0 | Little Cotton Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-21 | 2015-10-21 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Helen Street | 6095 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Dagny Pariani | Dagny Pariani | 10/21/2015 12:00:00 AM | Oconee | 10/8/2015 12:00:00 AM |  |  | 0 | un-named tributary to Middle Oconee | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | rags clogged the sewer | rod sewer to clear rags | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-10-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2510 Hood Ave NW - ATL | 760 | Fax received on 01/14/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/14/2017 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2018-09-10 | 2018-09-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2852 Cascade Rd. SW - Atlanta | 144 | Fax sent 2018-09-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/11/2018 12:00:00 AM |  | 9/10/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Section of pipe was leaking. | Crew performed a point repair. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-08 | 2018-03-08 | Blakely, City of (Blakely WPCP) | Early | Blakely | 530 Plant Street, Blakely | 200000 |  | Raw Sewage | Wastewater Regulatory Program | GA0025585 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/8/2018 12:00:00 AM |  |  |  |  | 0 | Baptist Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | All three main pumps experienced a thermal overload. Alarm system did not call out staff to notify of a problem. | Reset pump VFD drives. Will be working to have SCASA system upgraded. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1400 Block of Gornto Road | 4500 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-10-27 | 2015-10-27 | Broxton | Coffee | Broxton | West Avenue, North - Lift Station | 700 |  | Raw Sewage | Coastal District | GAJ020124 | Lift Station | Stream | Stream | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/27/2015 8:30:00 AM | Satilla | 10/27/2015 12:00:00 AM |  |  | 1 | un-named tributary | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Secondary pump "tripped" a breaker due to line blockage. Primary pump was out for repairs during spill event. | Cleared the blockage and pump electrical system was reset and pump was back in service. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-10-29 | 1 | 1 | 0 | 0 | 0 | 0
2016-01-14 | 2016-01-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2914 3rd Avenue, SW | 1 | faxes received 1/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 1/14/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill is ongoing |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-05 | 2018-03-05 | Clayton County (Northeast WPCP) | Clayton | Jonesboro | 648 River Bent Drive, Jonesboro | 3760 | Fax sent 2018-03-06 | Raw Sewage | Wastewater Regulatory Program | GA0020575 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/6/2018 12:00:00 AM |  |  |  |  | 1 | Morning Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-20 | 2016-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 3845 Springleaf Court, Stone Mountain | 29160 | Notification received on January 21, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 1/21/2016 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 19:00 hours, when a crew built a bem to contained the spill, installed a bypass pump rerouting the flow around the broken section of pipe, put in an emergency request for pipe repair and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-21 | 2017-03-21 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3213 Wrightsboro Rd. - Augusta | 45 | Email recieved 2017-03-21 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  |  | Alys Hannum | 3/21/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Technician used a high pressure jetting system to unclog the sewer gravity main. The downstream storm pipe was flushed and vacuumed out. The sewer gravity mains in the area will be assessed to determine the origin of grease. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-21 | 2016-11-21 |  | Fulton |  | 7740 Janann Way Sandy Springs 30350 | 5700 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  |  |  | Reginald Williamson | 11/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2017-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-19 | 2015-04-19 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2275 Gray Highway | 1920 | REC CALL 4/20/2015. REC FAX 4/21/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Ditch | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/20/2015 9:00:00 AM | Ocmulgee | 4/20/2015 12:00:00 AM |  |  | 1 | Ditch feeding Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rags | Debris has been removed and the affected area is being disinfected with lime. This line has been scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly “Hot Spot” Inspection list. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-20 | 0 | 1 | 0 | 0 | 0 | 0 | Mike Beard |  | MACON WATER AUTHORITY | [5 empty] | MACON WATER AUTHORITY | 478-464-5669
2015-12-29 | 2016-01-02 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 594 Industrial Way E, Macon MH 71726 | 1046140 | Fax and email received on 01/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/4/2016 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-31 |  | 1 | Boggy Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Hydraulic overload from the MWA service area recieving 12.62 inches of rain during December 2015. | Debris was removed from the area and the area was disinfected with lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-07 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2018-04-20 | 2018-04-20 |  | Fulton | Atlanta | 6341 Selborn Dr. SW - Atlanta | 5 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program |  | Private Lateral | Ground |  | Unknown |  |  |  | Alys Hannum | 4/21/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown. This is not a city problem. | This is not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-22 | 2016-11-22 | Cobb County Water System | Cobb |  | 4920 Hampton Lake Drive | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/22/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-20 | 2018-02-20 | Fulton County (Big Creek WPCP) | Fulton | Johns Creek | 5150 Taylor Road Johns Creek | 4500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/20/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Johns Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Vandalism | Debris has been removed from the manhole. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-20 | 2018-02-20 | Fulton County (Big Creek WPCP) | Fulton | Johns Creek | 5150 Taylor Road Johns Creek | 4500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/20/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Johns Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Vandalism | Debris has been removed from the manhole. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-22 | 2015-12-16 |  | Cobb |  | 3402 Falling Brook Dr. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  |  |  | Reginald Williamson | 12/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8in DI main | Spread Lime at spill area |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2015-12-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-13 | 2018-08-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | EDIT - PRIVATE 1870 Johnson Rd. NW - Atlanta | 1250 | Fax sent 2018-08-15 UPDATE sent 2018-08-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream | Stream | Debris |  | Alys Hannum |  | Alys Hannum | 8/15/2018 12:00:00 AM |  | 8/13/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | EDIT - PRIVATE Debris in the mainline | EDIT - PRIVATE Crew used a hydraulic pressure cleaner to contain the spill | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-08-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-31 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2708 East Lindsay Dr, Columbus | 14177 | Fax and email received 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Lindsay Creek. | Once the rain subsided, flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-06 | 2016-04-06 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 222 Sleepy Creek Dr., Athens | 172 | Initial email 4/6, full report faxed 4/7 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Equipment failure |  |  | Dagny Pariani | Dagny Pariani | 4/6/2016 12:00:00 AM | Oconee | 4/6/2016 12:00:00 AM |  |  | 1 | swamp to Sleepy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken manhole cover fell into trough of manhole, sewer overflowed | Removed broken manhole cover from trough and replaced cover. Cleaned and limed area. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2018-01-21 | 2018-01-21 | Columbus Water Works CSO | Muscogee | Evans | 3503 Lost Tree Lane, Evans GA 30809 | 2800 | Spill report received via fax. | Raw Sewage | Wastewater Regulatory Program | GA0036838 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 1/22/2018 12:00:00 AM |  |  |  |  | 0 | Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Unplogged sewer main with high pressure jet machine. Cleaned up spill area. Posted signs. Planned follow up to remove roots, camera line to find if any repairs are needed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-01-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-10 | 2015-12-16 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | MLK LIft Station | 5000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2015 12:00:00 AM | Satilla |  |  |  | 0 | Ashburn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags plugged the pumps in the station. | The City workers cleared the pumps and the belt was replaced. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-16 | 2016-03-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1990 Alison Court, SW | 3560 | fax received 3/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/17/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-28 | 2016-07-28 | Cobb County Water System | Cobb |  | 4630 Mavell Rd. | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary to NickaJack Creek. | Cobb Crew stopped the overflow at 4:30. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-23 | 2017-06-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4145 Green Hawk Trail, Decatur | 2080 | Notification received on June 28, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Rags |  |  | Hsin Yeh | Hsin Yeh | 6/23/2017 12:00:00 AM |  |  |  |  | 0 | Fowler Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rag blockage | The problem was corrected at 11:17 hours when the crew rodded the 8" sewer main downstream 129ft, cleared the blockage and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-29 | 2018-03-29 | Locust Grove, City of (Indian Creek WPCP) | Henry | Locust Grove | 4399 Strong rock Parkway | 5000 | Spill report is uploaded. | Raw Sewage | Wastewater Regulatory Program | GA0038849 | Collection System | Stream |  | Other |  | Marzieh Shahbazah | Reginald Williamson | Reginald Williamson | 3/29/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken air relief valve on sanitary sewer force main. Once the manhole was pumped clear to reveal the cause, the flow was closed off while repairs were made to the broken air relief valve and was placed back into operation later the same day. |  | 33e3f7fa-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1326 Graymont Dr. SW - ATL | 600 | Fax received 2017-03-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/28/2017 12:00:00 AM |  | 3/27/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-04 | 2015-12-04 | Cobb County MS4 | Cobb |  | 6400 Highlands Parkway | 600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Vandalism |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 12/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of structural damage causing the manhole to overflow into a t ributary of Nickajack Creek. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-09 | 2016-06-09 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1388 Burton Ave, Macon MH ID 58061 | 1200 | Email received on 06/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Roots |  |  | Paul Moisan | Paul Moisan | 6/10/2016 12:00:00 AM | Ocmulgee | 6/10/2016 12:00:00 AM |  |  | 1 | Rocky Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this spill was roots and rags. | Debris was removed from the area and it was disinfected with lime. This line is scheduled to be cleaned and televised, and chemically treated for root control. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-13 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-29 | 2015-05-29 | Oconee County (Calls Creek WPCP) | Oconee |  | manhole located behind Creekside subdivision | 600 |  | Raw Sewage | Northeast District - Athens | GA0050211 | Collection System | Stream | Stream | Debris |  | Steve Walker | Steve Walker | Steve Walker | 5/29/2015 10:00:00 AM | Oconee | 5/29/2015 12:00:00 AM |  |  | 1 | McNutt's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | plugged sewer line resulting in manhole overflow | County work crews reportedly un-plugged the sewer line, cleaned up spill debris and placed signs to notify the public, and issued a public notice. | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | 2015-06-01 | 1 | 0 | 0 | 0 | 0 | 0
2018-03-22 | 2018-03-22 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 4100 Block of Bemiss Road - Valdosta | 1500 | Letter sent 2018-03-27 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Lift Station | Stream | Stream | Contractor |  |  | Alys Hannum | Alys Hannum | 3/27/2018 12:00:00 AM |  | 3/22/2018 12:00:00 AM |  |  | 1 | Cherry Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Malfunctioning bypass equipment installed by a contractor. | Contractor fixed the malfunctioning equipment. Site and its discharge point have been cleaned and disinfected. Notices posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-21 | 2018-06-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | (PRIVATE) 1731 Pryor Rd. SW - Atlanta | 1280 | Fax sent 2018-06-22 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 6/22/2018 12:00:00 AM |  | 6/21/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline. UPDATE - PRIVATE | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-05 | 2018-06-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1388 Piedmont Rd. NE - Atlanta | 2400 | Fax sent 2018-06-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Roots |  |  | Alys Hannum | Alys Hannum | 6/6/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the line | Crew made repairs to the mainline |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-09 | 2017-05-09 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Peachtree Corners | 3564 Corners Way - Peachtree Corrners | 4962 | Fax received 2017-05-10 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 5/10/2017 12:00:00 AM |  | 5/9/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravity Main pipe failure - broken or separated - caused by erosion. | Placed signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-04 | 2016-03-04 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jester's Lake Drive, Jonesboro | 60000 | Fax received on 03/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 3/4/2016 12:00:00 AM |  | 3/4/2016 12:00:00 AM | 2016-03-04 |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 |  |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-04 | 1 | 1 | 1 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 344 Candlewood Drive | 1500 | fax received 5/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/23/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Reed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Unstopped manhole with pike pole. Cleaned up area, washed down manholes, spread lime, and posted signs. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2017-05-07 | 2017-05-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Rd. NE - ATL | 745 | Email received 2017-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/8/2017 12:00:00 AM |  | 5/7/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-26 | 2016-09-26 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | manhole near the Carlton Woods Lift Station, Moultrie | 9000 | Initial voicemail received 9/27 | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System |  |  | Wet weather |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/27/2016 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall caused a slow weep from a manhole | Monitored spill. Cleaned and limed area | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2015-01-17 | 2015-01-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 262 Buckhead Avenue, NE | 1000 | fax received 1-18-2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/15/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-04 | 2015-01-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Hoyt/Brookside Street | 12000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Sam Buckles | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Fork of Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain |  | 455ebb3c-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-490-4613 | CITY OF CORNELIA
2016-10-20 | 2016-10-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2503 Skyland Trail, Brookhaven | 3660 | Notification received on October 25, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 10/20/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 17:30 hours, when a crew pressure washed the 8" sewer main 318ft between the two manholes, cleared the blockage at 210ft and restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-03 | 2017-05-03 | FAIRBURN PUBLIC WORKS | Fulton | Fairburn | 8081 Plantation Creek | 3600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Whitewater Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-12 | 2018-03-12 | Cobb County Water System | Cobb |  | 4667 Patrick Drive | 100 | The crew members found manhole 311-E035 discharging sewage into roadway. Sewage ran into to a storm drain that leads to a tributary to Noonday Creek. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/12/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The Cobb water system crew stopped the overflow at 8:25 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-26 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-16 | 2018-04-18 | Cuthbert, City of (Cuthbert WPCP) | Randolph | Cuthbert | Approximately 1/4 mile west of the intersection of Wall Street and Tote Road along the railroad tracks of the Georgia Southwestern Railroad. | 400000 |  | Raw Sewage | Southwest District | GA0037249 | Force Main | Stream | Stream | Pipe failure |  | Linda Stevens | Linda Stevens | Linda Stevens | 4/18/2018 11:47:00 AM | Flint | 4/20/2018 12:00:00 AM | 2018-04-18 |  | 1 | Town Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | A broken force main pipe caused by the settling of the ground. | Force main was repaired | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 2018-04-26 | 1 | 1 | 1 | 1 | 0 | 0
2018-05-24 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3500 Austell Drive | 19311 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Lindsey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped allowing manhole to return to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1428 Rome Dr. NW - ATL | 5 | Fax sent 2018-01-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 1/17/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-01 | 2017-05-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3440 Boulder Park Dr. SW - ATL | 7755 | Fax sent 2017-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 5/8/2017 12:00:00 AM |  | 5/1/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-12 | 2015-09-12 |  | Clarke | Athens | 1270 Prince Ave. | 1838 | This spill was included on an enforcement action dated 9/22/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Rags |  |  | Dagny Pariani |  | 9/14/2015 12:00:00 AM | Oconee |  |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An accumulation of rags, paper products, and grease blocked the sewer line. | Line was rodded and flushed. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-27 | 2018-08-27 | Waycross, City of (Waycross WPCP) | Ware | Waycross | Manhole overflowed at the intersection of Alpha Street and Ethel Street in Waycross, Georgia. | 7500 | Notification was also provided to the City of Waycross television station (channel 10) and the Waycross Journal Herald. Joel Hall reported during the initial call to the after hours number that no distressed aquatic life was observed. | Raw Sewage | Coastal District | GA0020966 | Collection System | Storm Drain | Stream | Wet weather |  | Brett Berry | Brett Berry | Brett Berry | 8/27/2018 8:25:00 PM | Satilla | 8/28/2018 12:00:00 AM |  |  | 1 | Tributary D Waycross Drainage Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Root cause of the spill was due to unusually high flows experienced in this portion of the sewer collection system - exacerbated by higher than usual flows system-wide in the collection system due to rainfall related I/I issues typical with aging infrastructure. Upon subsequent inspection of the upstream lift station records, it was found that the run times on both pumps at the Garlington Lift Station on the day of the spill were approximately double the average week day run times. | Crew checked other downstream manholes in the collection system and found that levels were generally high throughout the system and no specific blockage was located. By 6:15 PM the flow stabilized and the manhole was no longer overflowing. The City's vacuum truck was mobilized to pump out the catch basins at Alplha Street and Ethel Street and at Alpha and Crawford Street. Signs were posted at the spill site and the locations where the sewage entered the storm water system (catch basins) and Tributary D of the Waycross Drainage Canal. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-08-31 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-12 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Manhole adjacent to storm pond at Lift Station #2, Albany. | 604800 | Phone call and email received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Stream |  | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Percosin Canal System | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | A direct result of what the National Weather Service reported as 8 - 9 tornadoes, plus straight line winds resulting in a power loss to 52 storm and sanitary lift stations. | Full power to all stations was not restored until 01/14/2017. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2016-03-07 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2345 Ripplewater Drive, Atlanta | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | Entrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hole found in top of creek crossing pipe | Sewer main repaired |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-05 | 2017-06-05 | Thomaston, City of | Upson | Thomaston | City Hall Lift Station located near 3rd Avenue | 450 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/5/2017 12:00:00 AM | Flint |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Water run-off appears to be a cause of the overloading of the station. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-26 | 2016-03-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 64 The Prado, NE | 1225 | fax received 3/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/28/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-27 | 2016-03-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 250 | fax received 3/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/28/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used construction material to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-14 | 2015-10-14 | Paulding County (Coppermine Road WPCP) | Paulding |  | Outfall line to Cadilac L/S | 1500 | Water being tested, monitor and jet line monthly | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Grease |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 10/15/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed Tributary to Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage, Grease | Jetted and Cleared lines, removed debris | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-10-15 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Alvey |  | PAULDING COUNTY - COPPERMINE WRF
2016-04-02 | 2016-04-02 | Broxton | Coffee | Broxton | West Avenue North | 6500 |  | Raw Sewage | Coastal District | GAJ020124 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/4/2016 8:41:00 AM | Satilla | 4/4/2016 12:00:00 AM |  |  | 1 | Unnamed Tributary | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lightning strike on phase converter and secondary pump. | Electrical repairs were made and pump restarted. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-04-20 | 1 | 1 | 0 | 0 | 0 | 0
2017-10-12 | 2017-10-12 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Industrial Park Lift Station in Eastman, GA | 5000 | Incident did not enter into state waters per City personnel. | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground | N/A | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 9/11/2017 12:00:00 AM | Ocmulgee | 9/11/2017 12:00:00 AM |  |  | 0 | N/A - Did not enter state waters | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rainfall and power outage at lift station from Hurricane Irma event. | 9/20/2017 - Received written report of incident and copy of PN distributed in the legal organ (Dodge County News) on September 20, 2017. 10/11/2017 - Written report received including start and stop times, and documentation showing TV, Radio, and health department were notified of incidents. Pictures of PN at spill locations also provided | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-10-03 | 1 | 1 | 1 | 0 | 0 | 0
2016-12-05 | 2016-12-05 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | MLK Lift Station | 150000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/12/2016 12:00:00 AM |  |  |  |  | 0 | Ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rainfall | The City stopped the spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-21 | 2016-06-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 576 | fax received 6/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/22/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | partially collapsed mainline | The crew performed a point repair |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-17 | 2018-07-17 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | 34 Hickory Trace Circle - Swainsboro | 1000 | Phone call received 2018-07-17 | Raw Sewage | Wastewater Regulatory Program | GA0039225 | Collection System | Ground |  | Grease |  |  |  | Alys Hannum | 7/17/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Line was cleared with a jet truck and lime applied to spill site. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-09 | Savannah, City of (President Street WRF) | Chatham | Savannah | Lift Station 22 Chambers/Allen, Savannah, GA | 1590 |  | Raw Sewage | Coastal District | GA0025348 | Lift Station | Canal | Canal | Natural Disaster |  |  | Dagny Pariani |  | 10/10/2016 12:00:00 AM | Savannah | 10/9/2016 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage during Hurricane Matthew. No generator at lift station. | Set up portable generator. Cleaned area with vac truck. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | Savannah I&D Treatment Plant, Port Wentworth, GA | 75 | Initial call and full report received 1/20/2017. | Raw Sewage | Coastal District | GA0038326 | Force Main | Ground, Storm Drain, Stream | Stream | Pipe failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 1/20/2017 12:00:00 AM | Savannah | 1/20/2017 12:00:00 AM |  |  | 1 | St. Augustine Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Break in 3" force main from sewage grinder station | Turned grinder station off. Repaired break in main. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-01-23 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2015-01-30 | 2015-01-30 | Savannah, City of (President Street WRF) | Chatham | Savannah | 1 International Drive - Savannah Trade Center – Hutchinson Island | 1350 |  | Raw Sewage | Coastal District |  | WWTP | Storm Drain | Shoreline | Grease |  | Steve Fox | Steve Fox | Steve Fox | 1/30/2015 12:00:00 AM | Savannah | 1/30/2015 12:00:00 AM | 2015-01-30 |  | 1 | Savannah River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Three overflowing manholes caused by grease blockage in sewer main | Broke blockage and cleaned area with lime. City FOG (fats, oils and grease) staff will investigate local business grease control procedures. The sewer / storm water mix was pumped from the storm drainage system. However, a portion of the release did make it to the Waters of the State. Notification were posted at the east and west side of the Trade Center on the Savannah River. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who notifies local media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-02-03 | 1 | 1 | 1 | 0 | 0 | 0
2018-05-18 | 2018-05-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 80 Peachtree Pl. NE - Atlanta UPDATE - PRIVATE | 6 | Fax sent 2018-05-19 UPDATE - PRIVATE | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/19/2018 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline UPDATE - PRIVATE | Crew used a hydraulic pressure cleaner to contain the spill UPDATE - PRIVATE |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-25 | 2016-07-25 | Dekalb County (Snapfinger Creek WPCP) |  | Clarkston | 764 Jolly Ave. Clarkston | 2280 | Notification received on July 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/25/2016 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 12:25 hours when the crew pressure washed the 8" sewer main, cleared blockage of grease at 60 ft to restore service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-27 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 54000 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 16:41 hours, when the rain subsided and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-09 | 2017-08-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3714 Roswell Rd. NE - ATL | 20 | Email received 2017-08-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Unknown |  |  | Alys Hannum | Alys Hannum | 8/10/2017 12:00:00 AM |  | 8/9/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-22 | 2018-05-22 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Northpoint Parkway near 399- Stock Building Supply | 2600 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Katie Meade | Kathy Lewis | Katie Meade | 5/22/2018 12:00:00 AM |  |  |  |  | 1 | Unnamed tributary to Clark Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags, rocks, debris in line | Cleared all materials and jetted line | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-23 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-23 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Crane Ferry and Warren Road - Augusta | 13680 | Email received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County Area. | Will assess the system via flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-23 | 2015-02-23 |  | DeKalb | Decatur | 4406 Snapfinger Woods Drive, Decatur | 5390 | Notification received on February 26, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/24/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The problem was corrected at 13:35 hours when a crew pressure washed the 10" sewer main upstream 420ft, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-06 | 2015-09-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill Street, NW | 11400 | CTS No. 77776 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/18/2015 12:00:00 AM |  |  | 2015-09-07 | 2016-09-28 | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Collapsed line |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-04 | 2018-04-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1424 Northeast Expressway Atlanta GA 30329 | 2940 | manhole 18-156-s060 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/4/2018 6:31:00 PM | Ocmulgee | 4/4/2018 12:00:00 AM |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-24 | 2015-02-24 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1794 Alvarado Terrance, SW | 1700 | fax received 2/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-03 | 2015-06-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 672 Siloam Avenue, SE | 304 | fax received 6/04/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 6/4/2015 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew installed a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-22 | 2015-10-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 3531 Dial Drive, Stone Mountain | 255 | Notification received on October 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/22/2015 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:14 hours, when a crew inserted a gooseneck into the surcharging manhole, removed the grease blockage which was in the invert and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-10 | 2015-09-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2384 Spring Creek Road, Decatur | 22507 | Notification received on September 16, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 9/10/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole Damage | The problem was corrected at 15:15 hours, when a crew, repaired the manhole defect with hydraulic concrete and bricks. While other crew cleaned, deodorized, disinfected the area around the manhole and restored regular services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-23 | 2017-05-23 | Thomaston, City of | Upson | Thomaston | City Hall Lift Station 3rd Avenue | 5635 |  | Raw Sewage |  |  | Collection System |  |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/23/2017 12:00:00 AM | Flint |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3.17 inches of rain |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-03 | 2017-08-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1085 Ferncliff Rd. NE - ATL | 1575 | Fax received 2017-08-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/4/2017 12:00:00 AM |  | 8/3/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-06 | 2017-03-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2693 Preston Drive, Decatur | 1325 | Notification received on March 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/6/2017 12:00:00 AM |  |  |  |  | 0 | Doless Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:03 hours when a crew pressure washed the 8" sewer main between manholes 250ft, removed the blockage at 150ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 |  | Columbus Water Works (South WRF) | Muscogee | Columbus | 4531 Bedford Court, Columbus, GA | 8258 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Upatoi Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Upatoi Creek. | Once the rainfall subsided, and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-29 | 2015-03-29 |  | DeKalb | Doraville | 216 Winterspark Drive, Doraville | 37900 | Notification received on March 30, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/30/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots, grease and rags blockage | The problem was corrected at 00:45 hours when a crew pressure washed the 8" sewer main 150ft, removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-02 | 2015-10-05 | BELL CREEK WPCP | Upson | Thomston | 180 DOT Drive, (Bell Creek WWTP) | 40000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/2/2015 12:00:00 AM | Flint | 10/3/2015 12:00:00 AM |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rains | The facility turned on the 6" bypass pump | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | 400 block of West Gordon Street, Douglas | 30000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/4/2016 11:30:00 AM | Satilla | 2/5/2016 12:00:00 AM | 2016-02-05 |  | 1 | Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | The spill was caused by heavy rainfall and inflow & infiltration. | Plans are to widen the scope of sewer line investigation. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-02-16 | 1 | 1 | 0 | 0 | 0 | 1
2015-03-03 | 2015-03-03 | Cobb County MS4 | Cobb |  | 3843 Spring Meadow Drive | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/3/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tanyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Tanyard Creek. | The Water system crew stopped the overflow at 10:40 a.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 2017-04-05 | Covington, City of (Covington WRF) | Newton | Covington | Bridgestone Pump Station - Covington | 2145 | Email received 2017-04-06 | Raw Sewage |  | GAJ020055 | Pump Station |  |  | Power failure |  |  | Alys Hannum | Alys Hannum | 4/6/2017 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Breaker tripped to pump power supply. | Breaker was reset and pump power was resumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-17 | 2017-05-17 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 6813 Saganaw Dr., Rex Manhole - 2206593 | 2400 | Fax received on 05/18/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 5/18/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Cleared line, and flow returned to normal |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-19 | 0 | 1 | 1 | 0 | 0 | 0 | Billy Vondenbosch |  | CLAYTON COUNTY WATER AUTHORITY
2017-08-02 | 2017-08-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 2826 Thombriar Road, Doraville | 10 | Notification received on August 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/2/2017 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Damaged manhole | The problem was corrected at 12:08 hours when the contractor stopped pressure washing the main, which stopped the sewer from coming out of the damaged manhole, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-24 | 2017-05-24 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6338 Ashwood Drive, Columbus | 672 | Fax received on 05/25/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 5/25/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Roaring Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the sewer pipe. | Debris was removed, and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-13 | 2015-09-13 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | Woodstock Knoll Pump Station | 2200 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 9/16/2015 12:00:00 AM | Coosa |  |  |  | 0 | unnamed creek to Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at pumping station, the panel blew a fuse transferring power to the generator. The line to the SCADA system was cut by a contractor and was not able to call out the alarm. | Fuse was replaced and the pumping station is now running normal. AT & T was contacted to repair the line to the SCADA System. Area of spill cleaned up and lime was spread in affected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Moon | 770-592-6000 | CITY OF WOODSTOCK
2015-09-13 | 2015-09-13 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | Woodstock Knoll Pump Station | 2200 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 9/16/2015 12:00:00 AM | Coosa |  |  |  | 0 | unnamed creek to Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at pumping station, the panel blew a fuse transferring power to the generator. The line to the SCADA system was cut by a contractor and was not able to call out the alarm. | Fuse was replaced and the pumping station is now running normal. AT & T was contacted to repair the line to the SCADA System. Area of spill cleaned up and lime was spread in affected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | Wendy Brasfield | 770-592-6000 x1701 | CITY OF WOODSTOCK
2015-09-13 | 2015-09-13 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | Woodstock Knoll Pump Station | 2200 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 9/16/2015 12:00:00 AM | Coosa |  |  |  | 0 | unnamed creek to Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power failure at pumping station, the panel blew a fuse transferring power to the generator. The line to the SCADA system was cut by a contractor and was not able to call out the alarm. | Fuse was replaced and the pumping station is now running normal. AT & T was contacted to repair the line to the SCADA System. Area of spill cleaned up and lime was spread in affected area. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Hooper | 770-592-6000 | CITY OF WOODSTOCK
2016-08-30 | 2016-08-30 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 72.6 TSS, weekly average concentration (mg/L): permit = 30, reported = 94 Flow was 0.981 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 72.6 | 94
2017-01-13 | 2017-01-13 | Swainsboro, City of (Yam Grandy Creek WPCP) | Emanuel | Swainsboro | Success Street & Prosperity Drive - Swainsboro | 900 |  | Raw Sewage |  | GA0039225 | Collection System | Reservoir |  |  |  |  | Alys Hannum | Alys Hannum | 1/13/2017 12:00:00 AM |  |  |  |  | 1 | Lake Caroline / Lake Terresa | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause was not mentioned. | Fecal coliform monitoring initiated upstream and downstream, Health department notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Cobb County Water System | Cobb |  | 2600 Oak Village Place | 2900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/8/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 506 S. McDonough Street, Decatur | 15740 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 21:50 hours, when the heavy rain subsided and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-05 | 2017-11-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 800 Gresham Ave. SE | 1185 | Fax sent 2017-11-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/6/2017 12:00:00 AM |  | 11/5/2017 12:00:00 AM |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Cred used a hydraulic pressure cleaner to clear the blockage |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-02 | 2018-02-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2043 Abby Lane, Atlanta GA 30345 | 1220 | manhole 18-194-s020 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/2/2018 3:29:00 PM | Ocmulgee | 2/2/2018 12:00:00 AM |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | pressure washed main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-29 | 2018-05-29 | Hartwell, City of (Hartwell WPCP) | Hart | Hartwell | Jailhouse Branch | 37500 | email sent. Written as follow Mr. Rodenbaugh On May 29 at 1450 we had a spill that effected Jailhouse Branch the spill was cause by heavy flows due to a storm that came through that afternoon we have one pump in that station due to a piping issue that we are currently getting fix after the flows slowed down the station was able to over come the flow and it stopped spilling at 1720 that evening . We estimated it to be around 250 gpm and calculated it to be 37,500 gallons that went in the Jailhouse Branch we have been collecting sample and all the other protocols per our permit I will be sending a written report on this spill and the spill on 5 /16/2018 at the wastewater plant on cuda Branch Dan Gaines City of Hartwell WWTP cheif operator | Raw Sewage | Wastewater Regulatory Program | GAJ020114 |  | Stream |  | Pipe failure |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/30/2018 12:00:00 AM | Savannah |  |  |  | 1 | Lake Hartwelll | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Pipe failure | Fixing lift station pipe | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-22 | 2018-01-22 | Cobb County Water System | Cobb |  | 1877 Kenwood Road | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spilled stopped at 12:18 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | Stephen McMullers |  | Cobb Water Systems
2016-01-11 | 2016-01-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1908 Delowe Place SW | 850 | fax received 1/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/12/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-30 | 2018-01-30 | Cobb County Water System | Cobb | Marietta | 27 Pine Valley Trl | 900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/4/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Concrete |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-19 | 2015-04-20 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | City of Social Circle Little River WPCP | 382790 | Verbal and fax notification received 4/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | WWTP | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 4/20/2015 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Facility experienced hydraulic overload due to excessive rain. Facility personnel had to turn off treatment units to allow wastewater to flow through the plant without treatment. | When hydraulic overload ceased, the treatment units were turned back on. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-20 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2015-03-24 | 2015-03-24 |  | Gwinnett | Snellville | 3073 Glynn Mill Drive | 1860 | fax received 3/24/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/24/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed 8" main with hydro jet. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-01-28 | 2017-01-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 200 Paris Drive - Lawrenceville | 2871 | Fax received 2017-01-28 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum |  | 1/28/2017 12:00:00 AM |  | 1/28/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Little Suwanee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris - wipes, paper, and other products. | Raked area and spread lime, placed signs at spill and waterway. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-30 | 2015-11-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3249 Bret Way, Decatur | 1875 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/30/2015 12:00:00 AM |  |  |  |  | 0 | Cobb's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 12:30 hours when a crew pressure washed the 8" sewer main 320' cleared the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-10 | 2017-05-15 | Cobb County Water System | Cobb |  | 4061 King Springs Rd. | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Laurel Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-24 | 2015-01-24 | Canton, City of (Canton WPCP) | Cherokee |  | Manhole located off Anderson Avenue, behind Hardee's | 25000 |  | Raw Sewage | Mountain District - Cartersville | GA0025674 | WWTP | Stream |  | 3rd party contractor |  | Cindy Nix | Kathy Lewis | Cindy Nix | 1/26/2015 12:00:00 AM | Coosa |  |  |  | 0 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line was impacted by construction debris, towels, mop heads and grease. | The obstruction was removed and the line was cleared of the blocking debris utilizing a jetting machine. Lime and straw were applied to the affected area surrounding the manhole where the spill occured. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | Clint Curl | 678-983-6795 | CITY OF CANTON
2018-07-13 | 2018-07-13 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1457 Rock Hill Drive | 2400 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/13/2018 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Tanyard Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-10 | 2018-01-10 |  | Fulton |  | 2345 Morris Rd. College Park, GA 30349 | 6600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/10/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Re-flushed sewer line while on site. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-16 | 2018-07-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2185 Chevy Chase Lane Decatur GA 30032 | 1000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/17/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Cobbs Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Crack in 24" concrete creek crossing | Built bern around crack, installed temporary 24" FC clamp 24" DIP for final repair |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-20 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-24 | 2018-05-24 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | Behind 4233 Citation Place - Snellville | 8078 | Fax sent 2018-05-24 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/24/2018 12:00:00 AM |  | 5/24/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Jack's Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, Paper, and other products | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-21 | 2017-02-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1402 Foxhall Lane, Atlanta | 7620 | Notification received on February 22, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/21/2017 12:00:00 AM |  |  |  |  | 0 | Entrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:15 hours when a crew pressure washed the 8" sewer main 350ft, removed the blockage at 290ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-08 | 2015-04-08 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM |  |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 38 mg/L on 04/08/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-22 | 2016-06-22 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 5495 Sugar Crossing Drive | 6216 | fax received 6/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/23/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Richland Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and affected wateray |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-02-28 | 2015-03-19 |  | Cobb |  | 2332 Milstead Circle N.E. | 310 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/28/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morgan Farm Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Morgan Farm Lake. | The overflow left gray water discharging from manohole with lid on leaving damp area to creek. Solids were contained inside the manhole. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Manholes just upstream of Utoy Creek WRC | 500 | ongoing. Verbal notification received 11/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/2/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | As of 11/02/2015, this spill is ongoing |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-18 | 2015-03-18 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1053 East Rock Springs Road, NE | 584 | fax received 3/19/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/19/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-29 |  |  | DeKalb |  | 3430 Kensington Road | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-13 | 2017-04-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 627 Utoy Cir. SW - ATL | 1220 | Fax received 2017-04-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/14/2017 12:00:00 AM |  | 4/13/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-13 | 2017-07-13 | Cobb County Water System | Cobb |  | 148 Rhodes Drive | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/13/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The spill was stopped at 6:15 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-03 | 2017-07-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Constitution Rd. SE - ATL | 525 | Fax received July 4th, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 7/4/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2667 Peyton Road, NW | 30 | emailed spill report received 12/26/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/26/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-12 | 2017-09-12 | Columbus Water Works (South WRF) | Muscogee | Columbus | 7301 Marne Road, Ft. Benning - Columbus | 2759 | Telephone call received 09/12/2017. Fax received on 09/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/12/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Upatoi Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 10" sewer main developed a break. | Once the break in the line was discuvered, crews made repairs and the spill was stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-23 | 2018-01-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3954 Memorial College Avenue, Clarkston GA 30021 | 2700 | posted 4 signs | Raw Sewage |  | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/23/2018 5:28:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek Tributary C | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole 18-043-s058 spilling due to grease blockage | Pressurewashed manhole |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Dechavion D Will |  | Dekalb Co Dept. Watershed Management
2015-01-26 | 2015-01-26 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3313 Pinestream Road, NW | 1460 | fax received 1/27/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/27/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-02 | 2016-09-02 | Douglas, City of (Southeast WPCP) | Coffee |  | Brantley Blvd. & S. Gaskin Ave | 90000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/2/2016 11:15:00 AM | Satilla | 9/2/2016 12:00:00 AM | 2016-09-03 |  | 1 | Un-named tributary of Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Hydraulic overload of the collection system from Tropical Storm Hermine. |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-09-08 | 1 | 1 | 0 | 0 | 0 | 0
2017-12-12 | 2017-12-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3878 Woburn Drive Tucker Georgia 30084 | 5600 | 4 signs posted | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/12/2017 4:08:00 PM | Ocmulgee | 12/12/2017 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease blockage | Pressure washed manhole 18-187-s020 |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-13 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Tonya Whatley |  | Dekalb County Department of Watershed Management
2015-09-08 | 2015-09-08 | Newton County (Yellow River WPCP) | Newton | Covington | 355 Lakeside Point | 2400 | fax received 9/09/2015. This was a secondary spill caused by the dislodging of debris that was causing a spill at another manhole upstream. | Raw Sewage | Wastewater Regulatory Program | GAJ020013 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/8/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Beaverdam Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and toilet paper from first blockage became lodged in downstream pipe | jetted line to remove blockage | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | NEWTON COUNTY WATER & SEWERAGE AUTHORITY | 770-786-1414
2015-02-26 |  | Dublin, City of (Dublin WPCP) | Laurens | Dublin | Manhole near 400 Saxon Street | 11025 | Verbal and email notification received 2/26/2014 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Dublin Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction work. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-27 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF DUBLIN | 478-277-5046
2016-12-09 | 2016-12-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | I-75 Ramp Southbound Connector, ATL | 830 | Fax received on 12/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/10/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 4045461328 | ATLANTA, CITY OF
2017-07-03 | 2017-07-03 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Manhole#9790 - Riverside Pkwy, Douglasville, GA | 1900 | Email received on 07/03/2017; Fax received on 07/05/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Lift Station | Stream | Shoreline | Power failure |  |  | Paul Moisan | Paul Moisan | 7/3/2017 12:00:00 AM | Chattahoochee | 7/3/2017 12:00:00 AM |  |  | 1 | Palmer Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Breaker tripped in lift station control panel. | The mechanic who discovered the spill was able to reset the breaker and pump station controls and get the pumps back online. Crews cleaned and disinfected the area around the manhole where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-06 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-25 | 2017-01-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3195 Panther Trl SW - ATL | 600 | Fax received on 01/26/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/26/2017 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | the cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2018-04-24 | 2018-04-24 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 2821 Kingstream Way - Snellville | 3481 | Fax sent 2018-04-24 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/24/2018 12:00:00 AM |  | 4/24/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Big Haynes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, Paper, and Other Products | Removed all deposited solids, placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-17 | 2016-11-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4280 Celebration Dr., SW, Atlanta | 4025 | Fax received on 11/18/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/18/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic Pressure cleaner. Placed on periodic inspection schedule. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-16 | 2018-04-16 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4937 Lisa Court, Columbus | 4384 | Fax sent 4/17/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Paul Moisan | 4/17/2018 12:00:00 AM |  |  |  |  | 0 | Dram Branch Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 8" sewer main was clogged with debris causing an overflow. | An 8" sewer main was clogged with debris causing an overflow. Once the debris was cleared the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-04-17 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | CITY OF PERRY PUBLIC WORKS FACILITY | Houston | Perry | 750 Vallley Dr Pump Station | 7200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/12/2017 12:00:00 AM | Unknown |  |  |  | 0 | Big Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage from a Tropical Storm | The spill stopped at 5:00 pm September 12, 2017. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-23 | 2016-09-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2892 Eastwyck Circle, Decatur | 4500 | Notification received on September 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/23/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected on September 23, 2016 at 13:36 hours when a crew pressure washed the 8" sewer main 93ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-12 | 2017-03-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1302 Piedmont Ave. NE - ATL | 580 | Fax received 2017-08-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Undefined blockage in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-02 | 2018-08-09 | Patterson, City of (Patterson WPCP) | Pierce | Patterson | Manhole located on Dallas St. & Hwy. 32, Williams St. and Echols St. | 4000 |  | Raw Sewage | Coastal District | GA0037206 | Collection System | Ditch | Ditch | Wet weather |  | Brett Berry | Brett Berry | Brett Berry | 8/3/2018 10:00:00 AM | Satilla | 8/7/2018 12:00:00 AM |  |  | 1 | Patterson Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Spill occurred following heavy rainfall of 2.5 inches in less than thirty minutes. | Signage placed at the location of the spill site. Local health dept and local media are being notified. | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-08-07 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-02 | 2015-12-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Road, SW | 166 | fax received 12/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Unknown |  |  | Kim Hembree | Kim Hembree | 12/3/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-29 | 2016-01-29 | Tifton, City of (New River WPCP) | Tift | Tifton | 205 Maple Street, Tifton, GA | 250 | Email received on 02/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System |  |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/1/2016 12:00:00 AM |  |  |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewer line was blocked with grease. | Blockage was removed, and hydrated lime was spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-01 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-23 | 2018-04-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 MeLaine Court Decatur GA 30032 | 102037 | manhole 15-184-s004 Revision from over 8000 gallons | Raw Sewage |  | GA0024147 | Collection System |  |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/23/2018 5:00:00 PM | Ocmulgee | 4/23/2018 12:00:00 AM |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | storm event | wait to end of storm event |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-09 | 2015-10-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2291 Burnt Creek Road, Decatur | 20800 | Notification received on October 12, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/9/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | A suction hose to a sanitary sewer pump malfunction. | The problem was corrected at 11:00 hours when a crew reconnected the suction hose to the pump inside the manhole stopped the spill and restore regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-19 | 2016-09-19 |  | Cobb |  | 4659 Newell Drive/Roswell Road | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-19 | 2016-11-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3451 Glenwood Road, Decatur | 1540 | Notification received on November 22, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/19/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 15:53 hours, when a crew rodded 8" sewer main 150ft, clearing the blockage at 144ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-18 | 2015-11-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1170 Howell Mill Road, NW | 646 | FAX RECEIVED 11/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 11/19/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-08 | 2018-05-08 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 171 Gwinnett Drive - Lawrenceville | 5367 | Fax sent 2018-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Vandalism |  |  | Alys Hannum | Alys Hannum | 5/8/2018 12:00:00 AM |  | 5/8/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Pew Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris as a result of vandalism | Raked area and spread lime, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-16 | 2015-03-16 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 480 Montgomery Ferry Road, NE | 715 | fax recieved 3/17/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/17/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-17 | 2015-04-17 | Savannah, City of (President Street WRF) | Chatham | Savannah | 2148 Graham Avenue | 1200 |  | Raw Sewage | Coastal District |  | WWTP | Ditch |  | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 4/17/2015 12:00:00 AM | Savannah | 4/17/2015 12:00:00 AM | 2015-04-17 |  | 1 | Savannah River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Force main failure – break in pvc pipe | Repaired break in force main and contained flows in ditch to assure sewage did not reach storm system. City of Savannah Jet Vacuum Trucks were utilized to contain and remove sewage. Spread lime on contaminated areas and samples were taken at spill site and downstream from discharge. Spill notification markers were placed at the spill site and at the discharge into storm ditch across from 61 Graham Ave. No recreational access in area. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-05-18 | 1 | 1 | 1 | 0 | 0 | 0
2017-11-19 | 2017-11-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1339 Andrews St. NW - ATL | 1980 | Fax sent 2017-11-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/20/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-04 | 2016-11-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2222 Donald Lee Hollowell Pkwy., NW, Atlanta | 625 | Fax received on 11/05/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/5/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline | Hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-15 | 0 | 1 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2015-12-27 | 2015-12-27 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 6750 Bay Point, Macon MH ID 69253 | 2700 | Fax and email received on 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024538 | Collection System | Reservoir |  | Roots |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Upper Ocmulgee | 12/28/2015 12:00:00 AM |  |  | 1 | Lake Tobesofkee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was roots. | Debris was removed from the area and the affected area was disinfected with lime. The line is scheduled to be cleaned and televised and will be chemically treated for root control. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-10-28 | 2015-10-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2950 Hardman Court, NE | 394 | fax received 10/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/28/2015 12:00:00 AM |  |  |  |  | 0 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew repaired the mainline. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-20 | 2017-04-20 | Cobb County Water System | Cobb |  | 2850 Paces Ferry Rd | 830 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | 2850 Paces Ferry Rd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-12 | 2018-07-12 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 39 East May Street - Winder | 3000 | Fax sent 2018-07-12 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream | Stream | Rags |  |  | Alys Hannum | Alys Hannum | 7/12/2018 12:00:00 AM |  | 7/12/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. to Fort Yargo Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper towel blockage | Jetted main to relieve blockage. Sanitized area with powdered lime. Installed new manhole, CCTV. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-14 | 2015-05-14 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  |  | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 83.6 mg/L on 05/14/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 169 Woodbine Circle SE - ATL | 750 | Fax received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This was a rain induced spill. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2017-04-20 | 2017-04-21 | Dekalb County (Snapfinger Creek WPCP) |  | Lithonia | 4664 Flat Bridge Road, Lithonia | 20 | Notification received on April 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/21/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A structure defect on a 1.5 inch pipe with a pinhole leak. | The problem was corrected at 07:45 hours when a crew turned the water off and completed the repair at 17:00 hours. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-25 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1964 East Starmount way, Decatur GA 30032 | 31500 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/7/2018 6:57:00 PM | Ocmulgee | 2/7/2018 12:00:00 AM |  |  | 1 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm event and heavy infiltration | Wait till end of storm event |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-15 | 2017-11-15 | Cobb County Water System | Cobb |  | 2529 Park St / Watts Dr | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8" Clay Main | Spilled stopped at 7:34 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-20 | 2017-12-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road Ellenwood, GA 30294 | 103950 | combination of storm event and mainetnance | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/21/2017 5:53:00 PM | Ocmulgee | 12/20/2017 12:00:00 AM |  |  | 1 | South River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | A bar screen was off line for repair, causing overflow | Got A bar screen running |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-21 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  |  | Collin Decker |  | Dekalb Co Dept. Watershed Management
2017-09-20 | 2017-09-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 4431 Lawrenceville Highway, Tucker | 69500 | Notification received on September 22, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/20/2017 12:00:00 AM |  |  |  |  | 0 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Pump failure | The problem was corrected on September 20, 2017 at 17:40 hours when DeKalb County crews removed grease from the wet well, restarted the lift station, stopped the spill, and returned normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-25 | 0 | 1 | 0 | 1 | 0 | 0
2015-08-22 | 2015-08-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1046 McConnell Drive, Decatur | 1600 | Notification received on August 24, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/22/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:00 hours, when the clean-up crew, rodded the sewer main downstream, eliminated obstruction at 27 ft and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-04 | 2016-11-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 345 Ashwood Ave., SW, Atlanta | 1880 | Fax received on 11/05/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/5/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-15 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-10-12 | 2017-10-12 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 400 Block of Connell Road - Valdosta | 3475 | Phone call 2017-10-13. Letter sent 2017-10-16, received 2017-10-23. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream | Stream | Debris |  | Alys Hannum | Alys Hannum | Alys Hannum | 10/13/2017 12:00:00 AM |  | 10/12/2017 12:00:00 AM |  |  | 1 | Two Mile Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Buildup of debris inside the sewer line. | Blockage removed, staff began cleanup, disinfection, and monitoring of the impacted area and spill location. Warning signs posted. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-26 | Tifton, City of (New River WPCP) | Tift | Tifton | 80 Old Brookfield Road | 2000 | REC CALL 2/27/2015 | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Emily Wingo | Emily Wingo | Emily Wingo | 2/27/2015 12:00:00 AM | Suwannee | 2/27/2015 12:00:00 AM |  |  | 1 | New River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | All pumps at Gum Creek list station turn on and overwhelmed influent list station at Treatment plant. Overflowed at manhole that feeds into influent list station on treatment plant ground. | Run Gum Creek lift station manually to prevent all pumps turning on at the same time | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Scott Murphy |  | ESG Operations, Inc. |  | CITY OF TIFTON | 229-391-3937
2015-12-25 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 7574000 | Due to multiple events occurring at this location during a short amount of time, this overflow was not confirmed with EPD until 1/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/21/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-18 | 2017-12-18 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange |  | 20254 | At lift station | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Stream |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/19/2017 12:00:00 AM | Chattahoochee | 12/19/2017 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | rock backfilled against pipe during main installation | Damaged section replaced with new pipe |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-27 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-06 | 2017-02-06 | Cobb County Water System | Cobb |  | Cherry Hill Drive | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cherry Hill Drive | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris causing it to overflow into Sope Creek. | The Water System was notfied at 10:45 a.m. and ur crew stopped the overflow at 11:30 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1800 Block of Remer Lane | 321225 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-30 | 2017-01-30 | Cobb County Water System | Cobb |  | 4650 Amberwood Trace | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of debris causing it to overflow into Willeo Creek. | The Water System was notified at 12:12 and our crew stopped the overflow at 1:16 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-07 | 2017-12-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 526 Ross St. SW - ATL | 100 | Fax sent 2017-12-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 12/8/2017 12:00:00 AM |  | 12/7/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-15 | 2017-03-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3158 Beech Drive, Decatur | 270 | Notification received on March 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 3/15/2017 12:00:00 AM |  |  |  |  | 0 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor | The problem was corrected on March 15, 2017 at 16:29 hours when a crew vacuumed the sewer amin, stopped the overflow, and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-20 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-30 | 2016-08-30 | Cobb County (RL Sutton WRF) | Cobb | marietta | 3182 Johnson Ferry Road | 370 |  | Raw Sewage | Wastewater Regulatory Program | GA0026140 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/30/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-29 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Creekside Subdivision, Lagrange | 23000 | Fax received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream | Stream | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee |  | 2015-12-29 |  | 1 | Dixie Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Second wave of heavy rainfall. | Continued search for sources of I/I. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Manhole TRK-0002 206 Sycamore Way | 74450 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 11/2/2015 12:00:00 AM | Chattahoochee | 11/3/2015 12:00:00 AM |  |  | 1 | Soque River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rainfall | Areas affected by spill have been cleaned up and powdered lime has been applied. The city of Clarkesville has already contacted Midway Electric to confirm that the pumps at Lift Station 2 were running at peak efficiency. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | Justin Allen | 706-754-4216 | City of Clarkesville
2016-12-21 | 2016-12-21 | Cobb County Water System | Cobb |  | 4932 Lakeland Dr / Hampton Lake Dr | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/21/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-07 | 2018-01-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Rd. SW - ATL | 645 | Fax sent 2018-01-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/8/2018 12:00:00 AM |  | 1/7/2018 12:00:00 AM |  |  | 1 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-16 | 2017-05-16 | Rome, City of (Coosa WRF) | Floyd |  | West Rome Community approximately 90 feet behind 106 S. Hughes Street | 4000 |  | Raw Sewage | Mountain District - Cartersville | GA0024341 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 5/17/2017 12:00:00 AM | Coosa |  |  |  | 0 | Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots | The sewer main was thoroughly cleaned and repaired | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-13 | 2017-01-13 | Forsyth County (Fowler WRF) | Forsyth | Cumming | 6580 Fox Creek Dr. - Cumming | 250 | Fax received 2017-01-17 | Raw Sewage | Wastewater Regulatory Program | GA0038695 | Collection System | Stream |  | Debris |  | Kim Hembree | Alys Hannum | Hsin Yeh | 1/13/2017 12:00:00 AM |  |  | 2017-01-23 | 2018-01-24 | 1 | Unnamed Tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Grease construction materials (2x4's and asphalt) | Jetted sewer line until blockage was freed; flushed line to clean once it was free flowing. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 1 | 0 | 1 | 1 | 0
2017-01-13 | 2017-01-13 | Forsyth County (Fowler WRF) | Forsyth |  | 6580 Fox Creek Dr. - Cumming | 250 | Fax received 2017-01-17 | Raw Sewage | Wastewater Regulatory Program | GA0038695 | Collection System | Stream |  | Debris |  | Kim Hembree | Alys Hannum | Hsin Yeh | 1/13/2017 12:00:00 AM |  |  | 2017-01-23 | 2018-01-24 | 1 | Unnamed Tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | Grease construction materials (2x4's and asphalt) | Jetted sewer line until blockage was freed; flushed line to clean once it was free flowing. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 1 | 0 | 1 | 1 | 0
2015-12-30 | 2015-12-30 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3203 Flint Drive, Columbus | 19941 |  | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Wet weather. | Area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-30 | 2018-08-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Clayton | 965 Jester Creek CT. Manhole 2206973 | 6000 |  | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Pipe failure |  |  | Juan Robles | Juan Robles | 8/31/2018 12:00:00 AM | Flint |  |  |  | 0 | Flint | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural collapse of a sewer pipe. | Damaged pipe was repaired. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-09-04 | 0 | 1 | 1 | 0 | 0 | 0
2018-08-13 | 2018-08-13 | Valdosta, City of (Mud Creek WPCP) | Lowndes | Valdosta | 1638 New Statenville Hwy - Mud Creek WPCP - Valdosta | 135000 | Phone call received 2018-08-13 | Undisinfected Primary Effluent | Wastewater Regulatory Program | GA0020222 | WWTP | Stream | Stream | Hydraulic Overload |  | Alys Hannum | Alys Hannum | Alys Hannum | 8/13/2018 12:00:00 AM |  |  |  |  | 1 | Knight's Creek/Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | "After a quick assessment, we discovered a clogged effluent screen on the east train secondary clarifier. Due to excessive flow thru the clarifier, algae had sloughed off the weirs and clogged the drain. The water level in the clarifier had risen above the weirs and was draining into the scum pit. At this point, the flow overcame the scum pit pumps and the clarifier effluent overflowed from the pit into a nearby retention pond that drains to Knight’s Creek." | "After cleaning the screen, clarifier levels returned to normal at 11:30 pm. We informed our Environmental Manager of the overflow, who immediately began sampling and monitoring the effected stream. To prevent an overflow of this type from occurring again, we added procedures to monitor clarifier effluent drains more frequently and will also increase cleaning frequency. " | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-17 | 2016-05-17 | Savannah, City of (President Street WRF) | Chatham | savannah | 3709 Clinch Street | 560 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Grease |  | Steve Fox | Steve Fox | Steve Fox | 5/17/2016 12:00:00 AM | Savannah | 5/17/2016 12:00:00 AM |  |  | 1 | springfield canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Grease blockage in gravity sewer main and increased by major rain event caused an overflow of storm water and sewage mix from a manhole to the storm system | Reduced flows to spill by reducing flow from an upstream sewer lift station. Spill notification markers were placed at the spill site where discharge went into canal and along other locations – Springfield Canal / West Gwinnett Street and Bowles Ford Park / Springfield Canal. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-01 | 1 | 1 | 0 | 0 | 0 | 0
2016-04-26 | 2016-04-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3985 Dogwood Farm Road, Decatur | 8900 | Notification received on April 29, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/27/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defect on the sewer main | The problem was corrected at 13:15 hours, when the blockage cleared itself, restoring normal flow. Repairing the hole is in progress. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-22 | 2015-11-22 | Tifton, City of (New River WPCP) | Tift | Tifton | 806 Bellmont Ave., Tifton, GA 31794 | 1000 | Email received on 11/23/2015; although the spill report states 11/23/2015, the spill occurred on 11/22/2015. | Raw Sewage |  | GA0048470 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 11/23/2015 12:00:00 AM |  | 11/23/2015 12:00:00 AM |  |  | 1 | New River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tifton collection system experienced a minor sewer spill at the manhole located at 806 Belmonth Ave. The cause of the spill was due to a grease blockage. | Hydrated lime was spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-29 | 2016-10-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Woods St., N.W., Atlanta | 1650 | Fax received on 10/29/2016; corrected report received by fax on 10/31/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 10/29/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was a by-pass pump malfunction. | The crew repaired the by-pass pump to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-10 | 2017-03-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 750 | Fax received Saturday, 2017-03-11 Location updated 2017-10-31 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Paul Moisan | 3/11/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was equipment failure. | Crew made repairs to the by-pass pump. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-07 | 2016-12-07 | Rome, City of (Rome WRF) | Floyd |  | Armuchee Community at the Swan Lake Mobile Home Park | 3500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Grease |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 12/7/2016 12:00:00 AM | Coosa |  |  |  | 0 | Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease and roots in the sewer main | The sewer main was thoroughly cleaned and crews have begun cleanup and removal procedures | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-23 | 2015-01-23 |  | Lowndes | Valdosta | 1194 JoRee Street | 4500 | Verbal notification by John Waite with City of Valdosta received 1/23/2015. Email follow-up from City sent 1/24/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/23/2015 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-05-24 | 2018-05-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 3515 Austell Drive | 106968 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Lindsey Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, manhole has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-20 | 2018-02-20 | Coweta County Water & Sewerage Authority (Shenandoah WPCP) | Coweta | Newnan | Niagara way Newnan, GA | 4038 |  | Raw Sewage | Wastewater Regulatory Program | GA0038822 | Lift Station |  | Ditch |  |  | Alys Hannum | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/23/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Brak in force main | repaired facilities | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-07 | 2016-03-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1957 Glenwood Ave. Atlanta | 25 | Notification received on March 8, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/7/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 18:09 hours, when a crew clamped the sewer main to seal the leak, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-08 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-05 | 2015-01-05 |  | Cobb |  | 234 Brookcliff Trace | 540 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/1/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and Silt in 8 Inch DIP Main | Flushed Main and Limed Spill area. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-05 | 2018-06-05 | Macon Water Authority (Rocky Creek WPCP) | Macon |  | 2141 General Winship Drive, MH ID 71370 | 4800 | The MWA had to hire a contractor to make this repair. The estimated completion date for this repair is Thursday, June 7th. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Ditch | Pipe failure |  | Reginald Williamson | Juan Robles | Juan Robles | 6/6/2018 12:00:00 AM | Ocmulgee | 6/5/2018 12:00:00 AM |  |  | 0 | Ocmulgee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that the cause of this spill was a broken sewer main. | Debris has been removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-08 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-30 | 2017-01-11 | Cobb County Water System | Cobb |  | 3276 Autumn Woods Trail | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of debris ausing it to overflow into a tributary to Mud Creek. | The Water System was notified and the crew stopped the overflow at 5:15 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-25 | 2016-02-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2699 Peachtree Road, NE | 890 | fax received 2/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/26/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-31 | 2018-05-31 | Villa Rica, City of (Tallapoosa West WPCP) |  | Villa Rica | City of Villa Rica Gravity Line | 4000 |  | Raw Sewage | Wastewater Regulatory Program | GA0027162 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/31/2018 12:00:00 AM |  |  |  |  | 0 | Towns Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a root ball blockage in the gravity sewer line that caused the flow to back up and spill through an upstream man hole. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-17 | 2017-02-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 6875 | Notification received on February 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Operator error |  |  | Hsin Yeh | Hsin Yeh | 2/17/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to the construction a pump turned off. | The problem was corrected at 9:40 hours when a crew turned on the pumps to stop the overflow and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-19 | 2016-05-19 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2761 Walnut Creek Road, Macon MH ID#59931 | 1440 | Fax received on 05/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 5/24/2016 12:00:00 AM |  | 5/19/2016 12:00:00 AM |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After blockage was removed, it was determined that the cause of this spill was grease and rags. | Debris was removed from the area, and the area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-26 | 1 | 1 | 0 | 0 | 0 | 0
2018-01-09 | 2018-01-09 | Oconee County (Calls Creek WPCP) | Oconee |  |  | 24000 |  | Treated Effluent | Northeast District - Athens | GA0050211 | WWTP |  |  | Hydraulic Overload |  | Phoebe Tchoua | Phoebe Tchoua | Phoebe Tchoua | 1/9/2018 12:00:00 AM |  |  | 2018-01-09 |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Effluent composite test results were calculated at 38.6 mg/L with a weekly avg max of 15 mg/L | Working on reducing solids inventory, improving settling, and working through the backlog of influent solids in the system | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 384e7336-1c4e-11e1-9fd5-12313b0cb679 | 2018-05-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4473 Sarr Parkway Stone Mountain | 1955 | Notification received on September 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/11/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:29 hours , when a crew pressure washed the 8" sewer main 298(ft) clearing the grease blockage at 145(ft), which restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-29 | 2015-01-29 |  | Rockdale |  | 1137 Brett Drive | 2480 | Received by Fax on 1/30/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Sarita Banjade | Sarita Banjade | 1/29/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Almand Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Removed Debris |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Rockdale Water Resources | 7702787500
2015-02-24 | 2015-02-24 | Cobb County MS4 | Cobb |  | 1190 Kennestone Circle N.W. | 320 | The overflow left sewer discharging from manhole with lid in place. Sewer water ran down drainage ditch 10' x 110' to storm drain culvert. No sewer water indicated in storm drain at this time. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of solids in sewer main causing the manhole to overflow into a tributary of Noonday Creek. | The Water System was notified at 12:19 p.m and our crew stopped the overflow at 3:00 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-14 | 2016-11-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 319 Lincoln St., SW, ATL | 0 | Fax received on 11/15/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Paul Moisan | Paul Moisan | 11/15/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill is unknown at this time, and spill is continuing. Investigation is ongoing. | Crew has responded. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-06 | 2015-05-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1247 Donald Lee Hollowell Parkway, NW | 15 | fax received 5/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/7/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-07 | 2017-06-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 130 Barry Street, Decatur | 2100 | Notification received on June 9, 2017 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/9/2017 12:00:00 AM |  |  |  |  | 0 | Peavine Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken 6" lateral | The problem was corrected on June 7, 2017 at 17:24 hours when the crew replaced the leaking 6" lateral and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-12 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-24 | 2017-09-24 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 144 W. Midland Avenue - Winder | 3600 | Email received 2017-09-24 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream | Stream | Roots |  |  | Alys Hannum | Alys Hannum | 9/24/2017 12:00:00 AM |  | 9/25/2017 12:00:00 AM |  |  | 1 | Tributary to Cedar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots protruded into 6" sewer main. | Main was jetted and cleared. Area sanitized with lime. Will TV the main to determine the cause and whether the pipe needs to be replaced. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-06 | 2018-04-06 | Rome, City of (Rome WRF) | Floyd |  | Directly behind 114 Cherry Street | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/6/2018 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary leading to Horseleg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer main | Sewer main has been thoroughly cleaned. Sewer spill mitigation protocol has been completed. The sewer main will be inspected with CCTV | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-20 | 2018-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2333 Peachtree Rd. NE - Atlanta | 290 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/21/2018 12:00:00 AM |  | 4/20/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-19 | 2017-03-19 | Cobb County Water System | Cobb |  | 3950 Mars Hill Road | 880 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/19/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Allatoona | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-29 | 2018-06-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1021 Harwell Rd. NW | 205 | Fax sent 2018-06-29 Correction sent 2018-07-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/2/2018 12:00:00 AM |  | 6/29/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-12 | 2018-06-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3731 Buford Highway Atlanta GA 30329 | 100 | 18-203-P049 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/12/2018 3:19:00 PM | Ocmulgee |  |  |  | 1 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Pressure washed 8" line from manhole 18-203-s052 to manhole 18-203-s051 200ft to clear blockage at 75ft |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-17 | 2017-08-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1753 Dodson Dr. SW - ATL | 8205 | Fax received 2017-08-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 8/18/2017 12:00:00 AM |  | 8/18/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-30 | 2015-07-30 | Cobb County MS4 | Cobb |  | 1852 King Arthurs Court | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/30/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a reslut of solids in sewer main causing the manhole to overflow into a tributary of Sope Creek. | The spill was stopped at 12:16. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-28 | 2016-11-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3073 Pantersville Road, Decatur | 10000 | Notification received on December 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/29/2016 12:00:00 AM |  |  |  |  | 0 | Doless Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease | The problem was corrected at 16:08 hours, when a crew pressure washed the 10" sewer main 216ft, clearing a frease blockage at 210ft and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-02 | 0 | 1 | 0 | 1 | 1 | 0
2017-10-23 | 2017-10-23 | Cobb County Water System | Cobb |  | 3411 Belleford Court | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 9:10 a.m. and our crew stopped the overflow at 10:25 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-23 | 2016-10-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 821 Celeste LN, SW, Atlanta | 940 | Fax received on 10/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/24/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the main line. | The crew used a hydraulic pressure cleaner to contain the spill. This area will be placed on periodic inspection schedule to determine the need for upgrading, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-20 | 2016-12-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 645 11th Street, NW, ATL | 1596 | Fax received on 12/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/21/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew used a hydraulic pressure cleaner. Area has been placed on periodic inspection schedule. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell |  | ATLANTA, CITY OF
2017-01-24 | 2017-01-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3929 Wedgefield Circle, Decatur | 2820 | Notification received on January 25, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/24/2017 12:00:00 AM |  |  |  |  | 0 | Fowler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:21 hours when the crew rodded the 8" sewer main 72 ft upstream, cleared the grease blockage at 63 ft, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-27 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-02 | 2016-03-02 | Columbia County (Crawford Creek WPCP) | Columbia | Evans | 621 Chimney Hill Circle | 100 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Betty's Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "Equipment failure" | "Fixed equipment. Cleaned up spilled area. Posted signs." |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2015-11-10 | 2015-11-10 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1372 Conway Road, Decatur | 25 | Notification received on November 16, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/10/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing Leaking | The problem was corrected at 17:29 hours when the repairing crew replaced four and half inches (4-1/2") of pipe, to restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-28 | 2015-08-29 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | Remer Lane | 151700 | CTS Nos. 77716 and 77714 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 9/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-13 | 2017-01-13 | Savannah, City of (President Street WRF) | Chatham |  | 601 Cranman Drive and 8809 Rivers End Drive Savannah, Georgia. Spill notification markers were place at both locations. | 2000 |  | Raw Sewage | Coastal District |  | Lift Station | Ditch | Canal | Equipment failure |  | Hailey Harden | Hailey Harden | Hailey Harden | 1/13/2017 1:10:00 PM |  | 1/13/2017 12:00:00 AM |  |  | 0 | Chippewa Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | By-pass pump failure during sewer main repair from washout caused from Hurricane Matthew | Restored pump service and contained water in ditch and set up by-pass pumps which pumped the contaminated water back into sanitary sewer system. | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2017-01-13 | 1 | 1 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jesters Lake Drive, Jonesboro MH # 2215621 | 198000 | Fax received 01/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/23/2016 12:00:00 AM | Flint | 1/23/2016 12:00:00 AM |  |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Capacity. | Lines will be inspected for inflow and infiltration to resolve capacity issues. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 1 | 1 | 0 | 0 | 0
2015-12-24 | 2015-12-27 | Cobb County Water System | Cobb |  | 939 Old Farm Walk | 520 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in manhole/ 8 inch PVC Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive, NW | 600 | fax received 2/04/2016. COA Service Request No. 7518986 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-29 | 2016-02-29 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Hampton | 1052 Knotty Pine Pl., Hampton Manhole 2209049 | 2400 | Fax received on 03/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  |  | Paul Moisan | 3/1/2016 12:00:00 AM | Flint |  |  |  | 1 | Hurricane Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease caused a blockage. | Blockage was cleared and flow returned to normal. Site was cleaned and work orders generated for additional work to determine cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-03-01 | 0 | 1 | 1 | 0 | 0 | 0
2016-09-22 | 2016-09-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4711 Bishop Ming Blvd, Stone Mountain | 13740 | Notification received on September 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/22/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected on September 22, 2016 at 11:00 hours when a crew rodded the manhole 60ft downstream, removed the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-27 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-15 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 66 Northwood Drive | 21840 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Long Island Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-24 | 2016-08-24 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 43 Flow was 0.959 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 43
2017-04-11 | 2017-04-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1556 Habershal Dr. NW - ATL | 10 | Fax received 2017-04-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/12/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-26 | 2018-03-26 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | GA Power Pole 2803 GA Hwy 100 | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/27/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Walker Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Outage, planned work on power by GA Power we were not notified of scheduled work | Power Restored, suggest back up power | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-26 | 2016-10-26 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1935 North Leg Road, Augusta | 9000 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Kim Hembree | 10/27/2016 12:00:00 AM |  |  |  |  | 0 | Tributary Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | The debris in and around the manhole was removed. Notifications of the spill have been placed in the affected area. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-31 | 0 | 1 | 0 | 0 | 0 | 0
2017-04-14 | 2017-04-14 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 5535 Mount Vernon Highway | 3340 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/18/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The manhole has been cleaned. The area impacted by the spill has been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-24 | 2016-03-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4711 Bishop Ming Blvd, Stone Mountain | 2500 | Notification received on March 28, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/24/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing | The problem was corrected at 19:43 hours, when a crew set up a by-pass pump, reroute the sewer flow until the repair is completed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-28 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-20 | 2017-10-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 100 Noble Creek Dr. - ATL | 4350 | Fax sent 2017-10-23 with no address; address on fax cover sheet. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 10/23/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-01 | 2016-07-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 15 Barksdale Drive, NE | 0 | fax received 7/04/2016. Spill volume undetermined | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 7/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2851 Ridgewood Circle, NW | 360000 | fax received 12/25/2015. CTS No. 78624 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Collapsed manhole |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-29 | 2016-02-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 210 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed mainline | The crew made a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-08 | 2015-05-11 | Bickford Senior Living | Cobb |  | 850 LeCroy Drive, Marietta | 5000 |  | Raw Sewage | Mountain District - Cartersville | GAU060067 | Lift Station | Stream |  | Power failure |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 6/1/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wastewater lift station electrical service being terminated without notice from former owner of 850 LeCroy Drive. | Power was restored | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-03 | 0 | 0 | 0 | 0 | 0 | 0 | Richard Eby | 913-782-3200 | Bickford Senior Living
2015-02-27 | 2015-02-27 | East Point (City of)- Sewers | Fulton | East Point | 2638 Meadow Lark Drive between Manhole # C-196-052 and C-196-025 | 7500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the Main resulting into a discharge into the Camp Creek Basin. | The city's crew jetted and vacuumed out the main to remove the blockage, and cleaned the affected area as required. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-27 | 2015-02-27 | East Point (City of)- Sewers | Fulton | East Point | 2638 Meadow Lark Drive between Manhole # C-196-052 and C-196-025 | 7500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the Main resulting into a discharge into the Camp Creek Basin. | The city's crew jetted and vacuumed out the main to remove the blockage, and cleaned the affected area as required. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-28 | 2017-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 893 Margaret Pl. NW - ATL | 35 | Fax sent 2017-11-29 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/29/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-23 | 2015-10-23 | Washington, City of (Rocky Creek WPCP) | Wilkes | Wshington | Off of Garland Avenue. | 4000 | Notification received on October 27, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0031101 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/26/2015 12:00:00 AM |  |  |  |  | 0 | Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Caused by a tree's root system growing into the sewer pipe causing it to bust. | The leak was fixed on October 23, 2015 by replacing a 15 foot section of the damaged pipe. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | 201 Dogwood & Camellia Drive - Dublin | 3240 | Letter received 2017-01-06 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-03 |  | 1 | Dublin Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Repair crew could not find a problem with sewer obstructions to cause backup or open inlets to allow excess surface water runoff to enter the system. Upon continual inspections there were no debris or solid materials overflowing from the manhole onto the street. | The area is part of an ongoing sewer replacement project to replace 3650 LF of existing parallel sewers; work began on the first of December. Authorities have been notified and signs posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-27 | 2016-01-02 | Andersonville, City of (Andersonville WPCP) | Sumter | Andersonville | Outfall 001. | 882000 |  | Treated Effluent | Southwest District | GA0033669 | WWTP | Stream | Stream | Other |  |  | Jay Howell | Jay Howell | 2/23/2016 12:00:00 AM | Flint | 2/24/2016 12:00:00 AM | 2016-02-23 | 2017-02-01 | 1 | Sweetwater Creek to Flint River in Flint River Basin | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive rainfall in area along with I & I in collection system. Continuous totalizer also appears to not be recording flow accurately during time of event. | Flowmeter being recalibrated and rainfall stopped. PN being done for through plant major spill and stream monitoring initiated 2/23/2016. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2016-04-12 | 1 | 1 | 1 | 1 | 1 | 0 | [12 empty] | 10.1 kg/day
2015-01-02 | 2015-01-05 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | Phone call received 1-05-2015. This is an outfall spill of partially treated effluent. The effluent TSS was 44 mg/L for January 2nd; 71 mg/L for January 3rd ; and 41 mg/L for January 4th. The spill volume will not be available until plant operations return to normal | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Filamentous bacteria is causing high TSS values in the R.M. Clayton WRC. This is a major outfall spill due to high effluent TSS. Total volume during the time of TSS violation was 86,600,000 gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-09 | 2015-11-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | email notification received 11/10/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is an outfall spill. TSS Permit Limit = 25 mg/L; TSS Reported Value = 150 mg/L. Total Volume of outfall spill = 124 million gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-23 | 2015-03-23 |  | DeKalb | Stone Mountain | 4547 Birch Ridge Trail, Stone Mountain | 1820 | Notification received on March 25, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/23/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and grease blockage | The problem was corrected at 13:26 hours when a crew pressure washed the 8" sewer main 400ft removed the blocakge and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-20 | 2016-11-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1605 Donald Lee Hollowell Pkwy, NW, ATL | 432 | Fax received on 11/21/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/21/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic Pressure Cleaner |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-19 | 2016-10-19 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1100 Block of North Lee Street | 1500 | Verbal confirmation received 10/19/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Storm Drain, Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 10/19/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-06-28 | 2016-06-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 2100 | EPD notified 7/20/2016 when hard-copy follow-up was received. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/20/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-22 | 2017-10-22 | Cobb County Water System | Cobb |  | 3720 Austell Rd. | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  |  | Reginald Williamson | Reginald Williamson | 10/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots in 8: PVC |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-21 | 2017-09-21 | Cobb County Water System | Cobb |  | 450 Dorset Way | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-15 | 2018-04-15 | Rome, City of (Rome WRF) | Floyd |  | 2610 Garden Lakes Blvd. East side of property facing Venetian Way. | 500 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/16/2018 12:00:00 AM | Coosa |  |  |  | 1 | Lake Conasauga | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in sewer main | Sewer main was thoroughly cleaned. Sewage was vacuumed out of an unnamed tributary leading to Lake Conasauga. Yard at spill site was cleaned and sprayed with biodegradable disinfectant. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-24 | 1 | 0 | 0 | 0 | 0 | 0
2016-10-03 | 2016-10-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2839 Pheasant Drive | 4600 | fax received 10/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/4/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Used jet truck to open sewer segments |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-01-19 | 2015-01-19 |  | DeKalb | Lithonia | 3808 Crossvale Road, Lithonia | 4800 | Notification received on January 20, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/20/2015 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 19:26 hours when a crew pressure washed 8" sewer main 300ft upstream, and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-18 | 2017-06-18 |  | DeKalb | Stone Mountain | 1057 South Indian Creek Drive, Stone Mountain | 1160 | Notification received on June 21, 2017. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/18/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:36 hours when the crew pressure washed the 8" sewer main 89ft, cleared the grease blockage at 69ft and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-21 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-30 | 2017-06-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur | 7750 | Notification received on July 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/30/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | The problem was corrected at 19:15 hours when the storm event subsided and the flow returned normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-10 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-12 | 2015-02-12 |  | Clarke | Athens | 1270 Prince Ave. | 700 |  | R-2 Water | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/12/2015 12:00:00 AM | Chattahoochee | 2/12/2015 12:00:00 AM |  |  | 0 | Brickyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in pipe/rags and grease | Rod and flush line | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 753 Woodward Way, NW | 25 | fax received 1/05/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/5/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-06 | 2016-12-06 | Tifton, City of (New River WPCP) | Tift | Tifton | WWTP - Tifton | 2100 | Phone call received on 12/06/2016. Email received on 12/07/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Shoreline | Wet weather |  | Paul Moisan |  | Paul Moisan | 12/6/2016 12:00:00 AM |  | 12/6/2016 12:00:00 AM |  |  | 1 | New River Basin | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall. | Hydrated lime was spread to mitigate and sanitize the affected area. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-12-08 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-12 | 2018-03-12 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 800 Lake Placid Drive Sandy Springs, 30342 | 23250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/12/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Failure | The sewer system immediately upstream and downstream has been cleaned. The exposed sections of pipe have been replaced. Inhibitors have been applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Lyons, City of (Lyons North WPCP) | Toombs | Lyons | South Washington Street, Lyons, GA 30436 | 5000 |  | Raw Sewage | Coastal District | GA0033391 | N/A | Ground | Ditch | Natural Disaster |  | Beth Stevenson | Brett Berry | Brett Berry | 9/12/2017 12:00:00 AM | Altamaha |  |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowing from flows exceeding he flow capacity of the section of the line. | N/A | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-19 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-15 | 2017-04-15 | Cobb County Water System | Cobb |  | 3421 Washington Commons Ave | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Blue Springs Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" DI main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-04-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-15 | 2017-05-17 | Cobb County Water System | Cobb |  | 446 Fountaine Rd | 160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  |  | Reginald Williamson | Reginald Williamson | 5/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease and debris |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Glenwood Ave SE - ATL | 20 | Fax received on 01/24/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by grease and debris in the mainline. | The spill was self-contained, and the area was placed on periodic inspection schedule to determine the need for upgrade, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2015-05-19 | 2015-05-19 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to be 35.4 mg/L on 05/19/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-31 | 2017-01-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 498 Sterling St. NE - Atlanta | 3 | Fax received on 02/01/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 2/1/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew tood steps to prevent recurrence and placed this area oon periodic inspection schedule. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-22 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2820 Pierce Drive S, Macon MH ID - 64565 | 6745 | Email received on 01/24/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 1/24/2017 12:00:00 AM |  |  |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was hydraulic overload due to heavy rains in the MWA area. | Debris was removed and the area affected was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-08 | 2016-02-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 132 Libby, LN., Jonesboro MH 2216029 | 2700 | Telephone call and fax received on 02/08/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/8/2016 12:00:00 AM | Flint |  |  |  | 1 | Kendrick Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease was found, and blockage was cleaned and flow returned to normal. | Lines will be televised and root cut and if problem is located, it will be repaired. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-10 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-09 | 2015-06-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2748 Seaborn Road, NW | 720 | fax received 6/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/10/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1461 Ellis Street | 21600 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Mid-City | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2017-01-30 | 2017-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2282 Defoor Hills Rd NW - ATL | 324 | Fax received on 01/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/31/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-04 | 2017-02-04 | Cobb County Water System | Cobb |  | 4428 Cove Island Dr. | 1030 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gease in 8 " Ductile Iron Main | Raked and limed area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-05 | 2018-05-05 | Columbia County (Little River WPCP) | Columbia | Evans | 314 Scarlett Court - Evans | 350 | Fax sent 2018-05-07 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Other | Shoreline | Grease |  |  | Alys Hannum | Alys Hannum | 5/7/2018 12:00:00 AM |  | 5/5/2018 12:00:00 AM |  |  | 0 | Private Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Offset pipe and grease | Unstopped sewer main with high pressure jet machine. Cleaned up spill area and posted signs. Follow up cleaning and video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-19 | 2018-07-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1089 Neal Pl. NW - Atlanta | 2000 | Email/Fax sent 2018-07-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/20/2018 12:00:00 AM |  | 7/19/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-11 | 2017-12-11 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 158 Paper Mill Road - Lawrenceville | 5145 | Fax received 2017-12-11 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 12/11/2017 12:00:00 AM |  | 12/11/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 500 Dairy Pak Rd., Athens | 19619 | Initial email 1/22, full report faxed 1/26 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 1/22/2016 12:00:00 AM | Oconee | 1/22/2016 12:00:00 AM | 2016-01-25 |  | 1 | wetlands to North Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Overflow during major rain event | Cleaned the area. Sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-26 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2016-06-05 | 2016-06-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 9700 | fax received 6/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/6/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-21 | 2016-07-21 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8415 Tara Blvd., Jonesboro Manhole #2207320 | 19200 | Fax received on 07/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 7/22/2016 12:00:00 AM | Flint |  | 2016-07-25 | 2017-07-18 | 1 | Robert Reed Tributary | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 0 | Debris in pipe. | Debris removed from pipe that caused pipe to collapse, and made repair. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-29 | 0 | 1 | 1 | 1 | 1 | 0 |  |  |  |  | Jennifer Brandon | 770-302-3462 | CLAYTON COUNTY WATER AUTHORITY
2016-03-09 |  |  | DeKalb |  | 215 Marray Drive | 5 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Placed hose farther down into manhole, replaced hose |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-11 | 2018-06-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 506 South mcDonough Street Decatur GA 30030 | 4000 | manhole 15-214-s013 | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Storm Drain |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/12/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | Wait for storm event to stop |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-01 | 2017-12-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2910 Argyle Dr. NW - ATL | 300 | UPDATE 2018-02-20: Spill volume corrected from 1,960 gallons to 300 gallons. Fax sent 2017-12-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/5/2017 12:00:00 AM |  | 12/1/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-16 | 2018-04-16 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Rd and Sylvia Dr. | 150000 |  | Raw Sewage | Wastewater Regulatory Program | GA0025852 | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/12/2018 12:00:00 AM | Suwannee |  |  |  | 1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Wet Weather |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-16 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-22 | 2018-08-22 | Paulding County (Coppermine Road WPCP) | Paulding |  | East Paulding Lift Station, 1541 East Paulding Drive | 10000 |  | Raw Sewage | Mountain District - Cartersville | GA0038865 | WWRF | Stream |  | Power failure |  | Katie Meade | Kathy Lewis | Katie Meade | 8/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tributary of Possum Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power surge caused station breaker to flop and generator failed to come on | Turned breaker back on, will have generator serviced as well as troubleshoot to see what caused the original power surge. Cleaned up debris, washed down station and placed lime on affected areas. | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-23 | 1 | 0 | 0 | 0 | 0 | 0
2016-04-03 | 2016-04-03 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultrie | 616 2nd Avenue NE, Moultrie | 1000 | Using CCTV, dye, and smoke testing to search for additional I/I issues. | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System |  |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Ochlockonee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy weather impacted the area causing surcharging of the sewer system | Monitoring location. Area limed. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | ESG Operations, Inc. | 478-954-8381
2016-07-04 | 2016-07-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 600 | fax received 7/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/5/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | The crew replaced a mechanical part on the bypass pump. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-03 |  |  | DeKalb |  | 2052 Grand Prix Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-29 | 2017-03-29 | Griffin, City of (Potato Creek WPCP) | Lamar | Griffin | Potato Creek WPCP | 46200 | Notification received on April 4, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0030791 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 3/29/2017 12:00:00 AM |  |  |  |  | 0 | Potato Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor | The spill occurred between 4:50 pm and 5:10 pm for a duration of 20 minutes, allowing 46,200 gallons of wastewater to reach the Potato Creek stream. The spill was caused by a dry weather high flow incident resulting from installation of a gate between the out of service #1 pond, and the plant influent pumping station. The #1 pond had been drained for construction purposes, but had some residual rain water accumulation. The residual rainwater, upon flowing to the influent pumping station, caused the plant headworks to be overwhelmed resulting in the spill. Spalding and Lamar County health departments were notified, as well as City of Thomaston utilities and the local radio stations. Stream monitoring immediately was implemented as per permit requirements. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-04 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-27 | 2015-04-27 | Cobb County MS4 | Cobb |  | 624 River Bend Circle | 250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2015 12:00:00 AM | Chattahoochee | 4/27/2015 12:00:00 AM |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Nickajack Creek. | The Water system was notified at 3:00 p.m. and the crew stopped the overflow at 4:40 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Rose Lane, Toccoa | 7800 | Notification received on February 8, 2018 via fax. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 2/8/2018 12:00:00 AM |  |  |  |  | 0 | Eastanollee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Approximately 1.9 inches of heavy rain was received on Wednesday morning in a very short time frame. This caused the two pumps in the station to be unable to keep up with the incoming flow, although both pumps were running at maximum speed. | The City of Toccoa is continuing tis work to find and eliminate sources of rain flowing into the sanitary sewer system. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-08 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Tifton, City of (New River WPCP) | Tift | Tifton | manhole located at 181 Brookfield Road, Tifton, GA | 1000 | Voice mail received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | New River Basin | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | mitigated by hydrated lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-06 | 2015-02-07 |  | Lowndes | Valdosta | 1900 Block of East Park Avenue (pump station) | 96500 | Phone call from Russ Dorman received 2/06/2015. Email follow up received 2/07/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Equipment failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/6/2015 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | The overflow was caused by a bypass pumping issue at the city pump station on East Park Avenue, which is currently being rehabilitated under the City's pump station rehabilitation program. | The contractor performing this work ordered additional bypass pumps to correct the problem. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-10-17 | 2017-10-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3530 Fairlane Dr. NW - ATL | 1455 | Email sent 2017-10-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/18/2017 12:00:00 AM |  | 10/18/2017 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-26 | 2015-12-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2205 Northside Drive, NW | 500 | fax received 12/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/28/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-27 | 2018-06-27 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 905 Cranberry Trail | 32850 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/26/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Big Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-11 | 2016-02-11 | Cobb County MS4 | Cobb |  | 4835 Archer Place | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/11/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | The crew stopped the overflow at 7:45. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-26 | 2017-01-26 | Cobb County Water System | Cobb |  | 4321 Macland Rd | 350 |  | Raw Sewage |  |  | Collection System |  | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/26/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Wild Horse Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-12 | 2017-12-12 | Savannah, City of (President Street WRF) | Chatham | Savannah | 224 West Boundary Street, Savannah, GA | 2520 | Initial phone call and and emailed full report received 12/12/17. | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Equipment failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 12/12/2017 3:00:00 PM | Savannah | 12/12/2017 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Control failure at lift station resulted in manhole overflow. | Corrected control failure, cleaned spill site. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-18 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6808
2016-11-16 | 2016-11-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5123 N Peachtree Road, Dunwoody | 2220 | Notification received on November 18, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/16/2016 12:00:00 AM |  |  |  |  | 0 | Kingsley Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | The problem was corrected at 13:00 hours, when a crew pressure washed the 8" sewer main 500ft, clearing the blockage at 86ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-21 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-04 | 2017-08-04 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2820 Pierce Drive, S - Macon MH ID 64565 | 1700 | Telephone call received on 08/07/2017; fax received on 08/08/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 8/7/2017 12:00:00 AM | Ocmulgee | 8/8/2017 12:00:00 AM |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was heavy rains in the MWA service area. | Debris was removed from the area, and the affected area was disinfected with lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-10 | 0 | 1 | 0 | 0 | 0 | 0 | Heather Veal | 478-464-5673 | MACON WATER AUTHORITY
2017-07-01 | 2017-07-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2804 Millwood Way, Decatur | 500 | Notification received on July 7, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 7/1/2017 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 13:20 hours when a crew cleaned up the spill area, checked the 8" sewer main which was clear and flowing normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-07 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-02 | 2018-04-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3831 east Avenue Clarkston GA 30021 | 1225 | man hole n/a | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System |  |  | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/3/2018 6:56:00 AM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Brocken sewer pipe | During the excavation to repair broken sewer pipe the sewer stopped getting into the creek and came up in excavation area |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-28 | 2016-11-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2835 Cherry Laurel LN, SW, ATL | 5 | Fax received on 11/29/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/29/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1999 Northside Dr. NW - ATL | 25 | Fax received 2017-08-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/21/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2123 Garden Circle, Decatur | 16550 | Notification received on November 4, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 11/2/2015 12:00:00 AM |  |  |  |  | 0 | Doolittle Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 20:30 hours when a crew delayed until the storm event passed, the water receded, the manhole stopped spilling and resumed to regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-15 | 2018-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 350 Camfield Ct. SW - ATL | 1635 | Fax sent 2018-01-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/16/2018 12:00:00 AM |  | 1/15/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-06 | 2016-09-06 |  | DeKalb | Dunwoody | 2311 Dunwoody Crossing, Dunwoody | 72910 | Notification received on September 7, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/6/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected on September 6, 2016 at 21:00 hours when the crew performed an emergency repair, placing a full circle clamp around the pipe to stop the spill and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-07 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-13 | 2015-05-13 |  | Rockdale |  | 1182 Shadowlawn Drive | 195 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/13/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | A tributary to Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure | Repair Pipe | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-14 | 2015-10-14 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 11/9/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 34.2 mg/L on 10/14/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-04 | Columbia County (Little River WPCP) | Columbia | Evans | 967 Watermark Drive - Evans | 6750 |  | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/6/2017 12:00:00 AM |  | 1/4/2017 12:00:00 AM |  |  | 1 | Euchee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction Debris | Unstopped main with high pressure jet machine. Removed debris, posted signs, follow up inspections. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-05 | 2016-04-05 | Lowndes County (South Regional WPCP) | Lowndes | Valdosta | Val-tech Road | 225000 | Email notification received 4/06/2016 | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 4/6/2016 12:00:00 AM |  |  | 2016-04-06 | 2017-04-25 | 1 | Drainage ditch to Withlacoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Split 16" force main | Repaired pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | LOWNDES COUNTY | 229-561-0360
2016-03-30 | 2016-03-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 236 | fax received 3/31/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/31/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew made a point repair to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-30 | 2017-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 348 Armour Dr NE - ATL | 1225 | Fax received on 01/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 1/31/2017 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was pump malfunction. | The crew replaced the by-pass pump. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-27 | 2017-03-27 | Fulton County MS4 | Fulton |  | 300 Magnolia Walk Ln. College Park, GA 30349 | 1400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-27 | 2015-01-27 | Cobb County MS4 | Cobb |  | 3797 Paul Samuel Rd. | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lake Halisport | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease in 8" PVC MAIN |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-03 | 2016-04-06 | Dawson, City of (Dawson WPCP) | Terrell | Dawson | Manhole 417 at Hwy 82 and Don Foster Rd | 5760 | This sewer line represents a recurring problem for the City. It has been placed on the next SPLOST agenda for funding to correct issues. | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Flint | 4/3/2016 12:00:00 AM |  |  | 1 | Brantley Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4" of rainfall on already saturated ground | Monitored flow. Area will be cleaned and limed as necessary. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Dawson
2016-12-29 | 2016-12-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2165 Cheshire Bridge Rd., NE, ATL | 3210 | Fax received on 12/30/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/30/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-12 | 2016-01-15 | Douglas County (Rebel Trails WPCP) | Douglas | Douglasville | DDCWSA - Rebel Trails WPCP. | 11000 | Email and letter received on 01/19/2016. | Secondary Effluent | Wastewater Regulatory Program | GA0049786 | WWTP | Stream |  | Unknown |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/18/2016 12:00:00 AM | Chattahoochee | 1/19/2016 12:00:00 AM |  |  | 1 | Anneewakee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Unknown process upset causing poor treatment resulting in high TSS. | The plant was pumped out with tank trucks and receded with good activated sludge bacteria from the Sweetwater Creek WPCP. The plant effluent was tanked out daily until the process was fully recovered. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 0 | 0 | 1 | 1 | 0
2016-01-15 | 2016-01-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2345 Adams Drive, NW | 10 | fax received 1/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/16/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-25 | 2016-12-25 |  | Baldwin | Milledgeville | Mayfair Court | 820 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/25/2016 12:00:00 AM |  |  |  |  | 0 | Tobler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The sewage spill occurred due to roots in the sewer line. This caused a blockage. | Unstopped sewer line and limed the surronding area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-11 | 2018-03-11 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 4679 GA Hwy 100 | 60000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Wet weather |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/12/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Tallapoosa River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive storm water infiltration, heavy hydraulic loading, inadequate RAS system, solids overloading | Rain emergency measures were instigated too late and the plant reached more than maximum capacity I (Ronald H Hale) made the decision to release material as it could no longer be contained. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-03 | 2016-06-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 5652 Rex Mill Creek, Rex Manhole 2212123 | 300 | Fax received on 06/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Vandalism |  |  | Paul Moisan | Paul Moisan | 6/3/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Cotton Indian Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-06 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 2398 Union Grove Court, Lithonia | 17875 | Notification received on September 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/12/2017 12:00:00 AM |  |  |  |  | 1 | Pine Mountain Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Storm Event / I&I | The problem was corrected at 10:35 hours when the crews used vacuum trucks to hold the sewer in the wet well until the backup pump was manually activated. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2018-09-06 | 2018-09-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2504 Campbellton Rd. SW - Atlanta | 3 | Fax sent 2018-09-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/7/2018 12:00:00 AM |  |  |  |  | 1 | S. Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe was leaking | Crew performed a point repair |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-02 | 2016-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2310 Metropolitan Parkway, SW | 984 | fax received 2/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/2/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-11 | 2017-05-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1461 Woodbine Ave. SE - ATL | 420 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/12/2017 12:00:00 AM |  | 5/11/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was equipment failure. | Crew made mechanical repairs to the by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-14 | 2018-03-14 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 110 Grogans Landing Sandy Springs, GA 30350 | 14560 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/14/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root Intrusion |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-09 | 2016-11-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2046 Bramble Wood Dr. Atlanta | 3740 | Notification received on November 10, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/9/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 15:00 hours, when a crew pressure washed the 8" sewer main 255ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-10 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-09 | 2016-08-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1936 Glenwood Ave, Atlanta | 35 | Notification received on August 12, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/9/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Right-of-Way/Lateral Issue | The problem was corrected at 16:35 hours when the repair crew changed out the 4" lateral to a 6" lateral and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-12 | 2017-01-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 311 Scott St SW - ATL | 25100 | Fax received on 01/13/2017. Although a major spill (25,100 Gallons), none of the spill made it to waters of the State. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/13/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Waycross, City of (Waycross WPCP) | Ware | Waycross | 512 Alice St. Waycross, GA 31501 | 3857 |  | Raw Sewage | Coastal District | GA0020966 | WWTP | Stream | N/A | Natural Disaster |  |  | Brett Berry | Brett Berry | 9/11/2017 12:00:00 AM | Satilla |  |  |  | 1 | Tebeau Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Irma | N/A |  | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-18 | 1 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 211 Wellington St., SW, ATL | 25 | Fax received on 01/04/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/4/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-03-26 | 2015-03-26 | Thomaston, City of | Upson | Thomaston | 855 N. Church Street, Thomaston, Georgia | 25000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/26/2015 12:00:00 AM | Flint | 3/26/2015 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The spill occurred due to a broken force main. | The force main was repaired and the affected areas were treated with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-15 | 2017-05-15 | Cobb County Water System | Cobb |  | 446 Fontaine Road | 160 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-31 | 2016-08-06 | Rochelle, City of (Southeast WPCP) | Wilcox | Rochelle |  | 0 |  | Treated Effluent | Southwest District | GA0024236 | WWTP | Stream |  |  |  | Jay Howell | Mel Taylor | Jay Howell | 9/21/2016 12:00:00 AM | Suwannee |  | 2016-09-19 |  | 0 | Mill Creek Tributary | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | Spill was not reported by facility, but found by EPD Personnel when reviewing August DMR | City of Rochelle SWPCP was sent a Notice of Violation on 9/22/16 | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 9f235bd8-1668-4732-af3d-ff34e316d5e5 | 2017-01-05 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-19 | 2016-02-19 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Rd. and Sylvia Dr. | 150000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/19/2016 12:00:00 AM | Satilla |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-12 | 2017-08-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 5547 Peachtree Boulevard, Chamblee | 1380 | Notification received on August 15, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/12/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Careek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 17:10 hours when the first responder crew repaired the 8-inch sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-06 | 2015-12-06 | Cobb County (Northwest WRF) | Cobb |  | 3186 Fern Valley Dr. | 340 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/6/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" CI Main | Spread Lime at Spill Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-20 | 2018-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2300 Defoor Hills Rd. NW - Atlanta | 160 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 4/21/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown; this is not a city problem. | None; this is not a city problem. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-20 | 2015-02-20 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 675 Hutchens Road, SE | 20 | fax received 2/821/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/20/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-23 | 2016-08-23 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD weekly average concentration (mg/L): permit = 12, reported = 35.7 Flow was 0.878 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 35.7
2017-06-30 | 2017-06-30 | Warner Robins, City of (Sandy Run Creek WPCP) | Houston | Warner Robins | 102 Fairways Drive, Warner Robins, Ga 31088 | 27000 | Notification received on July 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0030325 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 7/1/2017 12:00:00 AM |  |  |  |  | 0 | Bear Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather | ESG has cleaned the site and posted signs indicating the nature of the spill, as well as contact information. Public notice will appear in Houston Home Journal on July 5, 2017. A sample monitoring program has been initiated. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-03 | 0 | 1 | 0 | 0 | 0 | 0
2017-12-18 | 2017-12-18 | Cobb County Water System | Cobb | marietta | 2395 New Macland Road | 460 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/18/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud and Noses Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-04 | 2016-01-04 |  | Cobb |  | 1919 North Landing Way | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/4/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rubes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Rubes Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-22 | 2018-08-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2900 Landrum Dr. SW - Atlanta | 8 | Fax sent 2018-08-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  |  | Alys Hannum | 8/23/2018 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-22 | 2015-11-22 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Talmadge St., Athens | 55 | Incident reported in monthly overflows to dry land received 12/1 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Ground |  | Rags |  |  | Dagny Pariani | Dagny Pariani | 12/1/2015 12:00:00 AM | Oconee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer line was clogged with rags | Rodded sewer line and checked three manholes downstream to ensure no further issues. Cleaned area of solids and debris. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3495
2016-09-30 | 2016-09-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 950 East Paces Ferry Road, NE | 3540 | fax received 10/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/3/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-27 | 2018-03-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snapfinger Woods Drive, Decatur GA 30035 | 711900 | manhole 16-008-s004 found through source tracking | RO Waters | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/8/2018 10:40:00 AM | Ocmulgee | 3/8/2018 12:00:00 AM |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | manhole discharging into stormwater drain pipe | Rodded |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Thomaston, City of | Upson | Thomaston | City Hall LIft Station | 7560 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/13/2016 12:00:00 AM |  |  |  |  | 0 | Unnamed Tributary Ave L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overload due to heavy rains in the COT service area. | Debris will be removed from the surronding area and the area has been disinfected with lime. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-31 | 2015-03-31 | Cochran WPCP | Bleckley | COCHRAN | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Emily Wingo | Emily Wingo | 4/30/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | JORDON CREEK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | equipment failure at facility |  |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF COCHRAN |  |  |  | 31.7 mg/l
2015-05-08 | 2015-05-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 627 Utoy Circle, SW | 4800 | fax received 5/08/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/8/2015 12:00:00 AM |  |  |  |  | 1 | Utoy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-29 | 2018-01-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 288000 | Location is at Snapfinger facility | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/30/2018 7:09:00 PM | Ocmulgee | 1/29/2018 12:00:00 AM |  |  | 1 | South River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm event and heavy infiltration caused manhole 15-031-s003 to spill into South River | Wait until storm event was over |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-31 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-31 | 2017-10-31 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Grayson | 821 Cooper Rd. - Grayson | 8208 | Fax sent 2017-10-31 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Force Main | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 11/1/2017 12:00:00 AM |  | 10/31/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Big Haynes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Weather - Storm Damage to Gravity Main | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-26 | 2015-02-27 |  | Lowndes | Valdosta | 2410 Meadowbrooke | 87500 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-09-16 | 2015-09-16 | West Point, City of (West Point WPCP) | Troup | West Point | Waterworks Creek, 300 yards from the Chattahoochee River. | 1200 | Email received on 09/18/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020052 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 9/18/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Waterworks Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The problem appeared to be grease in the lines. The city identified two manhole structures in close proximity to the creek bank that had the standard ring and cover. | Clogged gravity line. The line was jetted and cleared of what appeared to be grease in the line. Both manholes had the ring and cover replaced with new gasketed bolt down ring and covers. One of the manholes was the spot of the overflow. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-10 | 0 | 1 | 1 | 0 | 0 | 0
2017-11-15 | 2017-11-15 | Cobb County Water System | Cobb |  | 2831 South Main Street | 270 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel | stopped spill at 5:21 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-20 | 0 | 0 | 0 | 0 | 0 | 0 | Stephen McCullers |  | Cobb Water Systems
2015-02-23 | 2015-02-23 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 851 Oakdale Road, NE | 1325 | fax received 2/24/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/24/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-05-28 | 2015-05-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 301 Clifton Street, SE | 3000 | fax received 5/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-22 | 2016-10-11 |  | Henry | McDonough | 145 Summit View Drive and 160 Glenmore Lane | 2440 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 10/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Wolf Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease accumulation was deemed to be the caused of the blockage. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | Patrick Hembree | 678-583-3902 | Henry County Water Authority
2016-02-05 | 2016-02-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | ATLANTA | 4760 Apache Trail, SW | 2720 | fax received 2/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/6/2016 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The construction crew made a repair to the main line to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-11 | 2017-03-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 53 Perimeter Center East, Atlanta | 5110 | Notification received on March 16, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/11/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:57 hours when a crew pressure washed the 10" sewer main upstream 326', cleared the blockage at 251' and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-16 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-22 | 2016-07-22 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Douglasville South Central WPCP DRY LAND - did not make it to state waters. | 12375 | Email received on 07/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Other |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 7/25/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump control failure at the South Central Influent Lift Station. | Work on issue to prevent from happening again. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-19 | 2015-08-19 | City of Fort Oglethorpe | Catoosa |  | Vero Beach | 8500 |  | Raw Sewage | Mountain District - Cartersville | GAU060002 | Collection System | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 8/21/2015 12:00:00 AM | Tennessee |  |  |  | 0 | Spring Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Substantial Rainfall | The city if currently conducting an SSES on the Main Interceptor Sewers in an attempt to locate sources of Inflow and Infiltration | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | Phillip Parker |  | CITY OF FORT OGLETHORPE
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1400 Gornto | 100200 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2016-02-03 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | Sowell Estate, Stone Mountain | 1440 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event cause overflow | Waited until storm passed and flow returned to normal |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3207 Delmar Ln NW - ATL | 25 | Fax received 2017-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/23/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-17 | 2016-02-17 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | A spill was not recognized to have occurred until the facility received a copy of it's lab results. Weekly average effluent BOD was greater than 50% the permit limit for two days, 2/16 and 2/17. BOD, Weekly average concentration (mg/L): permit = 12, reported = 30.7. Daily flow was 1.16 MGD. | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 3/16/2016 12:00:00 AM | Ogeechee | 3/16/2016 12:00:00 AM | 2016-03-16 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Outfall spill caused by an imbalance in the loadings of the facility due to heavy rainfall. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-21 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 30.7
2017-06-06 | 2017-06-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 111 West Paces Ferry Rd. NW - ATL | 300 | Email received 2017-06-07. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 6/7/2017 12:00:00 AM |  | 6/6/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-06 | 2017-04-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 149296 | Notification received on April 11, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/6/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 14:20 hours when the crews at Snapfinger Treatment Plant opened valves and operated pumps to stop the sewer from entering the storm drain. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-12 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-01 | 2016-02-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 54th Prado, NE | 75 | fax received 2/02/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/3/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-13 | 2016-04-13 | Grovetown, City of | Columbia | Grovetown | Manhole across from 3034 Ashland Way in Grovetown | 5000 |  | Raw Sewage | Northeast District - Augusta | GAJ020222 | Force Main | Ground, Storm Drain, Stream | Stream | Roots |  | Delaine Scott | Delaine Scott | Delaine Scott | 4/13/2016 12:00:00 AM | Savannah | 4/14/2016 12:00:00 AM | 2016-04-14 | 2016-04-18 | 1 | Unnamed Tributary to Euchee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The raw sewage overflow was due to roots growing within the sewer main which overtime collected grease and other solids resulting in the line clog and eventual overflow at a nearby manhole which was buried during the construction of the home. | The sewer line was jetted, roots removed and the line was cleaned. The area surrounding the manhole overflow was cleaned - grease and paper was removed and a layer of lime was applied to the entire area. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2016-04-14 | 1 | 1 | 0 | 0 | 0 | 0 | Raymond Fulcher |  | CITY OF GROVETOWN
2015-01-31 | 2015-01-31 | Cobb County MS4 | Cobb |  | 866 Chestnut Lake Dr. | 460 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/31/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease in 8" PVC Main | Cleaned and spread lime at spill area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-30 | 2016-06-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1024 Litherland Court, SE | 2350 | fax received 7/01/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/1/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-14 | 2015-07-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 246 Patterson Avenue, SE | 30 | fax received 7/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 7/15/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Someone removed the bypass pump hose from the manhole |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-26 | 2017-06-26 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn |  | Gascoigne Lodge at 1000 New Sea Island Road, St. Simons Island | 10000 |  | Raw Sewage | Coastal District | GA0021521 | Lift Station | Other | Channel | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 6/9/2017 11:21:00 AM | Satilla | 6/9/2017 12:00:00 AM | 2017-06-09 |  | 1 | Gascoigne Pond | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Electrical equipment malfunction at sewer lift station (2023) | Repaired electrical equipment at the lift station (2023), aerated affected area to raise DO. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-06-26 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Rd. SW - ATL | 2860 | 5 Day report received in the mail 2017-10-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/11/2017 12:00:00 AM |  | 9/13/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unspecified. May be connected to spill at 796 Gracewood Ave. SE on the same day. | Unspecified. May be connected to spill at 796 Gracewood Ave. SE on the same day. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-14 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb |  | 1515 Sheridan Road | 500 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-08 | 2016-03-08 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3526 Edgeworth Drive | 4750 | fax received 3/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/9/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2015-12-02 | 2015-12-02 | Dallas North WPCP | Paulding |  | Behind City Barn | 7500 |  | Raw Sewage | Mountain District - Cartersville | GA0026034 | WWTP | Stream |  | Roots |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 12/3/2015 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root Blockage | Jetted with root cutter to free blockage cleaned up debris, limed infected area | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | Kendall Smith | 770-443-8117 | City of Dallas - North WPCP
2015-12-02 | 2015-12-02 | Dallas North WPCP | Paulding |  | Behind City Barn | 7500 |  | Raw Sewage | Mountain District - Cartersville | GA0026034 | WWTP | Stream |  | Roots |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 12/3/2015 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root Blockage | Jetted with root cutter to free blockage cleaned up debris, limed infected area | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | Brandon Rakestraw | 770-443-8117 | City of Dallas - North WPCP
2018-05-06 | 2018-05-06 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 275 McDonald Road, Tallapoosa | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 5/8/2018 12:00:00 AM | Tallapoosa |  |  |  | 1 | Abrams Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in a sewer main caused man hole to over flow | The City Crew responded to a call and found blockage in the sewer line. The blockage was removed and flow was restored. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-10 | 1 | 0 | 0 | 0 | 0 | 0
2018-05-04 | 2018-05-04 | Marietta (City of)- Sewers | Cobb | Marietta | 763 Bonnie Dell Dr | 98 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Unknown | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/4/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/Construction |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-09 | 2016-12-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2196 Cheshire Bridge Rd, NE, ATL | 222 | Fax received on 12/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/10/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-1328 | ATLANTA, CITY OF
2017-01-02 | 2017-01-05 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Lift Station #3, Albany. | 682500 | Telephone call and emails received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Lift Station | Canal |  | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Percosin Canal system | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The National Weather Service reported 8 - 9 tornadoes plus straight line winds resulting in power loss to 52 storm and sanitary lift stations. | Full power to all stations was restored on 01/14/2017. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2017-10-18 | 2017-10-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 180 Howell Dr. SW - ATL | 25 | Fax sent 2018-02-20 after discrepancies noted in the semi-annual report. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 2/20/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The main line was holding and caused the clean out to overflow. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-11 | 2017-02-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 150 | Fax received Sunday 2017-02-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Paul Moisan | 2/12/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-26 |  | Lowndes | Valdosta | 1404 Gornto Road | 157500 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-08-11 | 2016-08-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4347 Flats Shoals Parkway, Decatur | 406 | Notification received on August 17, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/11/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 15:00 hours when the repair crew used concrete to reinforce the seal, stopped the leak and restored normal serice. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-18 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-15 | 2015-09-15 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 1049 Daventry Crossing, Woodstock | 1200 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 9/16/2015 12:00:00 AM | Coosa |  |  |  | 0 | Fitzgerald Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken PVC pipe blocked the line | CCWSA Construction Crews jetted the line and removed the PVC and debris | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 678-313-1947 | Cherokee Co W & S Authority
2017-01-13 | 2017-01-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1831 Briarcliff Circle, Atlant | 1120 | Notification received on January 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/13/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:33 hours when the crew pressure washed 195 ft upstream, cleared the blockage at 130 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 500 Block of Mack Drive | 51900 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-12 | 2017-01-12 | Gwinnett County (Yellow River WPCP) | Gwinnett | Liliburn | Behind 100 Woodcliff Dr - Liliburn | 9488 | Fax received 2017-01-12 | Raw Sewage | Wastewater Regulatory Program | GA0047911 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/12/2017 12:00:00 AM |  | 1/12/2017 12:00:00 AM |  |  | 1 | Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products | Raked area and spread lime, then placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-02 | 2016-05-02 |  | Henry | Stockbridge | 142 Augusta Drive in Stockbridge, Georgia | 6210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/2/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Pates Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The blockaage in the line was caused by rags and towels. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-05-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-04 | 2016-08-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1505 Chattahoochee Avenue, NW | 615 | fax received 8/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/5/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-20 | 2017-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 269 Fielding LN SW - ATL | 1210 | Fax received on 01/21/2017. Physical Letter received 02/07/2017 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a mechanical rod and hydraulic pressure ceaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2016-06-30 | 2016-06-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6039 Hillandale Drive, Lithonia | 2760 | Notification received on July 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/30/2016 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 15:07 hours, when a crew pressure washed the sewer main 240ft, clearing the grease blockage and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-07-05 | 0 | 1 | 0 | 0 | 0 | 0
2016-06-06 | 2016-06-06 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4320 Warm Springs Road, Columbus | 730 | Telephone call and fax received on 06/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 6/6/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Cooper Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris causing a manhole to overflow. | Once the debris was cleared from the main the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-28 | 2016-08-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 550 Johns Landing Way | 2306 | fax received 8/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/28/2016 12:00:00 AM |  |  |  |  | 1 | Pugh Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Crews shoveled up and removed debris from roadway. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-10-11 | 2017-10-11 | Cobb County Water System | Cobb |  | 2215 Creek Way Dr. | 880 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Barrett Creek Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-21 | 2015-09-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 381 Mt. Zion Road, SW | 75 | fax received 9/22/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/22/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-14 | 2015-09-14 | Savannah, City of (Georgetown WPCP) | Chatham | Savannah | Sewer manhole at inter-section of Barksdale Drive / Barksdale Way | 330 |  | Raw Sewage | Coastal District |  | WWTP | Ditch | Ditch | Grease |  | Steve Fox | Steve Fox | Steve Fox | 9/14/2015 12:00:00 AM | Savannah | 9/14/2015 12:00:00 AM |  |  | 1 | Grove River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | y | 0 | Manhole overflows due to grease blockage (residential area) | Cleared blockage and cleaned street curb line. Spill notifications will be placed at spill site where Barksdale Dr. crosses ditch and where Grove Point Road crosses ditch. All entities (Georgia Environmental Protection Division, Heath Dept. and City Public Information Office who will send out a news release to the media) were contacted | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-09-16 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Lift station H-5 located on Homer Avenue. | 1000 |  | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ditch | Ditch | Power failure |  | Jay Howell | Jay Howell | Jay Howell | 2/24/2016 2:00:00 PM | Ocmulgee | 2/25/2016 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | power failure. power restored in 15 minutes using portable bypass pump | power restored, solids removed from area and lime was put down. PN provided at outfall, health dept and all local media. written cert. provided 3/16/2016 along with copy of PN and notifications of local media. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2016-03-21 | 1 | 1 | 1 | 0 | 0 | 0 | Rusty Ashley | (229) 868-6051 | City of McRae-Helena
2018-01-31 | 2018-01-31 | Coleman Environmental, LLC (Village At Mountain Ridge WPCP) | Forsyth |  | Dosing tank discharged at SW corner of facility | 9058 |  | Raw Sewage | Mountain District - Cartersville | GAJ030769 | WWRF | Stream |  | Equipment failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/1/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Unnamed Tributary to Setting Down Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | LAS dosing system failure due to N clarifier failure | Cleaned out dosing tank via pump truck Got N clarifier functioning cleaned dosing system filters and got it back online. Working on affected area clean up. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-28 | 2015-07-28 | Blue Ridge, City of (Blue Ridge WPCP) | Fannin |  | 361 Austin Street | 800 |  | Raw Sewage | Mountain District - Cartersville | GA0037583 | WWTP | Stream |  | Roots |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 7/28/2015 12:00:00 AM | Tennessee |  |  |  | 0 | Unnamed stream on Austin Street | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and Grease in gravity sewer line | Line was jetted and roots & grease removed | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | James Weaver | 706-633-9489 | City of Blue Ridge
2016-01-30 | 2016-01-30 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 7592 Stonebush Way, Douglasville WSA Manhole 10272 | 640 | Fax received on 02/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 2/1/2016 12:00:00 AM | Chattahoochee | 1/31/2016 12:00:00 AM |  |  | 1 | Mill Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A sag in the sewer line caused a blockage. | A jet truck was used to clean the line and clear the blockage. Crews cleaned and disinfected the area where the spill occurred. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-08-17 | 2015-08-17 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 6144 Wandering Way | 1660 | fax received 8/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/18/2015 12:00:00 AM |  |  |  |  | 1 | Jackson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | flushed the main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-06-24 | 2018-06-24 | Cobb County Water System | Cobb |  | 359 Farm Place Ct. | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/24/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-05 | 2016-05-05 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Mansfield Street - Manhole located on the north end of the Harold Pate Bldg. | 150 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Storm Drain | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 5/5/2016 12:49:00 PM | Satilla | 5/5/2016 12:00:00 AM |  |  | 1 | unknown | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by a contractor's bypass pump failure (Mansfield Storm Drain Project). | JWSC responded using VacCon trucks to stop the spill while the contractor corrected the problem with their by-pass pumps. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-05-10 | 1 | 1 | 0 | 0 | 0 | 0
2015-01-12 | 2015-01-12 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 6009 Seren Cove, Woodstock | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Vandalism |  | Cindy Nix | Kathy Lewis | Cindy Nix | 1/14/2015 12:00:00 AM | Coosa |  |  |  | 0 | Rose Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandals opened a manhole and threw debris into the sewer system. A log was found blocking the pipe. This caused grease and debris to build up and plug the line. | CCWSA Construction Crews removed the log, jetted the line and removed the grease and debris. Lime was spread around the area saturated by wastewater. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 770-591-7156 | Cherokee Co W & S Auth
2017-04-18 | 2017-04-18 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 3455 Sandstone Trail | 1020 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson |  | Reginald Williamson | 4/18/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-28 | 2018-08-28 | Buford, City of (Southside WPCP) | Gwinnett | Buford | 2045 Buford Highway & 2033 Buford Highway - Buford | 9999 | Volume reported as "<10,000" Call made 2018-08-29 | Raw Sewage | Wastewater Regulatory Program | GA0023167 | Collection System | Ground |  | Debris |  | Reginald Williamson | Alys Hannum | Alys Hannum | 8/29/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sediment in the mainline | Cleared blockage, washed line. Vacuumed sediment. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-13 | 2016-02-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 536 Hollydale Court, NW | 15 | fax received 2/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/14/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew mad a repair on the mainline to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-03 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 819 Barrett Lane - Augusta | 300 | Fax received 2017-01-03 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM |  |  | 0 | Tributary to Raes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause was heavy rainfall, debris and rags. | Line reopened and resumed normal flow. Notices posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-06 | 2015-10-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3611 Woodbriar Circle, Tucker | 3240 | Notification received on October 8, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/7/2015 12:00:00 AM |  |  |  |  | 0 | Southfork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:02 hours, when a crew pressure washed the 8" sewer main 400ft, cleared the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-02 | 2016-03-02 | Fulton County (Big Creek WPCP) | Fulton | sandy springs | 240 Franklin Road Sandy Springs, 30342 | 6620 | Received email on 3/2/2016 from Mr. Glen Smith. | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The manhole has been cleaned. The section of the sewer system is being mitigated. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-02 | 2016-03-02 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 240 Franklin Road Sandy Springs, 30342 | 6620 | Received email on 3/2/2016 from Mr. Glen Smith. | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The manhole has been cleaned. The section of the sewer system is being mitigated. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-31 | 2015-12-31 | Warner Robins, City of (Sandy Run Creek WPCP) | Houston | Warner Robins | 250 Industrial Park Blvd, Warner Robins, GA | 626000 | Notification received on January 4, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0030325 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | Sandy Run Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | After the effluent pumps were checked and reset, the spill was stopped. The pumps have run without incident through the remainder of the holiday weekend. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-27 | 2017-04-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 401 Willow Lane, Decatur | 380 | Notification received on May 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 4/28/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flow monitor blocking | The problem was corrected on April 28, 2017 at 00:25 hours when a crew removed the flow meter and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-01 | 2018-02-01 | Rockdale County (Quigg Branch WPCP) | Rockdale | Conyers | 1260 Shawdowlawn Drive | 1400 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/1/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Boar Tusk Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The facility removed Roots. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-15 | 2015-06-15 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Latitude 34.506 Longitude 83.520 | 75 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Roots |  | Cindy Nix | Kathy Lewis | Cindy Nix | 6/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | South Fork of Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failed Orangeburg pipe from roots | The city jetted the line and removed the roots from around the affected sewer line. The affected area was cleaned and hydrated calcium carbonate was applied to the area | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-16 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-778-6461 | CITY OF CORNELIA
2015-02-18 | 2015-02-18 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 767 Linwood Street, SE | 10 | fax received 2/19/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/18/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-07-07 | 2016-07-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1277 Niles Avenue, NW | 1010 | Fax received 7/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/8/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failure of bypass pump. | The crew made repairs to the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-31 | 2017-10-31 | Cobb County Water System | Cobb |  | 595 Riverside Parkway | 370 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Stopped spill at 6:40 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-15 | 2018-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2190 Verbena St. NW - ATL | 395 | Fax sent 2018-02-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/16/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-02 | 2018-08-02 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 6 Lee Street - Winder | 4500 | Fax sent 2018-08-02 | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 8/2/2018 12:00:00 AM |  | 8/3/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. to Fort Yargo Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage, intensified by heavy rain/ I&I moving aggregate through the collection system. | Jetted main to remove blockage; removed aggregate and grease; sanitized area with powdered lime; CCTV'ed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-25 | 2018-07-25 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | 130 Yonah Drive | 120 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Debris |  | Brian Koehler | Kathy Lewis | Brian Koehler | 7/25/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Unnamed Tributary to the Soque River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Backed up sewer lateral | Contained and limed. Lateral unclogged by jetting machine. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-26 | 1 | 0 | 0 | 0 | 0 | 0
2016-07-08 | 2016-07-08 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Brookside Drive | 200 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream | Stream | Contractor |  | Brian Koehler | Kathy Lewis | Brian Koehler | 7/8/2016 12:00:00 AM | Chattahoochee | 7/8/2016 12:00:00 AM |  |  | 0 | South Fork of Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The city believes that Higgins Construction hit a sewer pipe with their excavating equipment and caused the pipe to sift creating a small crack between the concrete and sewer pipe coming into the manhole allowing sewage to begin to leak. | Repaired pipe | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3221 Broadway (Broadway Lift Station), Macon MH ID 58206 | 9020 | Phone call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Ephemeral ditch with no known outlet | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | Debris was removed from the area and the affected area has been disinfected with lime. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. The MWA has also purchased a pump that will be installed in the wet well at the station to assist the station in times of heavy flows. Estimated completion of install is May 1, 2016. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-09 | 2017-03-09 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2540 Greenleaf Dr, Macon MH ID 60611 | 1800 | Fax and email received on 03/10/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 3/10/2017 12:00:00 AM | Upper Ocmulgee | 3/10/2017 12:00:00 AM |  |  | 1 | Tobesofkee Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Debris was removed and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-14 | 1 | 1 | 0 | 0 | 0 | 0
2018-03-02 | 2018-03-02 | Fulton County (Big Creek WPCP) | Fulton |  | 5870 Hilderbrand Drive Sandy Springs, 30328 | 1960 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-02 | 2016-10-02 | Cobb County Water System | Cobb |  | 2885 Paces Lake Dr. | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chuck Roshak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | spread lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-02 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-04 | 2018-05-04 | Cobb County Water System | Cobb | Marietta | 3990 Cripple Creek Drive | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/4/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chastain Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-25 | 2017-11-25 |  | Fulton |  | 5300 Old Hundred Lane | 2170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/25/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-19 | 2016-07-19 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | MLK Lift Station | 300000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/19/2016 12:00:00 AM | Satilla |  |  |  | 0 | Ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rains | Replaced pumps | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-13 | 2015-10-13 | Cobb County MS4 | Cobb |  | 8140 Troon Circle | 104400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/13/2015 12:00:00 AM | Chattahoochee | 10/13/2015 12:00:00 AM |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of structural damage. The creek bank collapsed and caused the 36" pipe to break and shift allowing the sewer to escape directly into the tributary to Chattahoochee River. | The Water System was notified at 9:00 a.m. and the contractors set up by-pass pumping to stop overflow by 9:00 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2017-08-16 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1600 Kissingbower Rd. (M0202) - Augusta | 9800 | Email received 2017-08-18 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Contractor |  |  | Alys Hannum | Alys Hannum | 8/18/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow was caused by a contractor cleaning sewer gravity mains. When the contractors were attempting to remove a large root ball, a large portion of the root ball fell back into the manhole, flowing down the pipe, creating a blockage. | Utilities C&M was contacted. The sewer gravity main was augered combined with other efforts in order to remove the root ball from the sewer gravity main and manhole. Lime was spread in the affected area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-18 | 2017-12-18 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 275 Annes Court Athens | 2106 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/19/2017 8:37:00 AM | Oconee |  |  |  | 1 | Unnamed tributary to Middle Oconee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer line clogged due to grease and disposable wipes | Area cleaned of solids, rodded line used |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-20 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Joe McHugh |  | Athens - Clarke County
2016-04-19 | 2016-04-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1800 James Jackson Parkway, NW | 5880 | fax received 4/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/20/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-17 | 2016-02-18 | Thomaston, City of | Upson | Thomaston | 801 W. Gordon Street | 820 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/23/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Johnson Heights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Debris has been removed from the surronding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-22 | 2017-09-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 2945 Bouldercrest Road, Ellenwood | 37850 | Notification received on September 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 9/22/2017 12:00:00 AM |  |  |  |  | 0 | South river | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Roots and rags. | The problem was corrected on September 22, 2017 at 20:19 hours when the first responder crew rodded the 8-inch sewer main downstream 140-ft, cleared the blockage at 3-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-27 | 0 | 1 | 0 | 1 | 0 | 0
2016-09-28 | 2016-09-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2368 Spring Creek Road, Decatur | 2158 | Notification received on October 3, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/3/2016 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defective creek crossing. | The problem was corrected on September 29, 2016 at 12:15 hours when a crew built a dirt berm, contain the spill and called in for an emergency creek crossing repair. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-03 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-03 | 2015-05-03 |  | Columbia |  | 4316 Columbia Road | 1500 | fax received 5/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Other |  | Roots |  |  | Kim Hembree | Kim Hembree | 5/4/2015 12:00:00 AM |  |  |  |  | 1 | Private pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and grease | Unstopped sewer main with high pressure jet machine. Cleaned up spill area around manhole. Posted signs. Follow up video inspection and cleaning of main. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2017-01-30 | 2017-01-30 | Cobb County Water System | Cobb |  | 4650 Amberwood Trail/Chimney Springs Drive | 130 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-14 | 2017-05-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1481 Woodbine Ave. SE - ATL | 1395 | Fax received 2017-05-14 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/15/2017 12:00:00 AM |  | 5/14/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to equipment failure. | A repair was made to the by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-19 | 2016-11-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Rd. SW - ATL | 3220 | Physical Letter received 2017-02-07 | Raw Sewage |  | GA0039012 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Paul Moisan | 1/20/2017 12:00:00 AM |  | 1/19/2017 12:00:00 AM |  |  | 0 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Hydraulic pressure cleaner was used to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-10 | 2015-04-10 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | Intrenchment Creek WRC, 1510 Key Road | 830000 | ERT contacted 4/11/2015, CTS No. 76444. Email confirmation of spill from the City received 4/15/2015. | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 4/11/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Storm induced hydraulic inflow |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-19 | 2015-09-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1903 Sunbury Place, NW | 20 | fax received 9/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/20/2015 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-26 | 2017-01-26 | Cobb County Water System | Cobb |  | 4502 Circle 75 Pkwy | 680 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/26/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2400 Block of Gornto Road | 117000 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Withlachoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-12-16 | 2015-12-16 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 1/14/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 25.0 mg/L on 12/16/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-04 | 2016-01-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1955 LaDawn Lane, NW | 1360 | fax received 1/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/5/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-02 | 2017-03-02 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Corner of Bryant Street and Water Street. | 200 | According to the phone call, there was a backup at a pump station. A new employee went to investigate and resolve the issue. The new employee used a portable pump and deliberately pumped the raw sewage into an unnamed stream nearby in order to remove the backup and gain access. | Raw Sewage | Mountain District - Cartersville | GA0032514 | Pump Station | Stream |  | Equipment failure |  | Brian Koehler | Brian Koehler | Brian Koehler | 3/3/2017 10:15:00 AM | Chattahoochee |  |  |  | 0 | Unnamed tributary to Soque River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line Break / Sewer Pump | We found this issue as soon as we arrived on the job. Stopped the flow immediately. Then Employees were counseled on the correct method to prevent this from happening. This will not happen again. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 2017-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-25 | 2017-09-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1359 N Highland Ave. NE - ATL | 3475 | Email sent 2017-09-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/26/2017 12:00:00 AM |  | 9/25/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew used a hydraulic pressuce cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-02 | 2017-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 808 Fairburn Rd NW - ATL | 252 | Fax received on 02/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 2/3/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-24 | 2015-11-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 253 Scott Street, NW | 2478 | fax received 11/2/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/25/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-04-25 | 2017-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) |  | Atlanta | 325 Saint Johns Ave. SW - ATL | 25 | Fax received 2017-04-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 4/26/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-17 | 2017-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1728 Simpson Rd. NW - ATL | 4 | Fax sent 2017-12-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 12/18/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-13 | 2015-02-13 |  | Baldwin | Milledgeville | Vicinity of 117 West Hancock Street | 750 | Notification received by phone and email. Notified the facility to contact the Milledgeville Health Department about the spill. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Storm Drain |  | Roots |  |  | Sarita Banjade | Sarita Banjade | 1/13/2015 12:00:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root in the sewer Line | Private contractor was hired to repair the sewer line and work was completed on January 17. 2015. Appropriate cleanup procedures were followed at the spill site. |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-02-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE | 4784144059
2017-09-13 | 2017-09-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2562 Tilly Mill Road, Atlanta | 100 | Notification received on September 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/15/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The first responder crew inspected the upstream and downstream manholes and found the 10-inch sewer main to be clear and flowing normal at 12:50 hours. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-23 | 2018-04-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 750 Selig Dr. - Atlanta | 8500 | Fax sent 2018-04-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 4/24/2018 12:00:00 AM |  | 4/23/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical pump failure. | Crew used a bypass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1301 Riverside Drive, Macon MH ID 66885 | 281220 | Email received on 04/13/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/13/2016 12:00:00 AM | Upper Ocmulgee | 4/1/2016 12:00:00 AM | 2016-04-05 |  | 1 | Vineville Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this major spill was hydraulic overload due to heavy rains in the MWA service area. According to the National Weather Service, Macon-Bibb County received 5.42 inches of rain on Friday, April 1st | The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-14 | 0 | 1 | 0 | 0 | 0 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2017-11-24 | 2017-11-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 249 Burbank Dr. NW - ATL | 50 | Fax sent 2017-11-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/25/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-29 | 2016-09-29 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | ROW at rear of 204 Brookcrest Drive, Lagrange | 2580 | Fax received on 09/29/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 9/29/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Shoal Creek Tributary | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease choke in main caused a 4" clean-out, adjacent to tributary, to overflow. Cap to clean-out was missing. | Used high pressure jetting truck to clear choke in main. Replaced missing cap on clean-out. Will follow-up with extensive jetting of affected main(s). |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-09-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-07 | 2018-06-07 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 990 Scott Street | 290 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/7/2018 12:00:00 AM | Upper Ocmulgee |  |  |  | 0 | Beaverdam Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Stopped spill and cleaned piping. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-05 | 2016-08-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1450 Marietta Blvd. NW | 9240 | fax received 8/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 8/6/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-09 | 2017-05-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4261 Harrogate Dr. NW - ATL | 552 | Fax received 2017-05-10 EDIT 8/22/17: Location changed from 1130 Mount Paran Rd. to 4261 Harrogate Dr. NW as per update received 8/21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 5/10/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-02 | 2015-06-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1460 Hardee Street, NE | 15 | fax received 6/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 6/3/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "Equipment malfunction" |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-19 | 2016-10-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2291 Burnt Creek Road, Decatur | 33750 | Notification received on October 25, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/20/2016 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | The problem was corrected at 16:15 hours, when the contractors built a berm around the spilling area and also remoed the plug from the 24" sewer main, stopped the spill and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-09 | 2016-10-09 | Savannah, City of (President Street WRF) | Chatham | Savannah | 420 Wood Cliff Drive. | 90 |  | Raw Sewage | Coastal District | GA0025348 | WWRF | Canal | Canal | Power failure |  | David Lyle | Hailey Harden | Hailey Harden | 10/10/2016 12:00:00 AM | Savannah | 10/9/2016 12:00:00 AM |  |  | 1 | Harmon Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to the impacts of Hurricane Matthew, the generator malfunctioned from continuous use during the power outage. | Restored/repaired existing generator or brought in a portable generator. Also used the City Jet Vac. Truch to control extraneous flows until the generator was up. Spill notifications were placed at the spill site where it goes into a canal and Hayner's Creek at Rivers End. | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-02 | 2016-05-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 5615 Hunter Valley, Lithonia | 3900 | Notification received on May 6, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/2/2016 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The problem was corrected at 16:01 hours, when a crew rodded the manhole 3ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-10 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-19 | 2018-03-20 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 4679 GA Hwy 100 Tallapoosa | 100 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 3/20/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Greene Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage caused influent to shut down, rags blocked passage and caused material back up | Power restored, blockage removed, suggest back up power | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-11 | 2017-01-11 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 195 Cedar Springs Dr. | 50 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cedar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | blockage in line due to disposable wipes | rodded sewer, inspected two manhole structures downstream and upstream | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-01 | 2017-12-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1486 Wellswood Dr. SE - ATL | 460 | Fax sent 2017-12-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 12/2/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-27 | 2017-06-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 177 Huntington Rd. NE - ATL | 15 | Email received 2017-06-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/28/2017 12:00:00 AM |  | 6/27/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-07 | 2015-06-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 451 Sawtell Avenue, SE | 475 | fax received 6/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/7/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-23 | 2018-07-23 | Savannah, City of (President Street WRF) | Chatham | Savannah | 210 Andover Street, Savannah, GA | 510 | Initial phone call and full report emailed 7/23/18. | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain, Stream | Stream | Pipe failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 7/23/2018 12:00:00 AM |  | 7/23/2018 12:00:00 AM |  |  | 1 | Hampstead Canal | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravity main break released raw sewage into a storm ditch to Hampstead Canal - Casey Canal - Vernon River. | Repaired the break and used vac truck to remove storm/sewage mix from storm ditch immediately adjacent. Also contained and cleaned storm/sewage mix from larger storm system. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-07-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-20 | 2015-07-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2479 Abner Place, NW | 1260 | fax received 7/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/21/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-08-28 | 2015-08-29 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1400 Block of Gornto Road | 177000 | CTS Nos. 77716 and 77714 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 8/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-10-12 | 2017-10-12 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift Station, Eastman, GA | 25000 | 9/19/2017 - Stream monitoring data received (Week 1). 9/20/2017 - PN ran in newspaper (The Dodge County News) and District Office received copy of written report documenting spills. 10/11/2017 - Written report received including start and stop times, and documentation showing TV, Radio, and health department were notified of incidents. Pictures of PN at spill locations also provided | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 9/11/2017 10:00:00 AM | Ocmulgee | 9/11/2017 12:00:00 AM | 2017-09-12 | 2018-08-28 | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Raw sewage spill from Legion Drive Lift Station due to excessive rainfall and power outages from Hurricane Irma. | Requested stream monitoring, public notification requirements be implemented for incident. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-09-28 | 1 | 1 | 1 | 1 | 1 | 0 | Matt McDaniel |  | CITY OF EASTMAN WPCP
2017-10-12 | 2017-10-12 | Eastman, City of (Sugar Creek WPCP) | Dodge |  | Legion Drive Lift Station, Eastman, GA | 25000 | 9/19/2017 - Stream monitoring data received (Week 1). 9/20/2017 - PN ran in newspaper (The Dodge County News) and District Office received copy of written report documenting spills. 10/11/2017 - Written report received including start and stop times, and documentation showing TV, Radio, and health department were notified of incidents. Pictures of PN at spill locations also provided | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 9/11/2017 10:00:00 AM | Ocmulgee | 9/11/2017 12:00:00 AM | 2017-09-12 | 2018-08-28 | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Raw sewage spill from Legion Drive Lift Station due to excessive rainfall and power outages from Hurricane Irma. | Requested stream monitoring, public notification requirements be implemented for incident. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-09-28 | 1 | 1 | 1 | 1 | 1 | 0 | Matt McDaniel |  | CITY OF EASTMAN WPCP
2016-03-21 | 2016-03-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 1554 Smithson Court, Lithonia | 2800 | Notification received on March 22, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/22/2016 12:00:00 AM |  |  |  |  | 0 | Swift Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 18:23 hours, when a crew pressure washed the sewer main ream 124ft, clearing the blockage at 93ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-12 | 2015-10-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3150 Howell Mill Road, NW | 468 | fax received 10/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/13/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-25 | 2018-05-25 | East Point (City of)- Sewers | Fulton | East Point | 3204 Cloverhurst Drive between Manhole ID# C-163-011 and C-163-010 | 1500 | I talked to Richard Randolph the City's Engineer and he mentioned that this spill occurred in the City's right-away. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/30/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The proable cause of the spill was due to a breach in a private lateral connecting to the City's Sanitary Main resulting into a discharge in the Camp Creek Basin. | The City of East Point crews stopped the spill and cleaned the affected area as required. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 |  | Columbus Water Works (South WRF) | Muscogee | Columbus | 1454 Cherokee Ave./ Poplar Dr., Columbus, GA | 50973 | Fax received 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rain subsided, flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-12 | 2018-02-12 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2870 South Lumpkin Road, Columbus | 1315 | Fax received on 02/12/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Paul Moisan | 2/12/2018 12:00:00 AM |  |  |  |  | 0 | Upatoi Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An 10" sewer main was clogged with debris causing an overflow. | Debris cleared, overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-02-13 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-03 | 2018-05-03 | Marietta (City of)- Sewers | Cobb | Marietta | 750 Canton Rd. | 375 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/3/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/ Construction | Marietta Water personnel quickly relieved the blockage thus restoring normal service. Construction superintendent has been told to cease activity until manholes are secured from construction debris entry. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-07 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Tim Marshall |  | CITY OF MARIETTA
2018-05-03 | 2018-05-03 | Marietta (City of)- Sewers | Cobb |  | 750 Canton Rd. | 375 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/3/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Sope Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage/ Construction | Marietta Water personnel quickly relieved the blockage thus restoring normal service. Construction superintendent has been told to cease activity until manholes are secured from construction debris entry. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-07 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Tim Marshall |  | CITY OF MARIETTA
2015-05-27 | 2015-05-27 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  |  | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to rise to 45.6 mg/L on 05/27/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-28 | 2018-07-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3425 Malone Drive, Chamblee GA 30341 | 27375 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | 3rd party contractor |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/29/2018 6:26:00 AM | Ocmulgee |  |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outside contractor damaged main | Bypassed damaged area |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-09 | 2015-10-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1064 Parsons Street, SW | 250 | fax received 10/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/11/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to remove the blockage |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-19 | 2016-09-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1083 Westmoor Drive, NW | 244 | fax received 9/20/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/20/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-03 | 2016-03-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1300 Gault Street, SE | 3350 | fax received 3/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/4/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-11 | 2017-10-11 | Jesup, City of (Jesup WPCP) | Wayne | Jesup | Oran Way Lift Station | 3500 |  | Raw Sewage | Coastal District | GA0026000 | Lift Station | Ditch | Ditch | Power failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/11/2017 11:00:00 AM | Altamaha | 9/11/2017 12:00:00 AM |  |  | 1 | Penholloway Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Loss of power | Restored power | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-13 | 1 | 1 | 0 | 0 | 0 | 0
2018-04-05 | 2018-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 41 S. Prado NE - Atlanta | 50 | Fax sent 2018-04-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 |  | Ground |  |  |  |  | Alys Hannum |  | 4/6/2018 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Spill was self-contained. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-30 | 2015-07-31 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW, Cairo | 0 |  | Treated Effluent | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Hydraulic Overload |  |  | Dagny Pariani | Hsin Yeh | 7/31/2015 12:00:00 AM | Ochlockonee | 7/31/2015 12:00:00 AM | 2015-07-31 |  | 1 | Parker's Mill Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Heavy rainfall and I/I issues. Spill estimated at 10,500 gallons. | No immediate actions available. Cleanup involved clearing debris and applying lime. |  | d80f500b-2416-4653-adb7-23760952ef3b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025 x162
2015-01-12 | 2015-01-12 | Cobb County MS4 | Cobb |  | 4388 Claireesbrook LN | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tributary to Lake Acworth | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8" PVC Main near Tennis Courts |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-11 | 2018-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Richmond | Augusta | 1820 Doug Barnard Parkway - Messerly WPCP | 176040 | Email sent 2018-09-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 9/12/2018 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Control power failure caused half the main influent pumps to go offline. Combination of high flows and reduced pumping capacity resulted in an overflow. | Control power issues corrected. Plant personnel are reviewing the control wiring to determine modifications to prevent a recurrence. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | MillerCoors LLC | Dougherty | Albany | discharge through manhole, entered storm drain system and discharged to Flint river | 518000 |  | Other | Wastewater Regulatory Program | GA0049093 | N/A | Ground, Storm Drain, Stream |  | Equipment failure |  |  | Jill Causse | Shea Buettner | 2/26/2016 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Primary and secondary pump failures causing a release of untreated influent and stormwater | repair primary pump, remote storm drain temporarily capped, low flow alarm installed on the influent pump |  | ec78723e-818a-41f7-abda-40a99625de6f | a1cb0f9b-67db-410b-ad37-7abcde5c00f8 | 2016-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | MILLERCOORS LLC | 229-420-5096
2015-12-15 | 2015-12-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4024 Blanton Avenue, SW | 28320 | fax received 12/16/2015. CTS No. 78526 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/16/2015 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-16 | 2017-02-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1102 Beech Haven Road, Atlanta | 8400 | Notification received on February 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 2/16/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks and sands blockage | The problem was corrected at 13:33 hours when a crew pressure washed the 8" sewer main 250ft, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-24 | 2016-05-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1479 Cedar Ridge Way, Stone Mountain | 2880 | Notification received on May 25, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 5/24/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 13:15 hours, when a crew rodded the overflowing manhole 36 feet upstream, cleared the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2617 Sue Mack Drive, Columbus | 1847 | Fax, email and voice mail received on 02/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Lindsay Creek. | Once the rain subsided and flow returned to normal the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Manhole TRK-0002, 206 Sycamore Way | 13500 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream | Stream | Wet weather |  | Brian Koehler | Kathy Lewis | Brian Koehler | 11/9/2015 12:00:00 AM | Chattahoochee | 11/9/2015 12:00:00 AM |  |  | 1 | Soque River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rainfall | Areas affected by spill have been cleaned up and powdered lime has been applied. The City is making sure that the manholes at 206 Sycamore Way will be properly sealed to prevent a spill in the future. | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | Justin Allen | 706-754-4216 | City of Clarkesville
2016-02-29 | 2016-02-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 5045 Leeshire Trail, Tucker | 1850 | Notification received on March 3, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/1/2016 12:00:00 AM |  |  |  |  | 0 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure | The problem was corrected at 14:20 hours, when a crew reset the lift station pump, stops the spill and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-03 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-14 | 2017-02-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1841 Wells Dr. SW - ATL | 7200 | Fax received 2017-02-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Paul Moisan | 2/15/2017 12:00:00 AM |  | 2/14/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline and a malfunction of the by-pass pump plug. | Crew readjusted the by-pass pump to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-13 | 2018-06-13 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 1049 Windermere Crossing - Cumming | 1200 | Email sent 2018-06-14 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/14/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage inside manhole/cleanout | Jetted line and vac'ed spill. Limed area and removed solids. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Savannah, City of (Crossroads WPCP) | Chatham | savannah | City of Savannah I & D Treatment Plant – Water Filtration Plant Road Port Wentworth Georgia (6183 Highway 21 Port Wentworth) | 170 |  | Raw Sewage | Coastal District |  | WWTP | Ground, Stream | Stream | Pipe failure |  | Steve Walker | Steve Fox | Steve Fox | 5/23/2016 12:00:00 AM | Savannah | 5/23/2016 12:00:00 AM |  |  | 1 | St.Augustine Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Break on 3” force main from sewage grinder station | Turned station off and City of Savannah maintenance crews repaired break and spill notification markers were placed at the spill site / plant and the St. Augustine Creek / Highway 21. All entities (Georgia Environmental Protection Division, and Health Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | e22a0fa8-67c8-11e1-a69e-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-01 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-27 | 2016-02-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 301 E. Lake Blvd., SE | 315 | fax received 2/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/28/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-26 | 2016-09-26 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 1280 Wildwood Drive | 300 | email received 9/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Power failure |  |  | Kim Hembree | Kim Hembree | 9/27/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Got emergency generator running. Lime applied to spill site. Replaced meter base to restore power. Sign posted. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2017-03-31 | 2017-03-31 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Stockbridge | 3661 Hudson Way - Stockbridge MH #2200462 | 4800 | Fax received on 03/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Vandalism |  |  | Paul Moisan | Paul Moisan | 3/31/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a blockage caused by vandalism. | Blockage was cleared (debris was removed from the manhole). |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-04-03 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | Clayton Co Water Authority
2015-05-20 | 2015-05-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 692 Gary Avenue, NW | 30 | fax received 5/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/21/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-19 | 2015-04-19 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | 311 Creekside Drive (Creekside Subdivision) | 10200 | REC FAX 4/20/2015. REC FINAL REPORT 4/20/2015. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Stream | Stream | Wet weather |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/20/2015 9:25:00 AM | Chattahoochee | 4/20/2015 12:00:00 AM | 2015-04-20 |  | 1 | Dixie Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | heavy rainfall | Once rainfall subsided, the lift station serving this area was able to recover. I/I investigations continue in this area. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-20 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CITY OF LAGRANGE | 7706-883-2150
2017-06-03 | 2017-06-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2096 Niskey Lake Trl. SW - ATL | 300 | Email received 2017-06-05. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 6/5/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-27 | 2018-08-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 43 Mildred Pl. NW - Atlanta | 408 | Fax sent 2018-08-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/28/2018 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-26 | 2017-12-26 | Fulton County (Camp Creek WPCP) | Fulton |  | 5010 Terminus Dr. Fairburn, GA 30213 | 3000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/10/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Whitewater Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Deposition of foreign material. Will CCTV to determine cause. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-16 | 2015-12-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2300 Daniel Road, SW | 2550 | fax received 12/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/16/2015 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a mechanical rod to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-06 | 2017-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1870 Piedmont Rd. NE - ATL | 615 | Fax received 2017-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Paul Moisan | 2/7/2017 12:00:00 AM |  | 2/6/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause was grease and debris in the mainline | Hydraulic pressure cleaner used to contain the spill. Process to clean and disinfect the site has been initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-23 | 2018-04-23 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Dairy Pak Road | 18042 | Received report 4/30/18 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/23/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | North Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Wet weather | Used vac-con trucks to mitigate sewage overflow until ended |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3524 Johnathan Circle | 27000 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/1/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2017-04-24 | 2017-04-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 870 Mayson Turner Rd. NW - ATL | 1475 | Originally stated to be a private spill; correction indicates it is a public spill. Fax received 2017-04-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/25/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris. Originally stated to be a private spill; correction indicates it is a public spill. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-27 | 2016-04-27 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 1318 Eric Circle | 8387 | fax received 4/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/27/2016 12:00:00 AM |  |  |  |  | 1 | Lee Daniel Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | rags, other flushables, grease | raked area and spread lime; place signs at spill waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-11-02 | 2015-11-02 | Savannah, City of (President Street WRF) | Chatham | Savannah | 6806 Forest Park Drive | 4800 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 11/2/2015 12:00:00 AM | Savannah | 11/2/2015 12:00:00 AM |  |  | 1 | Harmon canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Gravity sanitary sewer main collapse caused system surcharge to further cause two manholes to overflow | Contained flow in storm ditch and set up by-pass pump to pump storm / sewage water mix to City of Savannah sanitary sewer collection system. City also utilized City vacuum trucks and City contractor tanker to remove extraneous / residual flows from ditch and area. Ditch was contained to stop sewage from continuing to overflow into the ditch and contractor arrived at site to repair the collapsed sewer main. Spill notifications will be placed at spill site, at 200 Eisenhower where the ditch crosses Eisenhower Drive and at the boat ramp at Harmon Canal. All entities - Georgia Environmental Protection Division, Heath Dept. and City Public Information Office (who will send out a news release to the media) were contacted. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-11-03 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-11 | 2016-03-11 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 348 Walnut Drive, Manhole No. 1076 | 300 | Email notification received Friday, 3/11/2016 @ ~9:00pm | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Roots |  |  | Kim Hembree | Kim Hembree | 3/11/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | "Cleared blockage with jet machine. Lime applied to spill site. Sign posted. Proper agencies notified." |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2018-07-11 | 2018-07-11 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 314 Fawn Dr. R/W | 0 |  | Raw Sewage |  | GA0021725 | Collection System | Ground | N/A |  |  |  |  | Dillon Rodenbaugh | 8/1/2018 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | na | na |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 |  | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-28 | 2015-01-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 632 Springdale Dr. | 1200 | REC FAX 1/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/29/2015 12:00:00 AM | Flint | 1/28/2015 12:00:00 AM |  |  | 1 | Tributary to Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | GREASE | Grease blockage was cleared and flow restored to normal capacity. The sanitary sewer structure will be scheduled for Closed Circuit Televising to determine actual cause of stoppage. Any needed repairs will be scheduled and completed. The CCWA Grease Trap Inspector will be notified of problem area for planned follow up actions if needed. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-29 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | Clayton Co Water Authority | 770-960-5205
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1100 Block of Joree Street | 80800 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2015-09-16 | 2015-09-16 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 4380 Gunnin Road | 3780 | fax received 9/21/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/21/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken main line | repaired broken pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-03-27 | 2016-03-27 | Tifton, City of (New River WPCP) | Tift | Tifton | Manhole located at the Tift Regional Waste Water Plant. | 4000 | Email received on 03/28/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | WWTP | Ditch | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 3/28/2016 12:00:00 AM |  | 3/27/2016 12:00:00 AM |  |  | 1 | New River Basin | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to the series of rain events throughout the weekend. | Hydrated lime has been spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-15 | 2017-06-15 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 1054 Elain Terrace, Forest Park | 675 | Fax received on 06/15/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Contractor |  |  | Paul Moisan | Paul Moisan | 6/15/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Conley Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Contractor hit pipe, and replaced it immediately with ductile iron. | Contractor repaired pipe. Pipe will be televised to ensure repair is accurate. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-06-19 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2016-12-06 | 2016-12-06 | Tifton, City of (New River WPCP) | Tift | Tifton | Manhole next to lift station at intersection of 26th and Ridge Street, Tifton | 4200 | Phone call received on 12/06/2016. Email received on 12/07/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Shoreline | Wet weather |  | Paul Moisan | Paul Moisan | Paul Moisan | 12/6/2016 12:00:00 AM |  | 12/6/2016 12:00:00 AM |  |  | 1 | Little River Basin | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was heavy rainfall. | The spill occurred on a roadway and was cleaned with a street sweeper. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-08 | 0 | 1 | 0 | 0 | 0 | 0 | Andrew Marzen |  | ESG Operations, Inc.
2015-10-22 | 2015-10-23 | Thomaston, City of (Town Branch WPCP) |  | upson | 649 S. Center Street | 6755 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/22/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill is a broken sewer main. | The City of Thomaston has hired a contractor to make the repair on the sewer main. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-02 | 2015-12-02 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 815 East Willow Park Drive | 900 |  | Raw Sewage | Mountain District - Cartersville | GA02-056 | WWRF | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/4/2015 12:00:00 AM | Coosa |  |  |  | 0 | unnamed tributary of Tar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive Rainfall | Vacuum trucks were used to mitigate the spill. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | David Oxford | 706-529-1010 | Dalton Utiilites
2018-07-12 | 2018-07-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4774 Wieuca Rd. NE - Atlanta | 239 | Fax sent 2018-07-13 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/13/2018 12:00:00 AM |  | 7/12/2018 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a bypass pump to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-27 | 2016-03-28 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 700 Block of Cypress Street | 14725 | Email notification received 3/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/29/2016 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-09-22 | 2016-09-22 | Dekalb County (Snapfinger Creek WPCP) |  | Brookhaven | 3571 Buford Hwy, Brookhaven | 3840 | Notification received on September 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/22/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected on September 22, 2016 at 12:40 hours when a crew pressure washed the 8" sewer main 200ft, cleared the blockage at 123ft and restore normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-26 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-11 | 2017-03-11 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Intersection of Williamson Rd and Raymond Kellie Dr, Macon MH ID 53093 | 3900 | Fax and email received on 03/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  |  |  | Paul Moisan | 3/13/2017 12:00:00 AM | Upper Ocmulgee | 3/11/2017 12:00:00 AM |  |  | 1 | Rocky Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease | After blockage was removed, flow returned to normal. The line is scheduled to be cleaned and televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-03-14 | 1 | 1 | 0 | 0 | 0 | 0 | Heather Veal |  | MACON WATER AUTHORITY
2018-06-25 | 2018-06-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1814 Peachtree St. NW - Atlanta | 45 | Fax sent 2018-06-25 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 6/26/2018 12:00:00 AM |  | 6/25/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment malfunction | Crew made repairs to the by-pass pump |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-20 | 2017-03-20 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 138 Welch Place | 4210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/20/2017 12:00:00 AM | Oconee |  |  |  | 0 | Sleepy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-31 | 2016-10-31 | Clarkesville, City of (Clarkesville WPCP) | Habersham |  | Corner of Bryant Street and Water Street | 20 |  | Raw Sewage | Mountain District - Cartersville | GA0032514 | WWTP | Stream |  | Equipment failure |  | Brian Koehler | Brian Koehler | Brian Koehler | 11/2/2016 1:08:00 PM | Chattahoochee |  |  |  | 0 | Soque River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Small Crack in the top of the man-hole riser | We have sealed the crack, and do not anticipate any more issues | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 2017-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2015-12-31 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 3221 Broadway, Macon MH # 57899, and 58206 | 88140 | Initial notification received on 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-30 | 2016-11-28 | 1 | Epemeral drainage ditch with no known outlet | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause was hydraulic overload, since the MWA service area received 12.62 inches of rain for December 2015. | Debris was removed from the area and the area was disinfected with lime. The MWA will continue its search for I/I into its sewer system through its CCTV and flow monitoring investigations and will develop rehabilitation projects based on this information and contractor conducted sewer evaluations. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-11 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-03-14 | 2016-03-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 4251 Long Branch Court, Brookhaeven | 15525 | Notification received on March 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/15/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 21:05 hours, when a crew pressure washed the sewer line 300ft and removed the blockage at 225ft and restored n ormal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-25 | 2015-02-25 |  | Grady |  | City of Cairo Wastewater Treatment Plant | 4200 | Received by email. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Hydraulic Overload |  |  | Sarita Banjade | Sarita Banjade | 2/26/2015 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Caused by a hydraulic overload due to heavy rainfall and failure of an influent pump. I/I issue | No immediate corrective actions available to mitigate the possible adverse effects of the spill. Debirs was cleaned from the grounds and lime applied. |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CAIRO - WPCP | (229)377-5025 ext. 162
2015-11-03 | 2015-11-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1404 Gornto Road | 27000 | verbal notification received 11/3/2015 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-04 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229.251.6528
2016-02-03 |  |  | DeKalb |  | 4477 Yorkdale Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event |  |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-23 | 2016-02-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 5900 North Cheryl Drive, Morrow Manhole 23032290 | 126000 | Voice mail on 02/23/2016; fax received on 02/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/23/2016 12:00:00 AM | Flint |  |  |  | 1 | East Jester's Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Heavy rainfall caused capacity issues. | Televise to locate a problem in the lines, and if a problem exists, repairs will be made. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-29 | 0 | 1 | 1 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive, NW | 3000 | email notification received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-10 | 2015-03-10 |  | Clarke | Athens | 105 Westchester Dr. | 50 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/10/2015 12:00:00 AM | Satilla |  |  |  | 0 | Middle Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | aerial pipe damaged | vacuum truck; crew repaired aerial | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-24 | 2016-10-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Atlanta Airport Lift Station #2 | 5000 | Telephone call and email received by Marzieh Shahbazaz on 10/25/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Lift Station | Stream |  | Equipment failure |  | Marzieh Shahbazah | Paul Moisan | Paul Moisan | 10/25/2016 12:00:00 AM |  |  | 2016-10-25 |  | 1 | Sullivan Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Airport Lift Station #2 pumps were rendered inoperable due to a faulty 5 amp fuse failure. |  | 33e3f7fa-ee02-11e0-b8d8-000c29971acc | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-26 | 0 | 0 | 1 | 0 | 0 | 0
2017-09-05 | 2017-09-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1095 Cascade Av. SW - ATL | 30 | Fax received 2017-09-06 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Roots |  |  | Alys Hannum | Alys Hannum | 9/6/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the service lateral. | "This is not a city problem". |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-24 | 2018-05-25 | Pearson, City of (Pearson WPCP) | Atkinson | Pearson | At the City of Pearson WWTP effluent outfall into an unnamed tributary to Little Red Bluff Creek to Red Bluff Creek. | 1013000 | Operator states that they have checked the unnamed tributary, Little Red Bluff Creek and Red Bluff Creek for signs of any adverse effects on the stream and/or fish kills and have observed none. | Treated Effluent | Coastal District | GA0038334 | WWTP | Stream | Stream | Equipment failure |  |  | Brett Berry | Brett Berry | 5/30/2018 10:00:00 AM | Satilla | 6/1/2018 12:00:00 AM | 2018-06-01 |  | 1 | Red Bluff Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 |  | 0 | The violation occurred during plant maintenance which required one half of the plant to be bypassed. During this time the plant received heavy rains and had a blower controller fail. This shortened detention times in the remaining basin and provided inadequate aeration. | Signage is being placed at the discharge point. The local health department and local media are being notified. Sampling is being conducted to ensure there are no harmful effects in accordance with the current NPDES permit and EPD protocol. |  | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2018-06-06 | 1 | 1 | 0 | 0 | 0 | 0
2018-05-23 | 2018-05-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | 4760 Miller Road | 212938 | Fax sent 5/24/2018 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 5/24/2018 12:00:00 AM |  |  |  |  | 0 | Cooper Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rains | Rainfall has stopped, manhole has returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-29 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-09 | 2016-04-09 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Manhole on outfall line at end of Golden Hills Drive Woodstock | 90440 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Vandalism |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 4/10/2016 12:00:00 AM | Coosa |  |  |  | 0 | Owl Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandals dropped a log into a manhole. | Removed log from manhole | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-07 | 2016-05-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3016 Westminster Circle, NW | 3211 | fax received 5/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/8/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-11 | 2015-11-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Estes Drive, SW | 380 | fax received 11/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 11/12/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cause is unknown | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-07 | 2018-05-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1110 Spring St. NW - Atlanta | 346 | Fax sent 2018-05-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Roots |  |  | Alys Hannum | Alys Hannum | 5/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-20 | Dekalb County (Snapfinger Creek WPCP) |  | Chamblee | 3520 Sexton Woods Drive, Chamblee | 182473 | Notification received on June 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/28/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm event / I&I | The site was cleaned on June 20th when the crew responded and no further spilling was observed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-30 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-03 | 2016-05-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1081 Mercury Drive, NW | 459 | fax received 5/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/3/2016 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-29 | 2015-12-29 | Town of Thunderbolt MS4 | Chatham | Thunderbolt | Marsh area off of Bonaventure Blvd | 5000 |  | Raw Sewage | Coastal District |  | Lift Station | Basin | Canal | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 12/29/2015 12:00:00 AM | Savannah | 12/29/2015 12:00:00 AM |  |  | 1 | Wilmington River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Pipe failure | installed bypass piping and earthen dam to vac release water | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-01-05 | 1 | 1 | 0 | 0 | 0 | 0
2016-10-07 | 2016-10-07 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 16 Bristlecone Way | 325 | fax received 10/07/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 10/7/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-07-26 | 2017-07-26 | Columbia County (Reed Creek WPCP) | Columbia | Martinez | 330 Wast Wynngate Drive - Martinez | 3000 | Fax received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0031992 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/26/2017 12:00:00 AM |  |  | 1 | Kelley Branch Trib. to Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rainfall | Monitored Area. Follow up inspection of area. Continue to look for points of inflow. Posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-01 | 2015-06-01 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 7/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the TSS effluent to reach 31.0 mg/L on 06/01/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-08 | 2016-02-08 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 2049 Old Mill Way | 4104 | fax received 2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/8/2016 12:00:00 AM |  |  |  |  | 1 | Bromolow Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-27 | 2015-01-27 | Cobb County MS4 | Cobb |  | 3280 Ground Pine Drive | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease/structural damage in sewer main causing the manhole to overflow into a tributary of Sope Creek | The Cobb Crew stopped the overflow at 12:40 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-27 | 2015-01-27 | Cobb County MS4 | Cobb |  | 3280 Ground Pine Drive | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/27/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of grease/structural damage in sewer main causing the manhole to overflow into a tributary of Sope Creek | The Cobb Crew stopped the overflow at 12:40 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-27 | 2018-08-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3130 Parrott Ave. NW - Atlanta | 7000 | Fax sent 2018-08-28 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 8/28/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure at pump station. | Repairs made. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-01 | 2018-06-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 7 Thirkield Ave. SE - Atlanta | 100 | Fax sent 2018-06-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/2/2018 12:00:00 AM |  | 6/1/2018 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-30 | 2015-11-30 | Encore Apartements | Cobb |  | 3290 Cobb Galleria Parkway | 1000 | Spill estimated 1000 gallons due to stream monitoring and onsite observations. | Raw Sewage | Mountain District - Cartersville | GAU060073 | N/A | Stream |  | 3rd party contractor |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 12/1/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Unnamed tributary to Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blocked Sanitary sewer line due to construction | Blockage in sanitary sewer line has been removed | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | Robert Malte | 770-818-4052 | Oxford Properties LLC | 3284 Northside Pkwy NW, Atlanta, Georgia, 30327
2017-12-13 | 2017-12-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4572 Golf Vista Circle, Decatur | 20 | Water has not entered waterway. Private owned | Unknown | Wastewater Regulatory Program | GA0024147 | Private Lateral |  | N/A | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/14/2017 2:38:00 PM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4 inch private cleanout surcharging. Not overflowing upon arrival | The landlord, Antoinette Robinson, was notified she will have to get a plumber to resolve issue. |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-15 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Leroy Higgins |  | Dekalb County Department of Watershed Management
2015-12-11 | 2015-12-11 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 2141 General Winship Dr., (GM ID 14217). | 100 | Email received on 12/11/2015, then a follow-up on 12/15/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 12/11/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Unnamed tributary feeding Vineville Branch | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was a leaking sewer main. | A point repair was made to the section of main that was leaking. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-11 | 2015-06-11 | Marietta (City of)- Sewers | Cobb | Marietta | 2086 Freywood Dr. | 100 | 2086 Freywood Dr. Under road in front of property | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 6/11/2015 12:00:00 AM |  |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure and Pipe leakage at joints |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-06-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-26 | 2015-05-26 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 6/2/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to reach 29.8 mg/L on 05/26/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-28 | 2017-10-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3670 Narrow Dr. SW - ATL | 80 | Fax sent 2017-10-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 10/30/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline, | The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-27 | 2016-07-27 | Rome, City of (Rome WRF) | Floyd |  | 120 Feet Southeast of the intersection of Alabama Highway and Pinecrest Drive | 6000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 7/27/2016 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Coosa River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage caused by roots in the sewer main | The sewer main was thoroughly cleaned and cleanup at the spill site is ongoing | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-07-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-04 | 2015-12-14 | Cobb County (RL Sutton WRF) | Cobb |  | 6400 Highlands Pkwy | 600 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/14/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Separated 10' Creek Crossing |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-23 | 2015-04-23 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Rocky Springs Lift Station in Eastman, GA. | 3000 |  | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Equipment failure |  | Jay Howell | Jay Howell | Jay Howell | 4/23/2015 8:13:00 AM | Ocmulgee | 4/23/2015 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure resulting in can lift station overflow of raw sewage. | Pumps sent off for repair and bypass line installed around affected lift station until such time the lift station is back operable. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-04-28 | 1 | 1 | 1 | 0 | 0 | 0
2017-12-23 | 2017-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4203 Clevemont Road, Elenwood GA 30294 | 18460 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/24/2017 12:36:00 AM | Ocmulgee | 12/24/2017 12:00:00 AM | 2017-12-24 |  | 1 | Conley Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole 15-039-s157 overflowing | bypass pump |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-27 | 0 | 1 | 0 | 0 | 0 | 0 | Roger Young |  | Dekalb Co Dept. Watershed Management
2018-07-10 | 2018-07-10 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Blankets Creek pump station on W Ridge Drive. The manholes at the from of subdivision behind sign on W Ridge Drive and Sixes Road backed up and overflowed as a result of the pump station issues. | 21000 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream | Stream | Pipe failure |  | Katie Meade | Kathy Lewis | Katie Meade | 7/11/2018 12:00:00 AM | Coosa |  |  |  | 1 | Blankets Creek | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Band on the force main broke at the Blankets Creek pump station | Isolated pump and replaced the band | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-13 | 1 | 0 | 0 | 0 | 0 | 0
2016-02-18 | 2016-02-18 | Cobb County MS4 | Cobb |  | 361 Six Flags Dr. | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/23/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Grease | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grrease in 8" PVC Main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-22 | 2017-09-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6765 Tribble Street, Lithonia | 4080 | Notification received on September 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/23/2017 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:15 hours when the first responder crew pressure washed the manholes 50-ft, cleared the grease/rags blockage at 10-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-27 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-23 | 2015-03-23 |  | DeKalb | Decatur | 2773 North Decatur Road, Decatur | 7640 | Notification received on March 25, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 3/23/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 11:25 hours when a crew pressure washed the 8" sewer main upstream 218ft removed the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-02 | 2016-07-02 | Ellijay WPCP | Gilmer |  |  | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0021369 | WWTP | Stream |  | Pipe failure |  | Steve Marchant | Kathy Lewis | Steve Marchant | 7/5/2016 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Ellijay River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collection system pipe failure due to previous erosion of stream bank | See report Dated 7/5/2016 | 4631c25c-eb6e-11e0-b8d8-000c29971acc | 4631c25c-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-07-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-07 | 2016-12-07 |  | Cobb | marietta | 2315 Dallas Highway | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gease in the sewer main | The crew stopped the overflow at 4:30 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-11 | 2017-07-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1280 Oakland Dr. - ATL | 2700 | Fax received 2017-07-12 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/12/2017 12:00:00 AM |  | 7/11/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-22 | 2017-01-23 | Dawson, City of (Dawson WPCP) | Terrell |  | Hwy 82 | 1440 | Creek monitored, report has conflicting data | Raw Sewage | Wastewater Regulatory Program | GA0021326 | Collection System | Stream |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/27/2017 12:00:00 AM | Flint | 1/4/2017 12:00:00 AM |  |  | 1 | Brantley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 7 inches of rain on saturated ground | area cleaned and limed if necessary |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-29 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Jon Bergozza |  | City of Dawson
2016-10-31 | 2016-10-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 42 Karland Dr., NW, Atlanta | 1165 | Fax received on 11/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/1/2016 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the main line. | Hydraulic pressure cleaner was used to contain the spill, and clear blockage. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-03 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2015-08-03 | 2015-08-03 |  | Henry |  | Eagles Landing Subdivision off of Eagles Landing Parkway at 141 Augusta Drive in Stockbridge, Georgia | 252 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/3/2015 12:00:00 AM | Ocmulgee | 8/3/2015 12:00:00 AM |  |  | 0 | Pates Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The blockage in the line was caused by vandalism. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-20 | 2017-01-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1500 Avon Ave SW - ATL | 25 | Fax received on 01/21/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The spill was self-contained. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2015-07-24 | 2015-07-30 | Broxton | Coffee | Broxton | West Avenue, North - Lift Station | 1000 |  | Raw Sewage | Coastal District | GAJ020124 | Lift Station | Ditch | Ditch | Rags |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/24/2015 8:22:00 AM | Satilla | 7/24/2015 12:00:00 AM |  |  | 1 | Unknown branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags blocked lift station pump | Rags removed and alarm floats lower in the lift station to improve response time. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-07-30 | 1 | 1 | 0 | 0 | 0 | 0
2015-06-10 | 2015-06-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2858 Marco Drive, NW | 980 | fax received 6/11/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/11/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-12 | 2018-01-12 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 1750 Stone Meadow Road | 300 | Found spill notification in DMR | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System |  |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/12/2018 12:00:00 AM | Oconee |  |  |  | 0 | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | infiltration/Inflow | Spill did not enter stream |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-19 | 2017-01-19 | Thomaston, City of (Town Branch WPCP) | Upson |  | 111 Monroe Street | 225 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/19/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease clogged. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-15 | 2017-02-15 | Savannah, City of (President Street WRF) | Chatham | Savannah | Intersection of York Lane and East Broad St., Savannah | 44099 | Verbal and written notification received 2/15/17. | Raw Sewage | Coastal District | GA0025348 | Force Main | Stream | Stream | Contractor |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 2/15/2017 12:00:00 AM | Savannah | 2/15/2017 12:00:00 AM | 2017-02-15 | 2018-01-30 | 1 | Savannah River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 |  | 0 | Break on a 20" force main occurred while testing of line was being performed upstream in conjunction with a major roadway project. | Rerouted the flow to discharge to another location. Repairing and replacing approximately 300' of the 20" force main. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-02-17 | 0 | 1 | 0 | 1 | 1 | 1 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2016-01-22 | 2016-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 1270 | fax received 1/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/22/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-13 | 2016-06-13 | Savannah, City of (President Street WRF) | Chatham | savannah | 37 Port Royal, Wilmington Island, Savannah, GA 31410 | 5600 |  | Raw Sewage | Coastal District |  | WWTP | Stream | Stream | Equipment failure |  | Steve Fox | Steve Fox | Steve Fox | 6/14/2016 12:00:00 AM | Savannah | 6/14/2016 12:00:00 AM |  |  | 1 | Betz creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Open sewer lateral clean-out while City of Savannah repaired sewer cave-in | Repaired sewer cave-in and mitigated spill site. Spill notification markers were placed at the spill site, at Penn Waller / Betz Creek, and Walthour Road / Betz Creek. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-15 | 1 | 1 | 0 | 0 | 0 | 0
2017-12-31 | 2017-12-31 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 5227 Ferry Creek Lane Acworth | 4173 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 1/1/2018 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Tate Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in gravity sewer line caused an overflow out of 4" service cleanout | Construction jetted the line to clear blockage | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-01-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-09 | 2015-07-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 187 Whiteford Avenue, SE | 2835 | fax received 7/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/10/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-19 | 2017-12-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 3611 Woodbriar Circle Tucker, GA 30084 | 960 | Into Tributary A | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/19/2017 1:09:00 PM | Ocmulgee | 12/19/2017 12:00:00 AM |  |  | 1 | South Fork Peachtree creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage, m/h 18-187-s211 and rags | Pressure wash line |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0 | Cornelius Williams |  | Dekalb Co Dept. Watershed Management
2017-06-30 | 2017-06-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 100 | Notification received on July 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Ground, Storm Drain |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 7/1/2017 12:00:00 AM |  |  |  |  | 0 | Dry land spill | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected at 21:00 hours when Snapfinger Plant's mechanics replaced an elbow, changed the flange gaskets, stopped the overflow and restored normal services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-07 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 2440 | fax received 12/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-22 | 2017-06-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2660 Peachtree Rd. NW - ATL | 840 | Email received 2017-06-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/27/2017 12:00:00 AM |  | 6/22/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (East Area CSO) | Fulton | Atlanta | Custer Avenue CSCF | 15800000 | Verbal and electronic mail notification not received until 12/28/2015. THIS IS A "CSO" AND COUNTS TOWARDS THE ROLLING AVERAGE ALLOWED IN THE PERMIT. | Primary Effuent | Wastewater Regulatory Program | GA0037168 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/28/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload of the East Area CSS. See attached document for details. This is a CSO of partially treated effluent. Total volume = 15,800,000 gallons. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-15 | 2016-10-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 111 Ormond Street, SE, Atlanta | 440 | Fax received on 10/16/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/16/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the main line. | This section was placed on a periodic inspection schedule, and to evaluate the need for upgrading, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-07 |  |  | DeKalb |  | 1752 Saint Lawrence Cove | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-13 | 2015-07-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 875 N. Grand Avenue, NW | 3420 | fax received 7/14/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/14/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-10 | 2016-11-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1630 W. Peachtree St., NW, Atlanta | 25 | Fax Recieved on 11/11/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/11/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the main line. | Hydraulic pressure cleaner used to remove debris. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-25 | 2016-08-25 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 602-617 Overlook Wood Way | 6554 | fax received 8/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Rags |  |  | Kim Hembree | Kim Hembree | 8/25/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Yellow River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Other Flushables | Raked and spread lime. Placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-09-03 | 2018-09-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 809 Peachtree Battle Ave. NW - Atlanta | 2600 | Fax sent 2018-09-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 9/4/2018 12:00:00 AM |  | 9/3/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump malfunction | Crew made mechanical repairs |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-29 | 2016-01-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1024 Litherland Court, SE | 610 | fax received 1/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/30/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-01 | 2018-04-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 31 Si Prado NE - Atlanta | 0 | Due to the ransomware attack on City of Atlanta, reports are being handwritten. Some information may be missing or hard to read. Spill amount undetermined as of 2018-04-01 Fax sent 2018-04-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/2/2018 12:00:00 AM |  | 4/2/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-15 | 2017-11-15 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1855 Park Drive, Columbus | 382 | Phone call received on 11/15/2017; fax received on 11/16/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/15/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 10" sewer main was clogged with debris causing overflow. | Debris cleared, overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-11-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-18 | 2015-07-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 102 Rogers Street, SE | 3186 | fax received 7/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/19/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew had to make repairs on the line in order to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-04 | 2017-08-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 97 Laurel Forest Cir. NE - ATL | 3255 | Fax received 2017-08-05, in mailbox 2017-08-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/5/2017 12:00:00 AM |  | 8/4/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-10 | 2017-05-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2551 Ivydale Dr. SW - ATL | 3050 | Fax received 2017-05-11 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/11/2017 12:00:00 AM |  | 5/11/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was equipment failure. | The crew made repairs to the by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-29 | 2015-06-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 809 Peachtree Battle Avenue, NW | 6225 | fax received 6/30/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/30/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-11 | 2015-09-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 442000 | CTS No. 77806 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 9/11/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-01 | 2016-02-01 | Cobb County MS4 | Cobb |  | 6819 Ivy Log Dr. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Gordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" PVC Main |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-19 | 2015-10-19 | Marietta (City of)- Sewers | Cobb | Marietta | 1550 Oakpointe Dr. At bridge on sewer easement. | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure. An exposed sewer main bell joint was leaking due to a failing gasket seal. A small amount of sewage was escaping to the nearby creek. | Marietta Water personnel quickly repaired the joint and shored up the bank with rock thus restoring normal service. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-22 | 2018-07-23 | Canton, City of (Canton WPCP) | Cherokee |  | Anderson Avenue, Canton: manhole at the Riverview Apartments behind Hardee's | 8100 | Due to the location of the manhole the majority of the sewage collected in a low lying area in and along the tree line and ran a wet weather ditch that feeds into an unnamed tributary to the Etowah River. The accessibility of this area is problematic due to ditch lines and vegetative growth the area could not be surveyed, but the topography of the area would limit the volume of the spill entering the Etowah River. | Raw Sewage | Mountain District - Cartersville | GA0025674 | WWTP | Stream |  | Grease |  | Katie Meade | Kathy Lewis | Katie Meade | 7/23/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed tributary to the Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rag blockage in the sewer line causing a backup and overflow. Notification of the spill was called in at 8 pm on 7/22/2018. | Using a jetter the blockage was cleared, and the pipe was cleaned. Granular degreaser was applied to the upstream manhole to remove any residual grease. Quick lime and straw was spread on the affected soil and the area was cordoned off. This manhole is one of many that is inspected weekly to try and prevent blockages. Manhole was last inspected on Friday 7/20/2018 and the flow though the manhole was normal with no issues. | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-07-24 | 1 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jesters Lake Drive, Jonesboro MH 2215621 | 441000 | Fax received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/4/2016 12:00:00 AM | Flint |  |  |  | 1 | Jester Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Heavy rainfall. | Began spill documentation, and made area safe during event. Sampling and lines upstream will be inspected for source of inflow and infiltration (I/I). | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-04 | 2016-05-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2355 Bolton Road, NW | 520 | fax received 5/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/6/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-12-08 | 2017-12-10 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 2803 Ga Hwy 100 Brocks Lift Station Tallapoosa | 36000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Power failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 12/11/2017 12:00:00 AM | Tallapoosa |  |  |  | 0 | Walker Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Extreme weather power outage that shut down our city, with emergency or back up power preventable | Power restored, treated area with hydrated lime and clean up persistent | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Adairsville, City of (North WPCP) | Bartow |  | 106 Cass Street | 42000 |  | Raw Sewage | Mountain District - Cartersville | GA0046035 | WWTP | Stream |  | Hydraulic Overload |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/7/2018 12:00:00 AM | Coosa |  |  |  | 0 | Oothkalooga Creek Tributary to the Oostanaula River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Major inflow and infiltration problems | Physically inspect every sewer manhole within the city sewer system and document the following conditions on the city's GIS sewer mapping software. Begin manhole surveys in the low lying areas. As defective manholes are found repair them. Compile an accurate sewer amp accessible through the City's GIS. Continue with the flow monitoring effort to isolate the problem areas. When suspect sewer zones are identified, employ smoke testing to locate specific sources of inflow. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-24 | 2017-09-24 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2577 Oakridge Drive | 2760 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/24/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Honey Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Frease and Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1440 Sowell Estate, Stone Mountain | 14150 | Notification received on January 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/21/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 19:20 hours when the heavy rain stopped and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-07 | 2016-05-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 610 Alex Drive, SW | 356 | fax received 5/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/8/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew set up a bypass pump to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-24 | 2015-11-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snapfinger Woods Drive, Decatur | 2140 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/24/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:26 hours when the crew rodded the main. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-14 | 2017-04-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4776 Snafinger Woods Drive, Decatur | 6560 | Notification received on April 18, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/14/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease / Rags blockage | The problem was corrected at 11:26 hours when a crew rodded between manholes 36ft in the 8" sewer main, clearing the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-18 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-02 | 2017-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 270 Washington St, SW - ATL | 756 | Fax received on 02/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 2/3/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | the crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-05 | 2017-09-05 | Cobb County Water System | Cobb |  | 275 Shallow Manor Drive | 12000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson |  | Reginald Williamson | 9/5/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2017-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-29 | 2015-08-30 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 600 Block of Scott Drive | 61100 | CTS No. 77714 and 77716. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 8/29/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Joe Coleman Drive - Augusta | 60000 | Fax received 2017-01-03, update received 21017-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding caused highly diluted wastewater to begin running out of several manholes by 11:00 AM on January 2, 2017. | Line is being monitored until normal flow resumes. Notifications posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-15 | 2016-02-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1033 Hollywood Road, NW | 1780 | fax received 2/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/16/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-17 | 2017-06-17 | Dekalb County (Snapfinger Creek WPCP) |  | Decatur | 1846 Meadow Lane, Decatur | 2680 | Notification received on June 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh |  | 6/17/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 19:15 hours when the crew pressure washed the 8" sewer main 375ft, cleared the grease blockage at 175ft and restored normal service. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-21 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-29 | 2015-01-29 |  | Spalding | Griffin | Lake Avenue sewer outfall line | 7200 | Notification received on January 29, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/29/2015 12:00:00 AM |  |  |  |  | 0 | Unnamed tributary to Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The line was cleared and the area was limed. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-28 | 2016-08-28 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 4310-4339 Old Bridge Lane | 7044 | fax received 8/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/29/2016 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Shoveled up and removed debris from roadway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-04 | 2015-01-04 |  | DeKalb | Decatur | 101 Green Street, Decatur | 5175 | Notification received on January 5, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/5/2015 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | The problem was corrected at 09:39 hours when a crew inspected manholes up and downstream, rain receded, and restores regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-17 | 2015-05-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2950 Martin L. King Jr. Drive, SW | 2805 | fax received 5/17/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/17/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-27 | 2016-06-27 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton |  | 8321 Magnolia Drive, Jonesboro Manhole ID #2216036 | 27000 | Fax received on 06/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 6/28/2016 12:00:00 AM | Flint |  | 2016-06-29 |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | Other | Pumps were restored to full functionality and surcharge was corrected. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-29 | 0 | 1 | 1 | 1 | 0 | 0
2016-06-27 | 2016-06-27 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8321 Magnolia Drive, Jonesboro Manhole ID #2216036 | 27000 | Fax received on 06/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Other |  |  | Paul Moisan | Paul Moisan | 6/28/2016 12:00:00 AM | Flint |  | 2016-06-29 |  | 1 | Flint River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | Other | Pumps were restored to full functionality and surcharge was corrected. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-29 | 0 | 1 | 1 | 1 | 0 | 0
2017-11-02 | 2017-11-02 |  | Clarke |  | 300 Eaglewood Court | 414 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2017 12:00:00 AM | Oconee |  |  |  | 0 | Middle Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | clogged pipe | flushed sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-02 | 2017-11-02 |  | Clarke | athens | 300 Eaglewood Court | 414 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2017 12:00:00 AM | Oconee |  |  |  | 0 | Middle Oconee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | clogged pipe | flushed sewer | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-17 | 2015-08-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 5935 Magnolia Ridge, Stone Mountain | 2400 | Notification received on August 17, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Grease |  |  | Hsin Yeh |  | 8/17/2015 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:39 hours, when the clean-up crew, rodded the sewer main up and downstream and restored regular flow. |  |  | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | Rocky Creek Lift Station. | 79050 | Email received on 12/25/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Lift Station | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/25/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rainfall, hydraulic loading pumps were overwhelmed at the Rocky Creek Lift Station causing an overflow into Rocky Creek. | An additional pump was replaced and flows returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-21 | 2017-02-21 | East Point (City of)- Sewers | Fulton | East Point | 1961 Dunlap Street from Manhole ID #C163-088 | 5500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek Basin | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The probable cause of the spill was rag and diapers in the sewer line, causing a backup. | The City's crew jetted and vacummed out the Main to remove the blockage, and cleaned the affected area, spread lime as required. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-22 | 2016-04-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 187 Whitefoord Avenue, SE | 290 | fax received 4/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 4/23/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-10 | 2017-05-10 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1501 Milstead Road | 2580 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/10/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Ragging | Clean Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-05 | 2018-07-05 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Manhole 835-3438 near LS 22. | 195000 |  | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Stream |  | Equipment failure |  |  | Juan Robles | Juan Robles | 7/6/2018 12:00:00 AM | Flint |  |  |  | 0 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at LS 22 (short circuit on control panel). | All controls were replaced on LS 22. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-09-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-20 | 2015-02-20 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1585 S Ponce De Leon Avenue, NE | 678 | fax received 2/21/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 2/21/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The crew performed point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-10 | 2018-03-11 | Chatham County | Chatham | Savannah | 2221 Cinder Landing Court, Savannah, GA | 94402 | Initial phone call to emergency response on 3/11/18. Full report received 3/14/18. | Raw Sewage | Coastal District | GAU060099 | Collection System | Storm Drain, Stream | Stream | Debris |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 3/11/2018 12:00:00 AM |  |  |  |  | 1 | Herb Creek - Wilmington River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Dirt and debris, potentially attributable to a buried manhole, clogged the sewer line between two lift stations. | Turned off the lift stations. Used vac truck to jet out the lines. Uncovered, cleaned out, and raised the buried manhole. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-03-15 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CHATHAM COUNTY
2015-08-27 | 2015-08-27 |  |  |  | Manhole ID#3758 Industrial Park offof King Mill Road | 6400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/27/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Indian Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | It was determined that a deteriorated pipe had collapsed causing the blockage. | Crews were able to quickly divert the flow from the pump station to a nearby manhole. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-03 | Tifton, City of (New River WPCP) | Tift | Tifton | manhole located at 720 Tifton Eldorado Road, Tifton, GA | 21600 | Voice mail received on 02/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/4/2016 12:00:00 AM |  | 2/4/2016 12:00:00 AM |  |  | 1 | Gum Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was due to rainfall which created surcharges in the system. | mitigated by hydrated lime and will begin monitoring program). | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-05 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-02 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WPCP 6th Street SW., Cairo | 0 | Initial call received 4/4, full report received 4/6. The influent and effluent spill both occurred on April 1, 2016. Monitoring results are submitted in regards to the effluent spill. | Treated Effluent | Wastewater Regulatory Program | GA0025771 | WWTP | Stream | Stream | Hydraulic Overload |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 4/4/2016 12:00:00 AM | Ochlockonee | 4/1/2016 12:00:00 AM | 2016-04-01 |  | 1 | Parker's Mill Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 1 | Hydraulic overload at the effluent side of the WWTP due to extremely heavy rainfall. Flow volume = 57,750 gals. Flow, Weekly Average (MGD): permit = 3.75, reported = 5.10 |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-04-05 | 0 | 1 | 1 | 1 | 0 | 0 | [8 empty] | CITY OF CAIRO | 229-377-5025
2016-11-16 | 2016-11-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 924 Woods St., NW, ATL | 790 | Fax received on 11/17/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 11/17/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | The crew made a repair to the by-pass pump. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-26 |  | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 4594 Lakewood Ave. | 1100 | The facility representative will send the full report shortly. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ditch |  | Rags |  | Mark Wyland |  | Reginald Williamson | 4/26/2018 12:00:00 AM |  |  |  |  | 0 | Wolf Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Gravel |  | 33e43666-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2018-04-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-23 | 2017-10-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Fakes Mill Road, Ellenwood | 22050 | Notification received on October 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 10/23/2017 12:00:00 AM |  |  | 2017-10-24 |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Storm Event / I&I | The problem was corrected at 15:12 hours when the first responder crew waited on the storm event to subside, flow volume to decrease, and the flow returned normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-22 | 2015-05-22 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Latitude 34.508179 Longitude 83.550438 | 300 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Pipe failure |  | Cindy Nix | Kathy Lewis | Cindy Nix | 5/22/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Little Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Overflow due to a cracked force main beside the lift station. | The flow was stopped and the affected area leading to the tributary was treated with hydrated calcium carbonate. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-06-04 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2324 Adams Dr. NW - ATL | 2480 | Fax sent 2018-02-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 2/8/2018 12:00:00 AM |  | 2/7/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain-induced spill | Unknown |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-18 | 2016-11-18 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 3714 Cactus Trail, Martinez | 100 |  | Raw Sewage | Wastewater Regulatory Program | GA0031984 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Kim Hembree | 11/18/2016 12:00:00 AM |  |  |  |  | 0 | Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Unstopped with high power jet machine and removed debris. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-05 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-24 | 2015-11-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2533 Henderson Mill Road, Atlanta | 1 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/24/2015 12:00:00 AM |  |  |  |  | 0 | Henderson Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing Leaking. | The problem was corrected at 15:35 hours when the crew built a berm and then repaired the main. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-24 | 2016-06-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 5420 Riverdale Road, College Park Manhole #2213464 Spill ID 128915 | 2400 | Fax received on 06/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 6/24/2016 12:00:00 AM | Flint |  |  |  | 1 | Sullivan Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow was returned to normal. Site was cleaned. Lines will be televised and grease cleaned, and if a problem is located, it will be repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-06-28 | 0 | 1 | 1 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Bell Drive @ Clay Drive - Augusta | 60000 | Email received 2017-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Swale | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/10/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richmond County area. | Line is being monitored until normal flow resumes. Notifications posted. Will assess the system through flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-27 | 2015-11-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 2468 Brookhurst Drive, Dunwoody | 3600 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 11/27/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected at 17:05 hours when the crew pressure washed the main. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-08 | 2016-06-08 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Conley | 4215 Thurman Drive, Conley | 4250 | Notification received on June 9, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 6/9/2016 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | The problem was corrected at 14:25 hours, when a crew pressure washed the sewer main 275ft, cleared the blockage at 170ft, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-05 | 2015-10-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2384 Spring Creek Road, Decatur | 54750 | Notification received on October 8, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/5/2015 12:00:00 AM |  |  |  |  | 0 | Burnt Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole Damage | The problem was corrected at 20:50 hours when the repair crew constructed a berm around the pipe with sandbags and hydraulic cement to contain the spill, called ina work order to repair 24" line and restore regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-28 | 2015-08-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 917 Stonewall Drive, SE | 30 | Fax received 8/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 8/28/2015 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-28 | 2017-06-28 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 8344 Dunellen Ln, Jonesboro Manhole 2202008 | 2800 | Fax received on 06/29/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 6/29/2017 12:00:00 AM | Flint |  |  |  | 1 | Kendrick Waters | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Shot and cleared blockage and flow returned to normal. Televise and make recommended repairs. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-06 | 0 | 1 | 1 | 0 | 0 | 0
2016-09-14 | 2016-09-14 | Marietta (City of)- Sewers | Cobb | Marietta | 700 Brookline Dr. | 2250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/15/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease/Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-15 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-13 | 2017-05-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 934 Euclid Ave. NE - ATL | 50 | Fax received 2017-05-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  |  |  |  | Alys Hannum | Alys Hannum | 5/15/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a collapsed mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-06 | 2017-03-06 | Columbus Water Works (South WRF) | Muscogee | Columbus | Mile Marker 2 JR Allen Parkway, Columbus | 760 | Fax received on 03/07/2017; voice mail received on 03/06/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tributary of Roaring Branch Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A main was clogged with debris, causing the manhole to overflow. | Once the debris was cleared from the main, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-31 | 2016-01-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2419 Coventry Drive, Columbus | 14273 | Fax and email received 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Lindsay Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic overloading, a manhole overflowed into Lindsay Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-09-20 | 2015-09-20 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 7926 Malone Street, Douglasville, GA 30134 | 200 | Notification received by fax on 09/21/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Collection System | Stream |  | Contractor |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/21/2015 12:00:00 AM | Flint |  |  |  | 1 | Huey Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer plug - contractor performing sewer line work for the Hwy 92 GDOT project installed sewer plug in downstream invert of manhole. | VacCon Crews were dispatched to the site and a jet truck was used to try and clean the line and clear the blockage. VacCon crews were unable to clear the blockage, and upon investigation inside the manhole the crews were able to determine a sewer plug had been installed in the downstream invert of manhole. Crews cleaned and disinfected the area around the manhole where the spill occurred. Signs were posted in the area to notify residents and public of the spill. Notification given to EPD, the Health Dept., and local media. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-09-23 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-17 | 2016-05-17 | Savannah, City of (President Street WRF) | Chatham | savannah | 7722 Waters Ave | 9180 |  | Raw Sewage | Coastal District |  | WWTP | Canal | Canal | Hydraulic Overload |  | Steve Fox | Steve Fox | Steve Fox | 5/17/2016 12:00:00 AM | Savannah | 5/17/2016 12:00:00 AM |  |  | 1 | casey canal | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Major rain event caused overflow (mix of storm water and sewage) from a manhole to the storm system | Reduced and stopped overflow by reducing upstream lift station flows. Spill notification markers were placed at the spill site where discharge went into Canal along with other locations – Eisenhower / Casey Canal, Sallie Mood / Casey Canal, and Montgomery Crossroads / Hayner’s Creek. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-06-01 | 1 | 1 | 0 | 0 | 0 | 0
2015-01-15 | 2015-01-16 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | Vocie message left with EPD on 1-16-2015. ERT contacted 1-16-2015. CTS No. 75720. | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This is a major outfall spill of treated effluent from the RM Clayton WRC. "TSS data from the composite samples confirmed that the effluent limit was exceeded on both the 15th (260 mg/L) and 16th (37 mg/L), but returned to within permitted limits on the 17th." "The root cause appears to have been due to a failure of the City’s vendor to deliver the necessary treatment chemicals on multiple occasions and, as a result, the facility ran out of polymer. An emergency delivery was obtained from other plants and from another vendor and the facility was able to start processing the solids properly. The final estimated spill volume is 45.2 million gallons. A public notice has been submitted to the AJC for publication (anticipated for 1/24)." Volume = 83,200,000 gallons, per Kris Garcia 3/13/2015. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-15 | 2015-10-15 | Cartersville, City of (Cartersville WPCP) | Bartow |  | 4 Cook Street | 4000 |  | Raw Sewage | Mountain District - Cartersville | GA0024091 | WWTP | Stream |  | Equipment failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 10/15/2015 12:00:00 AM | Coosa |  |  |  | 0 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical failure of by-pass pump | Switched to back up pump and cleaned area affected by spill | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-10-15 | 0 | 0 | 0 | 0 | 0 | 0 | Bob Jones | 770-387-5653 | City of Cartersville
2015-06-02 | 2015-06-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2219 Tiger Flower Drive, NW | 1860 | fax received 6/3/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/3/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-07 | 2018-01-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 425 Fulton St. SW - ATL | 300 | Fax sent 2018-01-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/8/2018 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Cres used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-14 | 2015-07-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3700 Roswell Road, NE | 590 | fax received 7/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/15/2015 12:00:00 AM |  |  |  |  | 1 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | the crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1400 Block of Gornto Road | 47375 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive Rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-12-31 | 2017-12-31 | Marietta (City of)- Sewers | Cobb | Marietta | 750 Canton Rd | 1750 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/31/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-22 | 2018-08-22 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1228 N. Thornton Avenue, Dalton | 4200 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 8/23/2018 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed tributary of Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in main | Dalton Utilities cleared blockage with high pressure jet. Line was camera inspected. Location will be earmarked for proactive preventative root maintenance. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-23 | 1 | 0 | 0 | 0 | 0 | 0
2016-01-16 | 2016-01-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 1397 Witham Drive, Dunwoody | 6900 | Notification received on January 19, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Pipe failure |  |  | Hsin Yeh | Hsin Yeh | 1/16/2016 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | sewer main missing joints | The problem was corrected at 00:27 hours, when a crew replaced two joints of 8" PVC pipe to the main, stopped the sewage from spilling into the creek and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 236 Farrington Avenue, SE | 250 | fax received 1/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/22/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3109 Albatross Lane, Decatur | 92480 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Cobb Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected on December 25th, at 8:30 hours, when the rain subsided and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-21 | 2015-04-21 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2375 Butner Road, SW | 7750 | fax received 4/22/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/22/2015 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-22 | 2016-12-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 824 Dill Ave., SW, ATL | 147 | Fax received on 12/27/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/27/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic pressure cleaner was used. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2018-02-17 | 2018-02-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 292 Oakdale Rd. NE - ATL | 114 | Fax sent 2018-02-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/18/2018 12:00:00 AM |  | 2/18/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-31 | 2015-12-31 | Newnan Utilities (Wahoo Creek WPCP) | Coweta | Newnan | Behind 7 Southfield Dr. in Woodstream subdivision | 3690 | Spill reported late. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | White Oak Creek Drainage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line had gravel and other debree that had settleed on bottom slowing the flow down causing a blockage. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-04 | 0 | 0 | 0 | 0 | 0 | 0 | Brad Binion |  | NEWNAN UTILITIES
2017-11-01 | 2017-11-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2003 Glendale Drive, Decatur | 4700 | Notification received on November 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 11/1/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Water main break. | The problem was corrected at 13:15 hours when the first responder crew pressure washed the 8-inch sewer main 170-ft, cleared the blockage at 165-ft, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-11-03 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-24 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Central City Park, Willie Smokey Glover Road, Macon, GA (MH #57743). | 21190 | Fax and email received on 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Storm Drain |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-26 | 2016-11-28 | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was hydraulic overload. The area received 5.75 inches of rain from December 21-24. | This manhole (MH #57743) is located in a parking lot. The area was washed down and any debris was removed. The MWA will continue its search for inflow and infiltration into its sewer system through its CCTV and flow monitoring investigations. The MWA also has projects planned to rehabilitate two large sewer interceptors that feed the Lower Poplar Treatment plant. These projects will help to reduce the I/I into the MWA sewer system. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2015-10-19 | 2015-10-19 | Warrenton, City of (South Pond WPCP) | Warren |  |  | 10000 |  | Primary Effuent | Northeast District - Augusta | GA0032786 | WWTP | Unknown | N/A | Other |  | Madara Tyler | Madara Tyler | Madara Tyler | 10/20/2015 12:00:00 AM | Ogeechee | 11/19/2015 12:00:00 AM | 2015-10-20 | 2016-10-31 | 0 | Golden Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  |  | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 2015-11-19 | 0 | 1 | 1 | 0 | 0 | 0
2015-10-19 | 2015-10-19 | Warrenton, City of (South Pond WPCP) | Warren |  |  | 10000 |  | Primary Effuent | Northeast District - Augusta | GA0032786 | WWTP | Unknown | N/A | Other |  | Madara Tyler | Madara Tyler | Madara Tyler | 10/20/2015 12:00:00 AM | Ogeechee | 11/19/2015 12:00:00 AM | 2015-10-20 | 2016-10-31 | 0 | Golden Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  |  | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 2015-11-19 | 0 | 1 | 1 | 0 | 0 | 0
2018-05-15 | 2018-05-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4406 Snapfinger Woods Drive, Decatur GA 30035 | 1975 | manhole 15-128-s004 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/16/2018 7:20:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-03 | 2016-08-03 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 2300 Country Walk | 2848 | fax received 8/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/4/2016 12:00:00 AM |  |  |  |  | 1 | Jacks Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-01-27 | 2016-01-27 | Rincon, City of (RIncon WPCP) | Effingham |  |  | 550000 |  | Treated Effluent | Coastal District | GA0046442 | WWTP | Stream | Stream |  |  | Beth Stevenson | Beth Stevenson | Beth Stevenson | 2/12/2016 12:00:00 AM | Savannah | 2/12/2016 12:00:00 AM | 2016-02-12 | 2016-02-12 | 0 | Sweigoffer Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 100 | 0 | Exceeded 5-day BOD wk avg by greater than 50%. The WPCP suspects dumping of septic waste in a manhole and have alerted City workers, police and fire to be on alert. The WPCP did not realize qualified as a spill until the District notified them after reviewing the DMR. |  | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 2016-02-29 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-04 | 2015-05-04 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 34.6 mg/L on 05/04/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-05 | 2018-07-05 | Tignall, Town of (Tignall WPCP) | Wilkes |  |  | 5000 |  | Raw Sewage | Northeast District - Athens | GA0046141 | Lift Station | Ditch |  | Power failure |  | Phoebe Tchoua | Bonnie Pope |  | 7/5/2018 12:00:00 AM |  |  |  |  | 1 | Rhodes Pond eventual to Broad River | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | minor spill |  | 384e7336-1c4e-11e1-9fd5-12313b0cb679 |  | 33de4454-ee02-11e0-b8d8-000c29971acc | 2018-08-10 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-03 | 2015-12-03 | Rome, City of (Rome WRF) | Floyd |  | Coosa Valley Fairgrounds near City of Rome Lift Station | 39000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/3/2015 12:00:00 AM | Coosa |  |  |  | 1 | Etowah River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Signigicant wet weather event | Conducting an investigation | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2016-03-23 | 2016-03-23 | Columbus Water Works (South WRF) | Muscogee | Columbus | 2900 Woodruff Farm Road, Columbus | 9038 | Received a phone call and email on 03/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Shoreline | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 3/23/2016 12:00:00 AM | Chattahoochee | 3/23/2016 12:00:00 AM |  |  | 1 | Bull Creek Tributary | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A 15" main slipped out of place at the joint. | Once the pipe was repaired, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-10 | 2018-07-10 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 334 Canton Road - Cumming | 800 | Email sent 2018-07-11 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/11/2018 12:00:00 AM |  | 7/10/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Kelly Mill Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel, PVC pipe, and flushable wipes blocking the line | Line jetted and cleared. Area cleaned of debris, lime applied, signs posted and Health Dept. notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-06 | 2018-05-06 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 2949 Salem Road | 9625 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/8/2018 12:00:00 AM | Ogeechee |  |  |  | 0 | Beaverdam Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Ragging | Remove Grease and Ragging | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-28 | 2017-10-28 | Thomaston, City of | Upson | Thomaston | Walmart Lift Station Force Main | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/7/2017 12:00:00 AM | Flint |  |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Pipe Failure | Repaired pipe. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Eatonton - Putnam Water & Sewer Authority (Eastside WPCP) | Putnam | Eatonton | Eastside WPCP | 50000 |  | Raw Sewage | Wastewater Regulatory Program | GA0032271 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/4/2017 12:00:00 AM |  |  |  |  | 0 | Rooty Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet Weather | Corrective action has been taken, grounds cleaned up, signs posted at affected waterways, stream monitoring in affect. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court, Decatur GA 30032 | 13500 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/7/2018 6:49:00 PM | Ocmulgee |  |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | storm event | Wait until storm passed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-09 | 2015-06-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2051 Flat Shoals Road, SE | 4560 | fax received 6-10-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 6/10/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-08-27 | 2016-08-28 | Dublin, City of (Dublin WPCP) | Laurens | Dublin | Lancaster and Woodrow Street | 250 | Email notification received 8/28/2016 | Raw Sewage | Wastewater Regulatory Program | GA0025569 | Collection System | Ravine | Ditch | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/28/2016 12:00:00 AM |  | 8/28/2016 12:00:00 AM |  |  | 1 | Drainage Ditch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe break at stream crossing | pipe repaired | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF DUBLIN
2015-05-24 | 2015-05-24 | Columbia County (Little River WPCP) | Columbia |  | Crawford Creek WPCP, 1000 Shepard Way | 100000 | Verbal notification received 5/25/2015. Fax notification received 5/26/2015 | Waste Activated Sludge | Wastewater Regulatory Program | GA0047775 | WWTP | Stream |  | Operator error |  | Sarita Banjade | Kim Hembree | Kim Hembree | 5/25/2015 12:00:00 AM |  |  |  |  | 1 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wasting pump was left in manual mode and was not turned off at the appropriate time | Wasting will be done on timer, not by hand | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY | 706.868.3474
2015-06-08 | 2015-06-08 | Griffin, City of (Cabin Creek WPCP) | Spalding | Griffin | Outfall off of Old Macon Road | 33000 |  | Raw Sewage | Wastewater Regulatory Program | GA0020214 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/10/2015 12:00:00 AM |  |  |  |  | 0 | Cabin Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and rocks blockage 8" sewer outfall line. | Rodded line/Cleaned area and limed area |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-06-16 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-17 | 2016-08-17 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12. Lab results indicated 32 mg/L BOD with a flow of 1.01 MGD. | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 9/9/2016 12:00:00 AM | Ogeechee | 9/9/2016 12:00:00 AM | 2016-09-12 |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Facility is having issues treating high BOD that is brought in from waste stabilization pond. | Coastal Processing installing a DAF unit on 9/13/16 for treatment, bypassing pond to allow it to mature. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-494-2474 |  | 32
2018-02-01 | 2018-02-01 | Garden City (Garden City WPCP) | Chatham | Garden City | 22 Brampton Road, Garden City, GA | 3600 | Initial phone call received 2/1/18. Full report emailed 2/2/18. | Raw Sewage | Coastal District | GA0031038 | Collection System | Ditch | Ditch | Pipe failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 2/1/2018 5:30:00 PM | Savannah | 2/2/2018 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Sewer service line broke causing sewage to spill into adjacent ditch. | Repaired line. Placed sand bags to contain spill. Used vac truck to clean ditch and laid lime on area. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-02-05 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | Garden City | 912-966-7777
2017-01-04 | 2017-01-04 | Rome, City of (Rome WRF) | Floyd |  | 402 Cedar Avenue | 3000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 1/4/2017 12:00:00 AM | Coosa |  |  |  | 0 | Silver Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots in the sewer main | Sewer main was thoroughly cleaned | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-29 | 2018-06-29 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | Red Lodge Lift Station-2797 Red Lodge Way, Douglasville, GA 30135 | 1000 |  | Raw Sewage | Wastewater Regulatory Program | GA0038709 |  | Stream | Stream | [5 empty] | 6/18/2018 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical storm caused a power outage and damaged electrical components in the control cabinet. | Crews were dispatched to the site. Mechanics/electricians were dispatched to the site and repaired electrical components inside the control panel. Crews cleaned and disinfected the area. Notification given to EPD, DoH, and local media. |  |  |  | 2018-06-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-28 | 2015-12-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 396 Brownlee Road, SW | 246 | This is a private spill. Spill report received 1/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/8/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. This is a private spill | Private spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-29 | 2017-03-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1811 Moores Mill Rd. NW - ATL | 150 | Fax received 2017-03-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/30/2017 12:00:00 AM |  | 3/29/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill at 9:00 PM. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-23 | 2015-01-24 |  | Lowndes | Valdosta | 2400 Block of Meadowbrook | 6000 | Email notification from the City received 1/24/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/24/2015 12:00:00 AM |  |  |  |  | 1 | Two Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-01-04 | 2017-01-04 | Columbus Water Works (South WRF) | Muscogee | Columbus | 564 Chesterfield Drive, Columbus | 876 | Telephone call and fax received on 01/05/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Debris |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/5/2017 12:00:00 AM |  |  |  |  | 1 | Double Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a main clogged with debris. | Once the debris was cleared from the main, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | Chris Cornett |  | COLUMBUS WATER WORKS
2015-10-14 | 2015-10-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2487 Howell Mill Road, NW | 1112 | fax received 10/19/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/19/2015 12:00:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-13 | 2017-03-13 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2228 Broad Street - Augusta | 450 | Email received 2017-03-14 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 3/14/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, rags and debris. | Sewer gravity main was cleaned and the downstream storm pipe was flushed and vacuumed out. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2005 Bencal Drive, Atlanta | 54000 | Notification received on May 1, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 4/27/2017 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | This spill wasn't report to DWM until April 24, 2017. It was determined that a spill of approximately 54,000 gallons had entered into Sugar Creek due to a heavy rain event on a 8 inch sewer main. The homeowner stated that the spill began around 10:00 and concluded around 16:00 on January 21st. DMW is going to pick up the follow-up spill sampling. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-01 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-03 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1200 Block of Waynewright Street | 199550 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2018-01-20 | 2018-01-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 210 Paris Drive - Lawrenceville | 4205 | Fax sent 2018-01-20 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  |  | Alys Hannum | 1/20/2018 12:00:00 AM |  | 1/20/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Little Suwanee Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, Paper, and other products; Grease | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-30 | 2017-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2222 Donald Lee Hollowell Dr. | 5 | Fax received on 01/31/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 1/31/2017 12:00:00 AM |  |  |  |  | 0 | Dryland | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was greas in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Rockdale County (Quigg Branch WPCP) | Rockdale | Conyers | 1060 Scott Street | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/10/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ragging in Sag | Repair Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 500 Dairy Pak Rd., Athens | 18925 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Other |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/30/2015 12:00:00 AM | Oconee | 12/30/2015 12:00:00 AM | 2016-01-02 |  | 1 | wetlands to North Oconee River | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Manhole overflowed during flood event | Cleaned the area. Vac truck captured much of the spill before it reached the wetlands. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-04-06 | 2015-04-06 | CITY OF ATLANTA - SOUTH RIVER WRC | Fulton | Atlanta | Intrenchment Creek WRC | 471000 | verbal notification received 4/7/2015. CTS No. 76395) | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 4/7/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Storm induced hydraulic inflow from high flows during a high intensity storm event. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-04 | 2016-03-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1957 Glenwood Ave. Atlanta | 1000 | Notification received on March 8, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 3/5/2016 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 18:15 hours, when a crew clamped the sewer main to seal the leak, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-08 | 0 | 1 | 0 | 0 | 0 | 0
2018-01-30 | 2018-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 458 Cherokee Ave. SE - ATL | 10 | Fax sent 2018-01-31 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/31/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 |  | Fulton | Atlanta | 2487 Howell Mill Road, NW | 1560 | fax received 11/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 11/4/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain induced |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-09 | 2015-04-09 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 2400 | fax received 4/10/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 4/13/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism, grease, debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-28 | 2018-01-28 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 2100 Steeple Chase Lane Roswell | 9120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/28/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-16 | 2017-04-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 118 Roseclair Dr. SE - ATL | 2 | Fax received 2017-04-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 4/17/2017 12:00:00 AM |  | 4/16/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris and a crack in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-25 | 2017-08-25 | Columbia County (Crawford Creek WPCP) | Columbia | Grovetown | 426 Keesaw Glen - Grovetown | 6000 | Fax received 2017-08-26 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 8/26/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Private Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Construction debris, rocks and sand. | Unstopped overflow with high pressure jet machine. Removed pieces of pipe and rocks from manhole. Planned follow-up video inspection. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-23 | 2016-03-23 | Buford, City of (Southside WPCP) | Gwinnett | Buford | Manhole between Roy Carlson Blvd and Bryant Road | 100000 | Verbal and email notification received 3/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0023167 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/23/2016 12:00:00 AM |  |  | 2016-03-23 | 2017-04-12 | 1 | Suwanee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease and debris | Blockage removed | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-25 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF BUFORD
2016-07-19 | 2016-07-19 | Cobb County MS4 | Cobb |  | 2944 Lowe Way | 180 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Swale | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" PVC Main | Stopped spill and washed down effected area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-08 | 2017-01-08 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 3305 Ridgefare Drive - Cumming | 5000 | Fax received 2017-01-09. Letter received 2017-01-13. | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream | Stream |  |  |  | Alys Hannum | Hsin Yeh | 1/9/2017 12:00:00 AM |  | 1/8/2017 12:00:00 AM |  |  | 1 | Sawmill Branch (trib to Big Creek) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause was roots and PVC pipe partially blocking the sewer line. | Cleaned the area affected. Lime applied. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-02 | 2018-04-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5352 North Peachtree Road, Dunwoody GA 30338 | 9440 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/3/2018 5:50:00 AM | Ocmulgee |  |  |  | 1 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken pipe | by-pass pump set to contain sewage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-06-11 | 2015-06-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1455 Fairmont Avenue, NW | 2941 | fax received 6/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/12/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-03-21 | 2018-03-21 | Cobb County Water System | Cobb |  | 735 Ernest Barrett Pkwy | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/21/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Larual Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Melrose Drive - Augusta | 60000 | Email received 2017-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/10/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-04 |  | 1 | Tributary to Rocky Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding throughout the Augusta Richhmond County area. | Line being monitored until normal flow is resumed. Notifications posted. Will assess the system via flow monitoring and CCTV to determine any areas with inflow and infiltration. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-19 | 2015-05-19 | Columbus Water Works (South WRF) | Muscogee | Columbus | Ditch @ 1304 Hunt Ave. | 337 | REC EMAIL 5/20/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Ditch |  | Debris |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/20/2015 11:25:00 AM | Chattahoochee |  |  |  | 1 | Mill Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and debris | The rags and debris were removed immediately and the overflow stopped. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2017-01-13 | 2017-01-13 | Savannah, City of (President Street WRF) | Chatham | Savannah | 709 Mall Blvd., Savannah, GA | 2000 | Initial notification and full report emailed to Hailey Harden 1/13/2017 | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Equipment failure |  |  | Dagny Pariani | Dagny Pariani | 1/13/2017 12:00:00 AM | Savannah | 1/13/2017 12:00:00 AM |  |  | 1 | Chippewa Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure during sewer main repair | Restored pump service. Contained the spill and redirected into sanitary sewer |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2017-10-17 | 2017-10-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2060 Peachtree Rd. NW - ATL | 50070 | Complaint called in 2017-10-17. Email sent 2017-10-18 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 10/18/2017 12:00:00 AM |  | 10/18/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Collapsed mainline. | By-pass pump installed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-16 | 2018-01-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2392 Pryor Rd. SW - ATL | 180 | Fax sent 2018-01-16 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum |  | 1/17/2018 12:00:00 AM |  | 1/16/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-14 | 2017-03-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3158 Beech Drive, Decatur | 347250 | notification received on March 20, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Contractor |  |  | Hsin Yeh | Hsin Yeh | 3/15/2017 12:00:00 AM |  |  |  |  | 1 | Cobbs Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outside contractor: Utility Group Inc.; bored through the 36 inch water main, which caused the 8 inch sewer main to reach full capacity, and overflow into the waterway. | The problem was corrected on March 15, 2017 at 11:42 hours when a crew turned off the 36" water main and the water finally receded to stop the manhole from overflowing. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-03-20 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-16 | 2015-11-16 |  | Cobb |  | 1030 Driskell Court | 80 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 8:45 a.m. and our crew stopped the overflow at 9:25. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 0 | Stephen McCullers |  | Cobb County Water System
2016-03-16 | 2016-03-16 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 208 Marco Drive | 350 | verbal notification received 3/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/17/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Cleared blockage with jet machine. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2017-03-01 | 2017-03-01 | East Point (City of)- Sewers | Fulton | East Point | 3160 Beech Drive East Point | 6000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags and Diapers | The City's crew jetted and vacuumed out the Main to remove the blockage, and cleaned the affected area, spread lime as required. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2788 Forrest Hills Dr., SW, ATL | 25 | Fax received on 12/07/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 12/7/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic Pressure Cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-08 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2015-12-24 | 2015-12-25 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1520 Dixon Drive, Columbus, GA | 19220 | Fax received on 12/24/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | Due to excessive rainfall, hydraulic loading a manhole overflowed into Weracoba Creek. | Once the rainfall subsided, and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2016-01-01 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1549 Celia Drive, Columbus. | 31643 | Fax and email received on 01/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Bull Creek. | Once the rain subsided and flow returned to normal the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Edmondson Lift Station, near 611 Wildwood Drive | 23400 | fax received 12/31/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Storm Drain |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/31/2015 12:00:00 AM |  |  |  |  | 1 | Strom drain leading to private lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | Excessive rain - 3.9" |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2017-02-10 | 2017-02-10 | Cobb County Water System | Cobb |  | 1977 South Cobb Dr. | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel in 8 in" vc main | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-27 | 2016-02-27 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 787 Sparkleberry Road | 6000 | fax received 2/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Other |  | Roots |  |  | Kim Hembree | Kim Hembree | 2/27/2016 12:00:00 AM |  |  |  |  | 0 | Private Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Removed roots. Cleaned up overflow. Lime area. Posted signs |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2018-03-07 | 2018-03-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1339 Marion St. SE - Atlanta | 1 | Fax sent 2018-03-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/8/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-05 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1800 Block of Remer Lane | 299125 | Verbal/Email notification received 2/05/2016-2/08/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-08-02 | 2018-08-02 | Forsyth County (Fowler & Shakerag WRF) | Fulton | Cumming | 6150 Vista Crossing Way - Cumming | 20 | Email sent 2018-08-03 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Pump Station | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 8/3/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken valve on low pressure system | Turned off pump, replaced valve, vac'ed up liquids and limed area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-29 | 2016-02-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 210 | fax received 3/01/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/1/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partially collapsed mainline. | The crew made a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-17 | 2015-11-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1033 Hollywood Road, NW | 1036 | fax received 11/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/17/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-08-21 | 2017-08-21 | Cobb County Water System | Cobb |  | 2570 North Cobb Parkway | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/21/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cobb crew members stoppped the spill. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-01 | 2017-05-01 | Cobb County MS4 | Cobb |  | 1012 Veterans Memorial Highway | 2450 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/1/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clay Branch Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel | The Water System was notified at 3:30 P.M. and the crew stopped the overflow at 5:50. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-27 | 2017-01-27 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | Manhole on the outfall line behind the Cherokee County Aquatic Center 1200 Gresham Mill Parkway Canton | 326760 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 1/27/2017 12:00:00 AM | Coosa |  |  |  | 0 | Little River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole collapsed and caused wastewater to spill from the ground | Construction crews put a temporary manhole in the line and stopped the spill. CCWSA will replace the line and insert a new permanent manhole next week. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-28 | 2018-05-28 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 187 Vine Circle - WWTP Outfall | 5340 | Email sent 2018-05-29 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | WWTP |  | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 5/29/2018 12:00:00 AM |  | 5/28/2018 12:00:00 AM |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tropical depression | Got diesel pump running and stopped spill. Signs posted. Lime applied. Proper agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-10-27 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn |  | 11812 Old Demere Road - 900 gallons, Lift Station 2004 at 440 Pikes Bluff Drive - 1200 gallons, 20 Hampton Point Drive - 1200 gallons, Lift Station 2058 at 230 Saint Annies Lane - 1200 gallons | 4500 | Due to Hurricane Irma collection system crews were not able to properly assess all SSOs as priority was given to conduct repair operations to restore both sewer and water systems to proper operational status. | Raw Sewage | Coastal District | GA0021521 | Collection System | Ditch | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 9/19/2017 1:04:00 PM | Satilla |  |  |  | 1 | Dunbar Creek & Frederica River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Irma | Various repair actions conducted. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-10-27 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-14 | 2017-09-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2626 Memorial Dr. SE | 2210 | Fax received 2017-09-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/15/2017 12:00:00 AM |  | 9/14/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Break in the mainline. | Crew performed a point repair. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2667 Peyton Road, NW | 5 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-10-28 | 2016-10-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill St., NW, Atlanta | 1350 | Fax received on 10/29/2016. | Raw Sewage |  | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 10/29/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the main line. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall | 404-546-8466 | ATLANTA, CITY OF
2018-02-12 | 2018-02-14 | Dawson, City of (Dawson WPCP) |  | Dawson | Hwy 82 and Don Foster Manhole 417 | 8640 |  | Raw Sewage | Wastewater Regulatory Program | GA0021326 |  | Storm Drain, Stream | Stream | Wet weather |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/15/2018 12:00:00 AM | Flint | 2/12/2018 12:00:00 AM |  |  | 1 | Bratley Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4" rainfall on saturated ground | Area cleaned and limed. Creek Monitoring in progress | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-15 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-11 | 2016-02-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1073 Neal Place, NW | 9520 | fax received 2/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/12/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew installed a bypass pump to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-09 | 2018-02-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1428 Rome Dr. NW - ATL | 905 | Fax sent 2018-02-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 2/10/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-19 | 2015-12-19 | Cobb County Water System | Cobb |  | 1307 Pebble Creek Rd. | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rockwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 inch Clay Main | Limed area and stopped overflow | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-09 | 2015-04-09 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 2970 | fax received 4/09/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 4/9/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism, grease, debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-25 | 2017-02-25 | Savannah, City of (President Street WRF) | Chatham | Savannah | Drainage canal behind 8 Millward Rd. | 420 | Initial notification and full report emailed 2/26/17. | Raw Sewage | Coastal District | GA0025348 | Collection System | Canal | Canal | Other |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 2/26/2017 12:00:00 AM | Savannah | 2/25/2017 12:00:00 AM |  |  | 1 | Drainage Canal to Wilmington River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fell on aerial sewer main damaging the pipe. | Removed tree and set up bypass pumps. Sewer main will be replaced. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-02-27 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2017-07-11 | 2017-07-11 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 2535 Mt Zion Parkway, Morrow, GA Manhole - 2217124 | 4770 | Fax received on 07/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Vandalism |  |  | Paul Moisan | Paul Moisan | 7/11/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Reeves Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Debris was removed from the line, and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-07-14 | 0 | 1 | 1 | 0 | 0 | 0
2016-03-28 | 2016-03-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 3600 | fax received 3/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/29/2016 12:00:00 AM |  |  |  |  | 1 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump hose | The crew made a repair to the bypass pump hose to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-30 | 2015-03-30 |  | Gwinnett | Norcross | Manhole upstream from Wolf Creek Pump Station | 1000 | fax received 3/30/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/30/2015 12:00:00 AM |  |  |  |  | 1 | Unknown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bad transformer | Replaced bad transformer |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-10-23 | 2017-10-23 | Cobb County Water System | Cobb |  | 3411 Belleford CT / Johnson Ferry Rd | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/23/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | clean and lime area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-27 | 2015-10-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 747 Lullwater Road, NE | 438 | fax recieved 10/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Roots |  |  | Kim Hembree | Kim Hembree | 10/28/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-09 | 2018-01-09 | Cobb County Water System | Cobb |  | 1644 Sir Galahad Dr./ Hill Rd | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/9/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Darien, City of (Darien WPCP) | McIntosh |  | Fourth Street Lift Station, Darien Georgia | 3000 |  | Raw Sewage | Coastal District | GA0033529 | Lift Station | Ditch | Ditch | Power failure |  | Hailey Harden | Hailey Harden | Hailey Harden | 12/6/2016 12:00:00 AM |  | 12/7/2016 12:00:00 AM |  |  | 0 | Darien River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power failure caused the pump at the lift station to be out of order | The City put out lime | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 2016-12-09 | 1 | 1 | 0 | 0 | 0 | 0
2018-08-09 | 2018-08-09 | Cleveland, City of (Cleveland WPCP) | White |  | Manhole at 1114 Campbell Street, Cleveland | 500 | Untreated wastewater leached into the stream buffer around the manhole. | Raw Sewage | Mountain District - Cartersville | GA0036820 | WWTP | Ground, Storm Drain |  | Wet weather |  | Matthew Stickney | Kathy Lewis | Katie Meade | 8/10/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and waste blocked sewer line. Leak around manhole. Localized storm event and associated flooding/infiltration into system. | Cleared line of debris. Cleaned up overflow area with lime. | 77dbdd3c-0b48-49c2-b623-a78b1b0170cf | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-14 | 1 | 0 | 0 | 0 | 0 | 0
2018-03-03 | 2018-03-03 | Griffin, City of (Potato Creek WPCP) | Lamar | Griffin | 823 Pamela Dr., Griffin GA | 2400 | Notification received on March 6, 2018. | Raw Sewage | Wastewater Regulatory Program | GA0030791 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 3/5/2018 12:00:00 AM |  |  |  |  | 1 | Potato Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The line was cleaned and returned to service the same day. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-10-08 | 2016-10-08 | Savannah, City of (Wilshire WPCP) | Chatham | Savannah | Windsor and Deerfield Drive, Savannah, GA | 135 |  | Raw Sewage | Coastal District | GA0020443 | Collection System | Storm Drain, Stream | Stream | Natural Disaster |  |  | Dagny Pariani |  | 10/9/2016 12:00:00 AM | Ogeechee | 10/8/2016 12:00:00 AM |  |  | 1 | Hoover Creek | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather during Hurricane Matthew contributed to a lift station malfunction which resulted in a manhole overflow. | Turned off upstream lift station which stopped the spill. Corrected malfunction. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2017-12-19 | 0 | 1 | 0 | 0 | 0 | 0
2016-03-01 | 2016-03-02 | Thomaston, City of | Upson | Thomaston | 801 W Gordon St. Upson Regional Hospital | 12150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/2/2016 12:00:00 AM | Flint |  |  |  | 0 | Town Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the major spill is a bypass pump that was setup to reroute the sewage to a downstream manhole, discharge piping (fitting) came apart causing sewage to be discharged onto the ground and the surronding area. | Debris will be removed from the area and the affected area will be disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 4895 Hwy 81, Manhole D1 | 24000 | email notification received 11/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Big Flat Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2017-02-20 | 2017-02-20 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3637 Monmouth Rd - Augusta | 13500 | Manhole #BC130M2328 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 2/21/2017 12:00:00 AM |  | 2/20/2017 12:00:00 AM |  |  | 1 | Tributary to Butler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease, debris and roots. | Line is being monitored and assessed to determine the source of the grease. Will assess the line via CCTV to determine if there is any structural damage. Notifications have been posted. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-13 | 2017-09-13 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Jubilee Lift Station - Social Circle | 200 | Phone notification 2017-09-13. Fax sent 2017-09-14 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Pump Station | Ground | Swale | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/13/2017 12:00:00 AM |  | 9/13/2017 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Problem with generator during power outage from Hurricane Irma. | Pump truck pumped down wet well enough to stop spill. Generator maintenance company repaired generator. Lime applied to spill site. Signs posted. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-24 | 2017-05-24 | Cobb County Water System | Cobb |  | 1700 Water PL SE | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/24/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rotten Wood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Stopped spill and raked and limed area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-26 | 2017-08-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1471 Northeast Expressway, Atlanta | 2420 | Notification received on August 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 8/26/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown blockage | The problem was corrected at 14:00 hours when the first responder crew pressure washed the 8-inch sewer main 220-ft, removed the blockage at 220-ft and restored normal flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-30 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-18 | 2016-05-18 | Cobb County MS4 | Cobb |  | 886 Blackwell Road | 200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/18/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer main causing the manhole to overflow into a tributary of Noonday Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-05 | 2015-01-13 |  | Fulton |  | Azalea Drive/Riverside Road Roswell 30075 | 1845003 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rains caused big creek to overflow the banks and inundate the sewer system along the Chattahoochee River and Big Creek. | Ongoing I/I Reduction Program | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-18 | 2015-09-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1250 Meadow Lane Road, Atlanta | 15750 | Notification received on September 21, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/18/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The problem was corrected at 15:00 hours when the crew pressure washed the 12" sewer main 117ft upstream, removing the blockage and restore regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-25 | 2018-04-25 | Lake Arrowhead WRF | Cherokee |  | Manhole at 229 Lakeview Circle Waleska | 100 |  | Raw Sewage | Mountain District - Cartersville | GAJ030819 | WWRF | Stream |  | Equipment failure |  | Katie Meade | Kathy Lewis | Katie Meade | 4/25/2018 12:00:00 AM | Coosa |  |  |  | 1 | Lake Arrowhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Overload tripped at Narrows Lift Station. This caused the gravity line to fill and over flow at manhole. | Elec breakers reset resuming normal operation of pumps. Area around manhole was cleaned and replaced with new pine straw. Water samples grabbed at spill site, upstream and downstream. Samples taken to lab to analyze for fecal bacteria | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-03 | 1 | 0 | 0 | 0 | 0 | 0
2016-01-03 | 2016-01-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 4154000 | CTS No. 78706. Verbal notification received 1/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/4/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | A plug that prevents flow from entering the creek has been washed away. A replacement plug has been ordered. Bypass pumps have been installed to divert flow into another section of pipe, but some flow is still escaping to the stream | Spill is ongoing | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-28 | 2017-06-28 | Savannah, City of (Crossroads WPCP) | Chatham | Savannah | 62 Highlands Blvd., Savannah, GA | 5700 | Initial notification and full report received 6/28/17. | Raw Sewage | Coastal District | GA0038326 | Force Main | Storm Drain, Stream | Stream | Pipe failure |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 6/28/2017 3:45:00 PM | Savannah | 6/28/2017 12:00:00 AM |  |  | 1 | St. Augustine Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A portion of PVC force main split causing the sewage spill. | Stopped Lift Stations feeding the force main in order to stop spill. Replaced the damaged PVC portion of the force main with ductile iron. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-06-30 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SAVANNAH | 912-658-6973
2015-02-18 | 2015-02-18 | Cobb County MS4 | Cobb |  | 4549 Woodlawn Lakes Dr. | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/18/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Clay Main | The spill was stopped at 21:15 hours | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-02-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | Intersection Lakemont Drive and Brookwood Drive | 2160 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWRF | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/26/2015 12:00:00 AM | Coosa |  |  |  | 0 | Tar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration of stormwater from heavy rains | Vacuum trucks were used to mitigate the spill | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | David Oxford | 706-529-1010 | Dalton Utiilites
2016-10-11 | 2016-10-11 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn | St. Simons Island | St. Andrews, St. Simons Island. | 500 |  | Raw Sewage | Coastal District | GA0021521 | Force Main | Ditch | Ditch | Debris |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 10/13/2016 9:00:00 AM | Satilla | 10/27/2016 12:00:00 AM | 2016-10-27 |  | 1 | Island Club Pond | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Main line blocked due to wash out of a manhole structure during Hurricane Matthew. | Cleared main line blockage and used vaccon truck to clean spill from road and right of way. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-10-31 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-12 | 2017-01-12 | Gwinnett County (Yellow River WPCP) | Gwinnett | Liliburn | Manhole behind 100 Woodcliff Drive - Liliburn | 9488 | Fax received 2017-01-13 | Raw Sewage |  | GA0047911 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Hsin Yeh | 1/12/2017 12:00:00 AM |  | 1/12/2017 12:00:00 AM |  |  | 1 | Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper and other products. Secondary cause - grease. | Raked are and spread lime. Placed signs at spill and waterway. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-26 | 2015-08-26 | Cobb County MS4 | Cobb |  | 240 Pine Valley Road | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/26/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of roots in sewer main causingthe manhole to overflow into a tributary of Sope Creek. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-09-10 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-06 | 2016-06-06 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 700 Block of Gil Harbin Blvd | 425 | Voicemail notification received 6/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 6/6/2016 12:00:00 AM |  |  |  |  | 1 | Dukes Bay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage from debris | Debris removed | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2017-04-06 | 2017-04-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1182 Oakland Ln. SW - ATL | 1155 | Fax received 2017-04-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/7/2017 12:00:00 AM |  | 4/6/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-12 | 2016-05-12 | Tifton, City of (New River WPCP) | Tift | Tifton | 125' West of 278 GA 125 Hwy. S, Tifton, GA, Tift County Animal Shelter | 1500 | Email recieved on 05/12/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System |  | Shoreline | Rags |  |  | Paul Moisan | Paul Moisan | 5/12/2016 12:00:00 AM |  | 5/12/2016 12:00:00 AM |  |  | 1 | Unnamed tributary of the New River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred at a manhole adjacent to the Tift County Animal Shelter. The cause of the spill was due to a blockage of nyla bones, pet hair, and rags. | Once the blockage was cleared, hydrated lime was spread to mitigate and sanitize the affected area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-13 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-25 |  |  | DeKalb |  | 4664 Flat Bridge Road | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Cairo, City of (Cairo WPCP) | Grady | Cairo | City of Cairo WWTP | 60000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Hydraulic Overload |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/21/2017 12:00:00 AM | Ochlockonee |  |  |  | 0 | Parkers Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic Overload due to heavy rainfall |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 65000 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/4/2018 5:22:00 PM | Ocmulgee | 2/4/2018 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Rain event | Wait until rain has stopped |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-07 | 2017-07-07 | Ellijay WPCP | Gilmer |  | 64 Merk Davis Drive | 5000 |  | Raw Sewage | Mountain District - Cartersville | GA0021369 | WWTP | Stream |  | Operator error |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 7/10/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed tributary to Coosawattee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Digester #1 was overflowed due to operator error during the wasting process | Overflow clean up began immediately after EPD came on site to inspect the overflow. New procedures to be implemented by operators during wasting process to prevent future occurrence. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-20 | 2015-03-20 | Cobb County MS4 | Cobb |  | 2401 Deerfield Dr. | 140 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Gravel in 8" Concrete Main | Cleaned and Limed Area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-09 | 2016-11-09 | Warrenton, City of (South Pond WPCP) | Warren | Warrenton |  | 10000 |  | Primary/Secondary Effluent | Northeast District - Augusta | GA0032786 | WWTP | Other |  | Wet weather |  | Madara Tyler | Madara Tyler | Madara Tyler | 12/15/2016 12:00:00 AM | Ogeechee | 11/16/2016 12:00:00 AM | 2016-12-15 | 2017-12-15 | 1 | Goldens Creek | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 |  | 0 | South BOD 5over 1.5 |  | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 7ef9249c-79fc-4e5a-9b9b-770306e1436a | 2016-12-19 | 0 | 1 | 1 | 0 | 0 | 0
2017-04-24 | 2017-04-24 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn |  | Fountain Lake Apartments | 500 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Ditch | Ditch | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/25/2017 2:00:00 PM | Satilla | 7/24/2017 12:00:00 AM |  |  | 1 | Fountain Lake Pond | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken gravity sewer main. | Gravity sewer main was repaired. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2017-07-25 | 1 | 1 | 0 | 0 | 0 | 0
2015-01-04 | 2016-01-04 | Cobb County MS4 | Cobb |  | 2718 Long Lake Dr. | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in 8 inch PVC Main |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-06 | 2016-05-06 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 13 Beech Haven Dr., Athens | 4036 | Initial email 5/6, full report faxed 5/10 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 5/6/2016 12:00:00 AM | Oconee | 5/6/2016 12:00:00 AM |  |  | 1 | unnamed tributary to Middle Oconee | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A t-shirt and rags clogged the sewer line | Hand rodded the line to remove the clog. Limed area. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-05-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2018-02-27 | 2018-02-27 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 5531 Roswell Road Sandy Springs, 30342 | 1290 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/27/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-03-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-29 | 2018-04-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2366 Dellwood Dr. NW - Atlanta | 50 | Spill originally reported as creek spill on 2018-04-30. Update sent 2018-05-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Andrea Kemberling | Alys Hannum | 5/2/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 49e1c9c4-eb6e-11e0-b8d8-000c29971acc | 2018-05-03 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-16 | 2016-09-16 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | Belvoir Heights, Athens | 0 | Monthly email of dry land overflows and backups into structures received 10/3/16. | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Ground |  | Unknown |  |  | Dagny Pariani | Dagny Pariani | 10/3/2016 12:00:00 AM | Oconee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown amount of sewage spilled to dry land. |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3495
2016-01-25 | 2016-01-25 | Americus, City of (Mill Creek WPCP) | Sumter | Americus | Manhole located approximately 370 feet from the creek. Americus, GA Same location as December 2015. | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0047767 | Collection System | Stream |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/25/2016 12:00:00 AM |  | 1/26/2016 12:00:00 AM | 2016-01-25 |  | 1 | Willets Brook | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | A result of a blockage in a 12" gravity sewer line. | A high pressure rodding machine was brought in to clear the line. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-02-10 | 0 | 1 | 0 | 1 | 1 | 0
2018-06-20 | 2018-06-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1581 Huber St. NW - Atlanta | 800 | Fax sent 2018-06-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 6/21/2018 12:00:00 AM |  | 6/20/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-21 | 2015-10-21 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1060 Scott Street | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/1/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Ragging in Sag | Repair Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-23 | 2016-08-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3175 Halhaway Court, Chamblee | 3000 | Notification received on August 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 8/23/2016 12:00:00 AM |  |  |  |  | 0 | Peachtree Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek Crossing | The spill was contained at 14:15 hours when a repair crew completed the pont repair, whicn then restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-29 | 0 | 1 | 0 | 0 | 0 | 0
2015-03-26 | 2015-03-26 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Intersection of Bridgewater Way & Bridgewater Circle, Brunswick | 3750 |  | Raw Sewage | Coastal District | GA0025313 | Collection System | Reservoir | Reservoir | Grease |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 3/27/2015 9:00:00 AM | Satilla | 3/26/2015 12:00:00 AM |  |  | 1 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | Blockage was removed. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-03-27 | 1 | 1 | 0 | 0 | 0 | 0
2015-11-19 | 2015-11-19 | Columbus Water Works (South WRF) | Muscogee | Columbus | 5901 Gateway Drive. | 2616 | Fax received on November 20, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Bull Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains a lift station was overwhelmed with grit and debris. The basin is Bull Creek Basin. | Once Columbus Water Works pumped out the grit and cleared the debris, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-23 | 0 | 0 | 0 | 0 | 0 | 1
2017-02-07 | 2017-02-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 199 Palatka St. SE - ATL | 950 | Fax received 2017-02-08 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Paul Moisan | 2/8/2017 12:00:00 AM |  | 2/7/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-20 | 2016-02-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2833 Glenlocke Circle, NW | 7287 | fax received 2/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/21/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-08 | 2018-05-08 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 600 Guy Paine Road MH ID 52673 | 3600 |  | Raw Sewage | Wastewater Regulatory Program | GA0024538 | Collection System | Stream | Stream | Rags |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/9/2018 12:00:00 AM | Flint |  |  |  | 0 | Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rags | Debris has been removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 275 Riverhill Dr., Athens | 7210 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 1/5/2016 12:00:00 AM | Oconee | 12/30/2015 12:00:00 AM |  |  | 1 | Middle Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowed during flood event | Cleaned area. Sewer upgrade under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Govenment of Athens-Clarke County | 706-613-3481
2018-08-02 | 2018-08-23 | Cave Spring, City of (Cave Spring WPCP) | Floyd |  | Little Cedar flowing through the middle of town en route to Big Cedar | 9600 |  | Raw Sewage | Mountain District - Cartersville | GA0025721 | WWTP | Stream |  | Wet weather |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 8/6/2018 12:00:00 AM | Coosa |  |  |  | 1 | Little Cedar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Greater than 8 inches of rain |  | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-08-23 | 1 | 0 | 0 | 0 | 0 | 0
2015-10-07 | 2015-10-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 3528 Pin Oak Circle, Doraville. | 4900 | Notification received on October 8, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/7/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 14:00 hours, when a crew built a 4x12 berm to contain the sewer spill, replace 14ft of the 8" sewer main and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-10-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-07 | 2018-02-07 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 4437 Wesleyan pointe Decatur GA 30034 | 60750 | Found evidence of spill | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/7/2018 7:38:00 PM | Ocmulgee |  |  |  | 1 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | storm event | Upon arrival was not spilling |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-26 | 2017-12-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 389 Collier Ridge Dr. NW - ATL | 1030 | Fax sent 2017-12-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 12/26/2017 12:00:00 AM |  | 12/26/2017 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-25 | 2018-04-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 901 Mercury Dr. NW - Atlanta | 100 | "This is not a city problem." Fax sent 2018-04-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  |  | Alys Hannum | Alys Hannum | 4/26/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | "This is not a city problem." | "This is not a city problem." |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-01 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-21 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Sylvia Dr. and Rockhouse Rd. | 150000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/21/2017 12:00:00 AM | Suwannee |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet Weather |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 907 Rose Circle, SW | 12500 | fax received 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-16 | 2015-01-16 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 6817 Maddox Rd. | 1600 | REC FAX 1/17/2015. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Vandalism |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/17/2015 12:00:00 AM | Ocmulgee | 1/17/2015 12:00:00 AM |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism. | Cleared blockage. Cleared and removed debris from overflowing manhole, cleaned gravity main, restored flow back to normal capacity. Manhole lid will be locked down and re-clean gravity main and televise. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-20 | 0 | 1 | 1 | 0 | 0 | 0 | [8 empty] | CLAYTON COUNTY WATER AUTHORITY | 678.422.2834
2016-01-28 | 2016-01-28 | Wildwood Ridge | Cobb |  | Wildwood Ridge Apartments | 1000 | EECO EPD-WQ-8050 executed on March 30, 2016 | Raw Sewage | Mountain District - Cartersville |  | N/A | Stream |  | Wet weather |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 1/28/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Caused by intense rain events over a series of days resulted in fallen trees along a steep embankment where an undergroudn sewer line was located, which in turn caused a break in the sewer line | Septic Express repaired the leak | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-02-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-03 | 2015-05-04 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1350 Tower Hill Street, NW | 4730 | verbal notification from the City received 5/04/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/4/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-08 | 2017-01-08 | Cobb County Water System | Cobb |  | 777 Townpark Lane | 920 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/8/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease causing it to overflow into a tributary of Noonday Creek. | The crew stopped the overflow at 10:50 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-18 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-14 | 2018-06-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1027 McConnel Drive Decatur GA 30033 | 940 | found evidence of SSO | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/15/2018 7:20:00 AM | Ocmulgee |  |  |  | 1 | South Fork Peachtree Creek & unnamed tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root blockage | Rodded |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-07 | 2015-05-07 |  | Fulton |  | 595 Glenforest Road Sandy Springs 30328 | 3150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/7/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary of Long Island Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The manhole has been cleanded. The area implacted by the spill is in the process of being cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-05-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-12 | 2015-09-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 253 Patterson Avenue, SE | 25 | fax received 8/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 9/13/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfunction |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-09 | 2015-12-09 | Cobb County MS4 | Cobb |  | 4175 Nance Rd. | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/10/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8 " PVC Main | Cleaned spill area, spread enzymes and lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-12-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-23 | 2017-08-23 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | 4277 Windward Lane - Norcross | 2261 | Fax received 2017-08-23 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/24/2017 12:00:00 AM |  | 8/23/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Beaver Ruin Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - Wipes, paper, and other products | Raked area and spread lime, placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-14 | 2016-11-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 219 Broadland Rd., NW, ATL | 10 | Fax received on 11/15/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/15/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | Steps were taken to prevent reoccurence. Placed on periodic inspection schedule. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-04 | 2015-09-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill Street, NW | 1328 | fax received 9/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/4/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-08 | 2015-03-08 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | This is an outfall spill. Reported TSS = 63 mg/l; Reported volume = ~35,000,000 gallons | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/8/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | The facility experienced a failure of the TWAS centrifuges and the facility was unable to remove sufficient solids from the waste stream. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-26 | 2015-12-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 1440 Sowell Estate, Stone Mountain | 1480 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/26/2015 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:20 hours, when a crew rodded the 8" sewer main 15ft, clearing the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2016-01-25 |  | Henry |  | 678 Fairhaven Blvd. | 45000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/25/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Reeves Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration from 7.6 inches of rain in the past 5 days. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Eatonton - Putnam Water & Sewer Authority (Westside WPCP) | Putnam | Eatonton | Westside WPCP | 120000 |  | Raw Sewage | Wastewater Regulatory Program | GA0032263 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/4/2017 12:00:00 AM |  |  |  |  | 0 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wet weather | Corrective action has been taken, grounds cleaned up, signs posted at affected waterways, stream monitoring in affect. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-12 | 2015-10-12 | Cobb County MS4 | Cobb |  | 102 Ridge Court | 70 |  | Raw Sewage | Mountain District - Cartersville |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 |  | Columbus Water Works (South WRF) | Muscogee | Columbus | 1833 Slade Dr./Cherokee Ave., Columbus, GA | 41857 | Fax received 12/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/24/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rainfall and hydraulic loading, a manhole overflowed into Weracoba Creek. | Once the rainfall subsided, flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-28 | 2015-09-28 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 10/14/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused the effluent TSS to reach as high as 27.0 mg/L on 09/28/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Cobb County Water System | Cobb |  | 1855 Hurt Rd. | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" PVC Main | The crew stoppedthe spill at 15:40 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-24 | 2015-10-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2721 Hedgewood Drive, NW | 3600 | fax received 10/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 10/25/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the pill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-27 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-12 | 2015-03-12 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 4400 Danforth Road, SW | 400 | fax received 3/16/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/17/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-02 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6790 Browns Mill Lake Road, Lithonia | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Rodded manhole 63ft to remove blockage, pressure wahsed main and restored flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-20 | 2015-07-20 | Cobb County MS4 | Cobb |  | 3010 Woodland Drive | 360 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a reslut of roots in sewer main causing the manhole to overflow into a tributary of Butler Creek. | The crew stopped the overflow at 2:20 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-20 | 2015-07-20 | Cobb County MS4 | Cobb |  | 3010 Woodland Drive | 360 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/20/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a reslut of roots in sewer main causing the manhole to overflow into a tributary of Butler Creek. | The crew stopped the overflow at 2:20 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-01 | 2018-02-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1428 Rome Dr. NW - ATL | 264 | Fax sent 2018-02-02 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 2/2/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew set up a by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-31 | 2017-01-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 953 Woodland Ave SE - ATL | 276 | Fax received on 02/01/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 2/1/2017 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-06 |  |  | DeKalb |  | 4948 Ardsley Drive | 2400 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 455 State Hwy. 138, Jonesboro Manhole 2215693 | 10500 | Fax received on 01/23/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/23/2017 12:00:00 AM | Flint |  | 2017-01-24 |  | 1 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | The cause of the spill was capacity (lack of). | Multiple lines and manholes will be inspected for the source of inflow. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0 | Billy Vondenbosch |  | CLAYTON COUNTY WATER AUTHORITY
2017-12-04 | 2017-12-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2530 Barge Rd. SW - ATL | 30 | Email sent 2017-12-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 12/5/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | 121 G Circle | 1000 | The spill was containedand did not appear to have reached surface water. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/11/2016 12:00:00 AM | Ogeechee |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-17 | 2016-10-17 | Cobb County Water System | Cobb |  | 1940 County Services Pkwy | 100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/17/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-27 | 2018-02-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1215 Church Street, Decatur GA 30030 | 25 |  | Raw Sewage |  | GA0024147 | Collection System |  |  | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/27/2018 5:38:00 PM | Ocmulgee | 2/27/2018 12:00:00 AM |  |  | 1 | South Fork Peachtree Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | cleaned out blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-01 | 0 | 1 | 0 | 0 | 0 | 0
2018-04-23 | 2018-04-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WWTP | 16460000 | Phone call received 2018-04-24, TSS - 174 mg/L. This spill is also entered as a violation. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream |  | Hydraulic Overload |  | Alys Hannum | Alys Hannum | Alys Hannum | 4/24/2018 12:00:00 AM |  |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | From 6:00 AM to 10:30 AM April 23rd, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River due to hydraulic overload. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-09 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-13 | McRae-Helena, City of (McRae-Helena WPCP) | Telfair | McRae-Helena | Long Bridge Road Lift Station in McRae-Helena | 250 | Spill was small but could have run through a ditch into the Little Ocmulgee River. | Raw Sewage | Southwest District | GA0048674 | Lift Station | Ground, Stream |  | Natural Disaster |  | Jay Howell | Jenna Detar | Jenna Detar | 9/11/2017 11:00:00 AM | Ocmulgee |  |  |  | 1 | Little Ocmulgee River | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | Power outage due to Hurricane Irma. | Area was cleaned and lime liberally applied. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | c55a0890-1b00-4f2f-a100-212b30005169 | 2017-10-05 | 1 | 0 | 0 | 0 | 0 | 0
2017-04-27 | 2017-04-27 | Fulton County MS4 | Fulton | Johns Creek | 5100 Old Alabama Road | 4320 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-03 | 2017-11-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2140 Martin Luther King Dr. SW - ATL | 30 | Fax sent 2017-11-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 11/4/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Self-contained |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-19 | 2017-06-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood | 6000 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/20/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Utility water line leaking | The problem was corrected at 18:45 hours when the WQC Supervisor turned off the valve to the 2" water line and stopped the leakage. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-02 | 2015-12-02 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 5651 Brook Hollow Parkway | 23400 | fax received 12/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/3/2015 12:00:00 AM |  |  | 2015-12-03 | 2016-12-27 | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 |  | Flushed the main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 1 | 1 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-04 | 2015-01-04 |  | Stephens | Toccoa | Ward Creek Liftstation located on Fernside Drive, Toccoa, Georgia | 6500 | Spill report received on January 5, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/5/2015 12:00:00 AM |  |  |  |  | 0 | Ward Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rain cause of the overflow. | In an effort to minimize the overflow, City personnel went over right away to utilize the vacuum truck to manually transport wastewater from the lift station to the Eastanollee Creek Wastewater Treatment Plant. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-23 | 2016-05-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 6028 Hwy. 42, Rex MH 2207766 | 450 | Fax received on 05/24/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 5/24/2016 12:00:00 AM |  |  |  |  | 1 | Tar Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage was cleared. | Line will be televised, and the root cut if a problem is located, it will be repaired. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-23 | 2015-09-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 211 Hemphill School Road, NW | 1260 | fax received 9/24/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 9/24/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-10 | 2016-03-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 400 Fairburn Road, SW | 5000 | fax received 3/11/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Vandalism |  |  | Kim Hembree | Kim Hembree | 3/11/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-26 | 2018-06-26 |  | Muscogee | Columbus | 3001 South Lumpkin Road | 45360 |  | Raw Sewage | Wastewater Regulatory Program |  | Force Main | Stream |  | Equipment failure |  |  | Juan Robles | Juan Robles | 6/26/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | SOUTH COLUMBUS CREEK BASIN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A contractor was repairing a force main when the plug that was installed failed. There was a pump around already installed to bypass the section of main being repair. | Once discovered that the plug failed, the pump was moved to a manhole further down thus eliminating that section of the main. Once the pump around was relocated the overflow stopped. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-29 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-10 | 2017-10-10 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 9812 Ivey Ridge Circle, Jonesboro Manhole 2268369 | 2400 | Fax received on 10/11/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/11/2017 12:00:00 AM | Flint |  |  |  | 1 | Swamp Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pipe was cleaned and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-12 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | Clayton Co Water Authority
2018-01-30 | 2018-01-30 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Influent Lift Station | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/30/2018 12:00:00 AM |  |  |  |  | 1 | Hat Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-31 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-26 | 2015-12-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 2886000 | Verbal notification received 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain event |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-09-13 | 2017-09-13 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Rest Area 52 Lift Station - Social Circle | 250 | Phone notification 2017-09-13. Fax sent 2017-09-14 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Pump Station | Ground | Swale | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/13/2017 12:00:00 AM |  | 9/13/2017 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical problem in panel box while operating on generator power. | Changed alternator switch. Pumps started working and spill stopped. Lime applied to spill site, signs posted. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-05 | Dallas North WPCP | Paulding |  | Saddle Brooke | 45000 | They cleaned and limed the entire area affected by spill | Raw Sewage | Mountain District - Cartersville | GA0026034 | WWTP | Stream |  | Pipe failure |  | Cindy Nix | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Coosa |  |  |  | 0 | Lawrence Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed pipe with in the gravity sewer line of trunk line to sewer plant | By pass pumping initiated with in 6 hours of first report of the spill. City workforce have begun repair of the sewer main. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | Kendall Smith | 770-443-8117 | City of Dallas - North WPCP
2015-04-24 | 2015-04-24 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3901 Campbellton Road, SW | 558 | fax received 4/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/25/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-04 | 2016-02-04 |  | Lowndes | Hahira | Manholes at the corner of W. Sargent and S. Newsome St, and 213 N. Nelson St | 3000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  |  | Dagny Pariani |  | 2/4/2016 12:00:00 AM | Suwannee |  |  |  | 1 | tributary to Franks Creek and Hodges Pond | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall, I and I, and local flooding | Pump stations running full time to move flow. City has a 5-year plan to correct I and I problems |  |  | 89352e56-9649-4d50-9761-577155a9c85b | 2016-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-05 | 2017-01-05 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3263 Rockmill Drive, Ellenwood | 1700 | Notification received on January 6, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/5/2017 12:00:00 AM |  |  |  |  | 0 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 10:15 hours, when a crew pressure washed the 8" sewer main 133ft between manholes, clearing the grease blockage at 100ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-19 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-29 | 2017-09-29 | LaGrange, City of (Long Cane Creek WPCP) | Troup | LaGrange | East Industrial Lift Station. | 4500 | Fax received on 09/29/2017. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Stream | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 9/29/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Long Cane Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partial piping separation at a tee in the lift station valve vault between pumps and the force main. Wastewater escaped from the piping system into the valve vault and overflowed from the vault. Cause of the piping failure is under investigation and being repaired at this time. Wet well is presently being pumped out using a vacuum truck while repair is being made. | Two vacuum trucks worked in series to keep the wet well pumped down as maintenance makes the necessary repairs in the valve vault. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-29 | 0 | 1 | 0 | 0 | 0 | 0 | Jim Russell | 706-883-2118 | LaGrange (City of)
2017-12-29 |  | Cumming, City of (Bethelview Road WPCP) |  | Cumming | 433 Canton Hwy - Cumming | 1000 | Voicemail left 2017-12-29. Letter sent 2018-01-02 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream | Stream | Rags |  | Alys Hannum | Alys Hannum |  | 1/29/2018 12:00:00 AM |  | 12/29/2017 12:00:00 AM |  |  | 1 | Trib. to Kelly Mill Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and wipes | Jetted the line and cleared the area, applied lime to the affected area, posted signage | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-26 | 2016-01-26 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 5180 Peachtree Industrial Blvd | 9862 | fax received 1/27/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/26/2016 12:00:00 AM |  |  |  |  | 1 | Hopkins Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Flushed main to restore flow |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-04-07 | 2015-04-07 |  | DeKalb | Stone Mountain | 949 Dunstan Lane, Stone Mountain | 50 | Notification received on April 15, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Hsin Yeh | 4/7/2015 12:00:00 AM |  |  |  |  | 0 | Tributary to Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A unknown reason caused a manhole overflowing | The problem was corrected at 9:30 hours when a crew pressure washed the 8" sewer main 50ft, cleared the blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-02 | 2016-04-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 800 Block of Gornto Road | 860 | Email notification received 4/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/4/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA | 229-251-6528
2017-03-05 | 2017-03-05 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 1683 Hillview Ave, Jonesboro | 7200 | Fax received on 03/06/2017 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 3/6/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Brow Rock Bottom Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was roots in the line. | Line cleared, and flow returned to normal. This section will be televised. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-14 | 0 | 1 | 1 | 0 | 0 | 0
2018-08-19 | 2018-08-19 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1814 Peachtree St. NW - Atlanta | 2770 | Email sent 2018-08-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 8/20/2018 12:00:00 AM |  | 8/19/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew used a by-pass pump |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-11 | 2015-11-11 |  | Upson | Ashburn |  | 95000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/19/2015 12:00:00 AM | Flint |  |  |  | 0 | Ashburn Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by 3.1 inches of rain and I and I. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-11-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-11 | 2016-04-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2449 East Club Drive, Brookhaven | 4160 | Notification received on April 14, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/11/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | The problem was corrected at 10:34 hours, when a crew rodded the overflowing manhole 96ft, cleared the blockage ant 33ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-04-14 | 0 | 1 | 0 | 0 | 0 | 0
2017-08-01 | 2017-08-01 | Henry County Water Authority (Indian Creek WRF) | Henry | Locust Grove | Frog Road | 35000 | Dryland Spill | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/1/2017 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rrepair was made on the ductile iron force main utilizing two solid sleeves and the line was put back into service at approximately 1:00 am on August 2, 2017. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-23 | 2017-05-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4023 Smithfield Trail, Ellenwood | 4520 | Notification received on May 26, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/23/2017 12:00:00 AM |  |  |  |  | 0 | Crawford Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 09:03 hours when the crew pressure washed the 8" line between manholes 300 ft., cleared the blockage, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-02-01 | 2015-02-01 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3484 Fairburn Place, NW | 1480 | fax received 2/02/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 2/2/2015 12:00:00 AM |  |  |  |  | 1 | Sandy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-06 | 2017-01-06 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 834 Fleming Avenue - Augusta | 3900 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 1/8/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Rae's Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the sewer gravity main. | Sewer gravity main was jet-washed to clear the blockage. Will clean the sewer gravity main and CCTV to determine the source. Gravel in the customer's driveway was removed and will be replaced. Street gutter and storm line were cleaned. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-26 |  |  | DeKalb |  | 3759 Salem Meadows Drive | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-26 | 2018-08-26 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Cumming | 6190 Parkway North Drive | 5 | Email sent 2018-08-26 UPDATE email sent 8-28 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Collection System | Ground |  | Debris |  |  | Alys Hannum |  | 8/26/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in lateral | Jetted sewer lateral, cleaned up solids, spread lime, notification sent. |  |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-27 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-04 | 2018-06-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 750 Selig Dr. SW - Atlanta | 6000 | Fax sent 2018-06-05 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 6/5/2018 12:00:00 AM |  | 6/4/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unspecified | Line is bypassed for containment. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-18 | 2016-12-18 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forrest Park | 928 Shield Crest Way, Forest Park Manhole 2204650 | 3750 | Email and fax received on 12/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 12/19/2016 12:00:00 AM |  |  |  |  | 1 | Conley Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage from roots was located on a gravity main within the City of Atlanta collection system (spill occurred on Clayton County side). | Clayton County cleared the blockage, and contacted the City of Atlanta in regards to reporting the spill and performing maintenance on their gravity main. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-19 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2018-02-09 | 2018-02-09 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Doraville | 5217 Fleur De Lis Court, Doraville GA 30360 | 2320 | manhole 6-307-s047 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Roots |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/10/2018 6:37:00 PM | Ocmulgee | 2/9/2018 12:00:00 AM |  |  | 1 | Northeast Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root blockage | Rodded sewer main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-12 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Creekside Subdivision. | 1500 | Fax received on 04/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/1/2016 12:00:00 AM | Chattahoochee | 4/1/2016 12:00:00 AM |  |  | 1 | Dixie Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rains, I/I. | Overflow stopped by parking City vehicles on overflowing manhole covers. Will be installing bolt-down covers (which have been ordered but not yet arrived) at spill location and continuing to seek out and correct I/I sources. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-04 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-02 | 2015-04-02 | Cobb County MS4 | Cobb |  | 2000 East West Connector Presbyterian Village Senior Home | 480 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/2/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 8" Clay Main | Cleaned area and Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-17 | Cobb County MS4 | Cobb |  | 3171Burnt Hickory Road | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This oveflow occurred as a result of roots causing it to overflow into Mud Creek. | The Water System was notified at 3:15 p.m. and our crew stopped the overflow at 3:30 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | Stephen McCullers | 770-419-6225 | 680 South Cobb Dr.
2017-09-11 | 2017-09-11 | Thomaston, City of | Upson | Thomaston | Hwy 74 Lift Station | 7620 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Power failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/11/2017 12:00:00 AM | Flint | 9/11/2017 12:00:00 AM |  |  | 0 | Potato Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power Failure | The power was restored and sewage release was stopped. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-14 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Brian Kelly |  | WSG Operations
2016-03-17 | 2016-03-17 | Cobb County Water System | Cobb |  | 1000 Williams Drive | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 3/8/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a reslut of debris in sewer main causing the manhole to overflow into a tributary of Noonday Creek. | The Water System was notified at 4:41 p.m. and the crew stopped the overflow at 6:25p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-05 | 2015-03-05 | City of Fort Oglethorpe | Catoosa |  | Manhole at the end of Vero Beach adjacent to Chattanooga Spring Creek Pump Station | 2500 |  | Raw Sewage | Mountain District - Cartersville |  | Pump Station | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 3/5/2015 12:00:00 AM | Tennessee |  |  |  | 0 | Spring Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The area received around one inch of rainfall causing flooding | Looking for source of inflow and/or infilration | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-04-01 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-14 | 2016-12-14 | Winder, City of (Marburg Creek WPCP) | Barrow | Winder | Intersection of Capitol Avenue and Tuggle Street. | 225 |  | Raw Sewage | Wastewater Regulatory Program | GA0023191 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Hsin Yeh | 12/14/2016 12:00:00 AM |  | 12/14/2016 12:00:00 AM |  |  | 1 | Mulberry River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the line caused by grease buildup. | Spread lime, added the location to the preventative maintenance schedule. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-13 | 2015-04-13 |  | DeKalb | Lithonia | 1001 Cloffside Run, Lithonia | 2720 | Notification received on April 14, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/13/2015 12:00:00 AM |  |  |  |  | 0 | North Crooked Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 12:53 hours when a crew pressure washed the 8" sewer main 380ft upstream, cleared the grease blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-04-15 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Polo Golf & Country Club WPCP | Forsyth |  | Polo Golf and Country Club, on Golf Course in the rough next to Tee #2 | 150000 |  | Raw Sewage | Mountain District - Cartersville | GAJ030950 | WWTP | Stream |  | Wet weather |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 1/7/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Cheatham Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy impact of rainfall with unbefore seen inflow/infiltration. Unusual velocity change to wet well floats caused malfunction |  | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | Mark Rasmussen | 678-513-5022 | Big Creek Utility | 6400 Polo Club Dr, Cumming, Georgia, 30040
2015-01-06 | 2015-01-06 |  | DeKalb | Lithonia | 5348 Timor Trail, Lithonia | 1620 | Notification received on January 7, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/6/2015 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:09 hours when a crew pressure washed the 8" sewer main 186ft upstream, and restores regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-01-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-20 | 2018-08-20 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Manhole approx. 100 feet south of Oglethorpe Blvd. bridge (cross street College Drive). | 29700 |  | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Other | Shoreline | Wet weather |  |  | Juan Robles | Juan Robles | 8/21/2018 12:00:00 AM | Flint | 8/21/2018 12:00:00 AM | 2018-08-21 |  | 0 | Flint River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Heavy rain of 0.51" in 15 minutes according to USGS river gage. | Bypass pump was started and overflow was stopped. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-09-06 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-30 | 2016-09-30 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 433 Canton Road | 600 | verbal notification received 9/30/2016 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/30/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Big Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage from grease and paper products | Jetted line, cleaned area. Signage posted. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-30 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF CUMMING
2015-11-28 | 2015-11-28 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 235 Colonial Drive Woodstock | 23625 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 11/30/2015 12:00:00 AM | Coosa |  |  |  | 1 | Unnamed tributary to Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blocked the sewer line and caused wastewater to back up and overflow from a manhole. | CCWSA Construction Crews jetted the line and removed the debris | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | Nate Giddens | 678-313-1947 | Cherokee Co Water & Sewage
2017-01-04 | 2017-01-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 214 John Wesley Dobbs Ave., NE, ATL | 352 | Fax received on 01/05/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/5/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | Marshall Hall |  | ATLANTA, CITY OF
2017-04-06 | 2017-04-06 | Douglas, City of (Southeast WPCP) | Coffee | Douglas | From a manhole inside the Southeast WPCP located on 622 Iron Road. | 7000 |  | Raw Sewage | Coastal District | GA0024431 | Collection System | Ground, Storm Drain, Stream | Stream | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 4/6/2017 10:00:00 AM | Satilla | 4/6/2017 12:00:00 AM |  |  | 1 | Un-named tributary of the Seventeen Mile River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to localized flooding from heavy rain events. |  | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-03-12 | 1 | 1 | 0 | 0 | 0 | 1
2016-11-12 | 2016-11-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill St., NW, Atlanta | 1600 | Fax received on 11/13/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 11/13/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 700 Block of Jane Street and Ann Street | 15250 | Verbal/Email notification received 2/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-02-19 |  |  | DeKalb |  | 550 Houston Mill Road | 0 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rodded sewer main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-26 | 2017-09-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2372 Armand Rd. NE - ATL | 3555 | Fax sent 2017-09-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 9/27/2017 12:00:00 AM |  | 9/26/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-16 | 2015-01-16 |  | Richmond | Augusta | 3627 Bermuda Circle | 137 | fax received 1/17/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/17/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The line was opened and resumed normal flow. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2016-09-16 | 2016-09-16 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lilburn | 909 Indian Lake Drive | 2057 | fax received 9/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/16/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Jackson Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-01-22 | 2017-01-23 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1820 Doug Barnard Pkwy - Augusta | 57120 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/23/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The augusta area received 3.5 inches of rainfall beginning on January 21, 2017 and ending on the morning of January 23, 2017. Heavy rainfall caused flows in the WCTS to exceed the pumping capacity of the treatment facility. | Begun monitoring Butler Creek as required. Augusta has previously identified projects that are needed in order to remove significant amounts of rainwater from the wastewater collection system. These projects are in various stages of design and implementation. Augusta has begun the process of increasing the peak pumping capacity of the treatment facility to further mitigate. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 2200 Block of Park Lane | 7360 | Verbal notification received 10/11/2016. Email follow up received 10/12/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 10/11/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe separation due to excessive erosion caused by Hurricane Matthew. | Pipe plugged and bypassed until repair can be made. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-01-04 | 2018-01-19 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3643 Glenwood Road, Decatur GA 30032 | 1319400 | Notified of SSO on January 19, 2018. Source tracking began on January 4, 2018 but was delayed due to snow and ice. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Equipment failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/19/2018 8:17:00 PM | Ocmulgee |  |  |  | 1 | Shoal Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Broken main. Manhole 15-168-s031 spilling into creek. | Bermed up area to contain spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-22 | 0 | 1 | 0 | 0 | 0 | 0 | Earnest Veal |  | Dekalb Co Dept. Watershed Management
2017-12-31 | 2017-12-31 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2023 Freemont St. SE - ATL | 100 | Fax sent 2018-01-01 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/1/2018 12:00:00 AM |  | 12/31/2017 12:00:00 AM |  |  | 1 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew uses a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-29 | 2016-02-29 | Savannah, City of (President Street WRF) | Chatham | savannah | 220 Deerwood Road | 520 |  | Raw Sewage | Coastal District |  | WWTP | Storm Drain | Canal | Equipment failure |  | Steve Fox | Steve Fox | Steve Fox | 2/29/2016 12:00:00 AM | Savannah | 2/29/2016 12:00:00 AM |  |  | 1 | savannah river | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | y | 0 | Control failure at LS 69 – Wilmington Island | Corrected control failure (wiring). Contained flow in Canal. Spread lime on contaminated areas and samples were taken at pond. Spill notification markers were placed at the spill site where discharge went into pond and along other shore locations. All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-03-01 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-10 | 2016-05-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 2321 Strathmoor Manor Drive, Lithonia | 3640 | Notification received on May 12, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/11/2016 12:00:00 AM |  |  |  |  | 0 | Pole Bridge Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 20:44 hours, when a crew rodded from the overflowing manhole 21 feet, cleared the blockage, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-05-13 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-30 | 2017-03-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 3127 Buford Highway, Atlanta | 76325 | Notification received on April 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Rags |  |  | Hsin Yeh | Hsin Yeh | 3/31/2017 12:00:00 AM |  |  |  |  | 1 | North Fork Peachtree Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Blockage of rags | The problem was corrected at 21:45 hours when a crew pressure washed between manholes 224ft, cleared the blockage at 180ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-04-03 | 0 | 1 | 0 | 0 | 0 | 0
2016-07-05 | 2016-07-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1277 Niles Avenue, NW | 2510 | fax received 7/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 7/6/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump malfuction | A contractor, Sunbelt Rentals, made a repair to the bypass pump. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-03-29 | 2016-03-29 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 1201 Summerbrook Cr., Athens | 896 | Initial email and full report faxed 3/30 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 3/30/2016 12:00:00 AM | Oconee | 3/29/2016 12:00:00 AM |  |  | 1 | tributary to Middle Oconee | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Flushable wipes clogged the sewer line causing the manhole to overflow | Rodded the sewer line. Cleaned and limed area. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-30 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-11-07 | 2015-11-07 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 2227 Baker Carter Drive | 13050 | email notification received 11/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Little Haynes Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2018-07-27 | 2018-07-27 | Fulton County (Big Creek WPCP) | Fulton |  | 7100 Roswell Road | 19380 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/27/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Grease and Debris | The manhole lines have been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-06-20 | 2017-06-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 644 Wesley Dr. NW - ATL | 255300 | Email received 2017-06-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 6/21/2017 12:00:00 AM |  | 6/20/2017 12:00:00 AM | 2017-06-21 | 2018-07-12 | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The spill was rain-induced. | The spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-21 | 0 | 0 | 0 | 1 | 1 | 0
2016-02-29 | 2016-02-29 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 3979 Woodward Mill Road | 6861 | Fax received 2/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/29/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Raked area and spread lime. Placed signs at spill and waterway. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-08-03 | 2018-08-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 40120000 | This spill is also entered as a violation. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 8/6/2018 12:00:00 AM |  | 8/4/2018 12:00:00 AM |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | South River Major TSS Spill From midnight August 3 to midnight August 4, City of Atlanta had a passive bypass of the sand filters that resulted in a major spill for TSS to the Chattahoochee River. August 4 TSS - 34 mg/L Permit Limit = 15 mg/L | Seeking additional landfill options for the removal of solids |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-28 | 2017-06-28 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3942 Memorial College Avenue, Clarkston | 2840 | Notification received on Jun e 30, 2017 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/28/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:24 hours when the crew pressure washed the 8" main from manhole 18-043-s203 200ft and cleared the blockage at 180ft, which at this time restored the normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-30 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-26 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 815 East Willow Park Drive | 8100 |  | Raw Sewage | Coastal District | GAJ020056 | WWRF | Stream |  | Wet weather |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 12/26/2015 12:00:00 AM | Coosa |  |  |  | 0 | Tributary of Tar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Infiltration of stormwater from heavy rains over several days | Five total vacuum trucks were used to mitigate the spill | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | David Oxford | 706-529-1010 | Dalton Utiilites
2017-06-20 | 2017-06-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 3010 Trafalgar Way, Chamblee | 6000 | Notification received on June 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 6/20/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 18:18 hours when the crew waited for the storm event to subside. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-23 | 0 | 1 | 0 | 0 | 0 | 0
2015-06-22 | 2015-06-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 560 Susan Creek Drive, Stone Mountain | 4920 | Notification received on June 24, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/22/2015 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 15:43 hours when a crew pressure washed the 8" sewer main downstream 180ft, clearing the grease blockage, and restored services |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-06-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-12 | 2016-02-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2933 Panthersville Road, Decatur | 29520 | Notification received on February 16, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/12/2016 12:00:00 AM |  |  |  |  | 0 | Doless Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken Main | The problem was corrected at 16:40 hours, when a crew built a berm to contain the spill and restored normal flow. The repair was completed on February 13, 2016. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-16 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 4949 South Royal Atlanta Drive, Tucker | 2500 | Notification received on September 15, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/11/2017 12:00:00 AM |  |  |  |  | 0 | Camp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 18:45 hours when the crews setup vaccum trucks to hold the sewer in the wet well until the backup pump was restored. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Vidalia, City of (Swift Creek WPCP) | Toombs | Vidalia | 1000 block of Vann Street Extension | 36000 |  | Raw Sewage | Coastal District | GA0025488 | Collection System | Ground, Stream | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/4/2016 2:10:00 PM | Altamaha | 2/4/2016 12:00:00 AM | 2016-02-05 |  | 1 | Rocky Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rain event (over 6 inches) and inflow issues cuased a manhole to over flow. | Sewer line investigation ongoing and widening to include other branches of the sewer main. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-03-08 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-17 | 2016-03-17 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1370 Brooklawn Road, Brookhaven | 1320 | Notification received on March 21, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 3/17/2016 12:00:00 AM |  |  |  |  | 0 | Perimeter Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 17:16 hours, when a crew pressure washed the sewer main 445ft, clearing the blockage at 348ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-22 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-02 | 2017-01-06 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Lift Station #49, Albany. | 14400 | Telephone call and email received on 01/03/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Lift Station | Unknown |  | Power failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/3/2017 12:00:00 AM |  |  |  |  | 1 | Unknown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The National Weather Service reported 8 - 9 tornadoes, plus straight line winds resulting in the power loss to 52 storm and sanitary lift stations. | Full power to all lift stations was restored on 01/14/2017. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2017-12-09 | 2017-12-09 | Douglasville, City of (South Central WPCP) | Douglas | Lithia Springs | 3507 Meadowview Drive, Lithia Springs | 53000 | Fax and email received on 12/12/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | WWTP | Stream |  | Power failure |  |  | Hsin Yeh | Hsin Yeh | 12/12/2017 12:00:00 AM |  |  |  |  | 1 | Dry Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The spill occurred due to a power failure, which was caused by the heavy snow storm. | The spill was stopped when the power in the area was restored. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-01-16 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-25 | 2015-07-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 785 Ponce De Leon Place, NE | 292 | fax received 7/29/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/29/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-09 | 2016-11-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1227 Niles Ave., N.W., Atlanta | 10 | Fax received on 11/10/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 11/10/2016 12:00:00 AM |  |  |  |  | 0 | Dry Land - did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was a by-pass pump malfunction. | Pump was repaired, and the area was placed on periodic inspection. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell |  | CITY OF ATLANTA
2018-03-23 | 2018-03-23 | Columbia County (Little River WPCP) | Columbia | Augusta | 3477 River Watch Parkway - Augusta | 900 | Fax sent 2018-03-23 | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream | Stream | Grease |  |  |  | Alys Hannum | 3/23/2018 12:00:00 AM |  | 3/23/2018 12:00:00 AM |  |  | 1 | Tributary to Reed Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Unstopped overflow with high pressure jet machine. Cleaned up area. Posted signs. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2018-03-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Thomaston, City of | Upson | Thomaston | Martha Mills LIft Station | 7725 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/13/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The Cause of this spill was hydraulic overload due to heavy rains in the COT service area. | Debris has been removed from the surronding area and the area has been disinfected with lime. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-28 | 2017-03-28 | LaFayette, City of (LaFayette WPCP) | Walker |  | 100 Feet North of Shattuck Industrial Blvd Lift Station | 50000 | A portable pump was set up at the Shattuck Industrial Blvd Lift Station and the wastewater was pumped into a tanker truck to minimize any additional spill during the force main repairs. | Raw Sewage | Mountain District - Cartersville | GA0025712 | WWTP | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 3/29/2017 12:00:00 AM | Coosa |  |  |  | 1 | Chattooga Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Crack in Force main from Shattuck Industrial Blvd Lift Station | The force main was uncovered the cracked pipe cut out and replaced with new pipe and clamps. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-07-13 | 2016-07-13 | Cobb County Water System | Cobb |  | 2839 Pine Meadow Drive | 110 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/13/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots in the sewer main causing the manhole to overflow into an unnamed lake tributary to Noonday Creek. | The Cobb Crew was able to stopped the overflow at 10:50 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-17 | 2015-02-17 |  | DeKalb | Dunwoody | 4867 Ashford Dunwoody Road, Dunwoody | 45900 | Notification received on February 18, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 2/18/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 19:39 hours when a crew sat up a bypass pump, contained the spill, vacuumed rags and pressure washed 10" sewer line. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-04 | 2017-12-04 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 370 Twin Brooke Way - Lawrenceville | 2690 | Fax sent 2017-12-04 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  |  | Alys Hannum | 12/4/2017 12:00:00 AM |  | 12/4/2017 12:00:00 AM |  |  | 1 | Unnamed Trib. of Yellow River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Debris | Raked area and spread lime; placed signs at spill and waterway |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-26 | 2016-08-26 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Doraville | 3604 Spring Drive | 5018 | fax received 8/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Other |  |  | Kim Hembree | Kim Hembree | 8/26/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Crooked Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole failure | raked area and spread lime; placed signs at spill and waterway |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2018-07-03 | 2018-07-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3160 Donald Lee Hollowell Py. NW - Atlanta | 300 | Fax sent 2018-07-04 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 7/4/2018 12:00:00 AM |  | 7/3/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-01 | 2016-04-01 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | 1011 Lower Poplar Street, Macon MH ID 64097 | 3800 | Call received on 04/04/2016; email received on 04/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024538 | WWTP | Stream | Shoreline | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overload due to heavy rains in the service area and a loss of powere at the Lower Poplar Water Reclamation Facility. | Debris was removed from the area, and the area was disinfected with lime. The Lower Poplar Water Reclamation Facility lost power during the storms on Friday morning April 1st. Once power was restored to the plant, the manhole stopped overflowing. The MWA will also continue to search for inflow and infiltration into its sewer system through its CCTV inspection and flow monitoring programs. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-06 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-16 | 2015-09-16 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 4380 Gunnin Road | 3780 | fax received 9/16/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/16/2015 12:00:00 AM |  |  |  |  | 1 | Unnamed Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken pipe | Repaired the main |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2017-04-30 | 2017-04-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1266 Sheridan Road, Atlanta | 3200 | Notification received on May 3, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/1/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 21:03 hours when a crew pressure wasted the connecting 12 inch sewer main 630ft, clearing the blockage at 390ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2018-02-11 | 2018-02-11 | Tallapoosa, City of (Tallapoosa WPCP) | Haralson |  | 20 Arbacoochee Street | 13000 |  | Raw Sewage | Mountain District - Cartersville | GA0020982 | WWTP | Stream |  | Equipment failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/12/2018 12:00:00 AM | Tallapoosa |  |  |  | 0 | Hollywood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Overheating of single pump in wet well due to excessive rain | Restored power and suggested city install secondary pump and back up power | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-03-20 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-05 | 2015-05-05 | Columbus Water Works (South WRF) | Muscogee | Columbus | Bridge @ 4124 Forrest Road | 50 | REC CALL 5/6/2015. REC EMAIL 5/6/2015. REC EMAIL CORRECT 5/7/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream | Stream | 3rd party contractor |  | Emily Wingo | Emily Wingo | Emily Wingo | 5/6/2015 2:04:00 PM | Chattahoochee | 5/6/2015 12:00:00 AM |  |  | 1 | Cooper Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A contarctor working on the bridge caused a small leak on an 8" pipe inside a concrete wall. | The pipe was plugged immediately and the overflow stopped. A pump around was put in place until the permanent repair could be made. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-05-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBUS WATER WORKS | (706)-649-3490
2015-04-19 | 2015-04-19 | Jasper, City of (Jasper WPCP) | Pickens |  | 41 Choctaw Circle Jasper GA 30143 | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0032204 | WWTP | Stream |  | Wet weather |  | Cindy Nix | Kathy Lewis | Cindy Nix | 4/21/2015 12:00:00 AM | Coosa |  |  |  | 0 | Champion Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Thunderstorms, heavy rain, infiltration | City of Jasper employees walked 3 sanitary sewer lines that connect to this pump station. City of Jasper will make any necessary repairs. | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-04-22 | 0 | 0 | 0 | 0 | 0 | 0 | David Hall | 706-692-9103 | CITY OF JASPER
2017-05-09 | 2017-05-09 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 8350 Roswell Road Sand Springs, 30350 | 69300 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/9/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-05-15 | 0 | 0 | 0 | 0 | 0 | 0 | Glenn Smith |  | Fulton Co Dept of Pub Wks
2016-03-09 | 2016-03-09 | LaGrange, City of (Long Cane Creek WPCP) | Troup | Lagrange | Hammet Road/Shoal Creek Lift Station | 4000 | Fax received on 03/09/2016. | Raw Sewage | Wastewater Regulatory Program | GA0036951 | Lift Station | Stream | Shoreline | Equipment failure |  |  | Paul Moisan | Paul Moisan | 3/9/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Shoal Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump failed at the Shoal Creek Lift Station. | Plant Maintenance crew replaced the failed pump which stopped the overflow. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-11 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-07 | 2016-12-07 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2614 Cross Creek Road, Augusta | 750 |  | Raw Sewage | Wastewater Regulatory Program | GA0037621 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 12/7/2016 12:00:00 AM |  |  |  |  | 0 | Butler Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris (rags and trash) was the cause of the overflow. | The line was opened and resumed normal flow. City will assess the line with CCTV to determine what future actions need to be taken to prevent future issues. The storm ditch was vacuumed out. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-12-08 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-01 | 2016-01-02 | Columbus Water Works (South WRF) | Muscogee | Columbus | 6906 Dixie Street, Columbus | 35287 | Fax and email received on 01/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 1/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Due to excessive rains and hydraulic loading, a manhole overflowed into Bull Creek. | Once the rain subsided and flow returned to normal, the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0 | Chris Cornett |  | Columbus Water Works
2016-09-06 | 2016-09-06 | Louisville, City of (Forstmann WPCP) | Jefferson | Louisville | Louisville Forstmann WPCP, Louisville | 0 | BOD, weekly average concentration (mg/L): permit = 12, reported = 72.2 TSS, weekly average concentration (mg/L): permit = 30, reported = 82 Flow was 0.193 MGD | Treated Effluent | Wastewater Regulatory Program | GA0050243 | WWTP | Stream | Stream | Other |  |  | Dagny Pariani | Dagny Pariani | 10/3/2016 12:00:00 AM | Ogeechee |  |  |  | 1 | Ogeechee River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | 0 | Immaturity of pretreatment pond at Coastal Processing caused high BOD/TSS loadings to the WPCP | Coastal Processing installed a DAF unit, bypassing pond to allow it to biologically mature |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOUISVILLE | 478-625-3166 |  | 72.2 | 82
2015-11-09 | 2015-11-09 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 296 The Plaza, Athens | 36768 | Initial and full report received 11/10 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 11/10/2015 12:00:00 AM | Oconee | 11/9/2015 12:00:00 AM | 2015-11-09 |  | 1 | Brooklyn Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | surcharge due to major rain event | lime applied. sewer upgrade is under design. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-11-12 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-07-22 | 2017-07-22 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 3395 Sixes Road Canton | 3360 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/23/2017 12:00:00 AM | Coosa |  |  |  | 0 | Unnamed stream behind 3395 Sixes Road Canton | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8 Inch sewer clogged | Construction jetted line and cleared the clog. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-14 | 2015-12-14 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 2449 Towne Lake Parkway, Woodstock, GA 30189 | 7770 | During further repairs on 12/15/15, an additional 1,350 gallons spilled from a cleanout drain at the vacant building. | Raw Sewage | Mountain District - Cartersville | GA0046451 | Collection System | Stream |  | Grease |  | Ebony Johnson | Ebony Johnson | Ebony Johnson | 12/14/2015 12:00:00 AM | Coosa |  |  |  | 0 | Unamed Tributary to Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy debris and roots blocked the sewer line. Paper, grease, and grit backed up in the line over time causing the overflow of a grease trap at a vacant building. | CCWSA construction crews jetted the line and used a vacuum truck to remove the debris, grit, roots, and grease from the line. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 2015-12-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-11 | 2016-05-11 | Rome, City of (Coosa WRF) | Floyd |  | 330 Woods Road | 500 |  | Raw Sewage | Mountain District - Cartersville | GA0024341 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 5/12/2016 12:00:00 AM | Coosa |  |  |  | 0 | Beech Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots in the sewer main | The sewer main was thoroughly cleaned | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-17 | 2018-06-17 | Cobb County Water System | Cobb |  | 5371 Whitehall Place | 1400 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/17/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nickajack Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The crew stopped stopped the spill at 4:50 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-29 | 2018-08-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1994 Bent Creek Wy. SW - Atlanta | 1493 | Fax sent 2018-08-31 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 8/31/2018 12:00:00 AM |  | 8/29/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Section of the pipe encased in concrete was leaking | Crew performed a point repair |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-04 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-10 | 2017-11-10 | Cumming, City of (Bethelview Road WPCP) | Forsyth | Cumming | 818 Atlanta Road - Cumming | 5500 | Call received 2017-11-11 | Raw Sewage | Wastewater Regulatory Program | GA0046019 | Collection System | Stream | Stream | Debris |  | Alys Hannum | Alys Hannum | Alys Hannum | 11/11/2017 12:00:00 AM |  | 11/10/2017 12:00:00 AM |  |  | 1 | Sawmill Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Plastic Steps and flushable wipes partially blocking the sewer line. | Line was jetted and cleared. The area affected has been cleaned up and lime has been applied. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-07 | 2015-11-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2334 Adams Drive, NW | 200 | fax received 11/07/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/7/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-05 | 2016-04-05 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 310 Thomasville Blvd., SE | 1592 | This is a private spill | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  |  |  |  | Kim Hembree | Kim Hembree | 4/6/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This is a private spill. | Private spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-01-22 | 2016-01-22 | Fulton County (Big Creek WPCP) | Fulton | Roswell | Azalea Drive/Riverside Road | 101277 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson |  | Reginald Williamson | 1/22/2016 12:00:00 AM | Coosa |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Wer Weather | Ongoing I/I | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc |  | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-04 | 2016-01-04 | Savannah, City of (President Street WRF) | Chatham | Savannah | Springfield Canal / CSX RR; east of 4720 Meadow Ave; north of 1600 Staley Ave; west of CSX RR (X Coordinate 977532.798; Y Coordinate 743243.889) | 3750 |  | Raw Sewage | Coastal District |  | WWTP | Canal |  | Rags |  | Steve Fox | Steve Fox | Steve Fox | 1/5/2016 12:00:00 AM | Savannah |  |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Sewer blockage in gravity main – rags & debris caused sewage discharge through pipe crack / defect | Contained flow in Springfield Canal, set up by-pass pumps and pumped water mix of storm drainage and sanitary sewer to City sanitary sewer collection system. Removed blockage and repairing break in gravity main. Utilized City of Savannah Jet Vacuum Trucks to further contain and remove sewage. Spread lime on contaminated areas. Spill notification markers were placed at the spill site where discharge went into storm swale, along Springfield Canal at Bowles Ford Pond, and Springfield Canal West Gwinnett Street. No recreational access in spill area (densely forested area). All entities (Georgia Environmental Protection Division, and Heath Department) were contacted along with all media through a news release from the City of Savannah Public Information Office. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-01-05 | 1 | 1 | 0 | 0 | 0 | 0
2017-10-22 | 2017-10-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2060 Peachtree Rd. NW - ATL | 10 | Fax sent 2017-10-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 10/23/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Equipment failure. | Crew replaced a hose on the by-pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-16 | 2015-02-16 | Winder, City of (Marburg Creek WPCP) | Barrow | Winder | Winder Marburg Creek WRF | 0 | Verbal notification from Jamie received 2/17/2015. | Undisinfected Secondary Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Power failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/17/2015 12:00:00 AM |  |  |  |  | 1 | Marburg Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to a power failure, the Marburg Creek WRF had to bypass the UV disinfection process. The facility does not have a backup or auxiliary power source during power outages. They use offline basins as storage basins. In this instance, the offline storage basins filled before power was restored and the facility was forced to send the flow through the plant without UV. | Power restored | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF WINDER
2015-08-17 | 2015-08-17 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | 820 Harrington Drive | 3850 | fax received 8/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream |  | Rags |  |  | Kim Hembree | Kim Hembree | 8/18/2015 12:00:00 AM |  |  |  |  | 1 | Tributary to Fishing Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Rod sewer line, remove rags, and lime area. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2018-08-14 | 2018-08-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2533 Henderson Mill Road Atlanta GA 30345 | 9566 | Discovered 8/23/18, source tracking to the 14th. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 8/23/2018 8:14:00 AM | Ocmulgee |  |  |  | 1 | Henderson Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | cracked pipe | made 4 ft repair to stop spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-20 | 2016-03-20 | Savannah, City of (President Street WRF) | Chatham | savannah |  | 5000 | this spill was managed by Water Utility Management, LLC, who recently purchased the Chatham county conveyance system. | Raw Sewage | Coastal District |  | WWTP | Other | Ditch | Power failure |  | Steve Fox | Steve Fox | Steve Fox | 3/20/2016 12:00:00 AM | Savannah | 3/21/2016 12:00:00 AM |  |  | 1 | herb creel | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | The lift station located on LaRoche Ave. at Hopecrest Ave was wired improperly. This caused the circuit-breaker to trip and the primary pump did not run. The secondary pump was not wired to run at all. The alarm (audible with light) was inoperable, and the unit did not have a ‘dialer’ mechanism to remotely alert operators. The lift station filled and the collection system began to fill, and the first point of overflow was a manhole at the cul-de-sac end of Elizabeth Circle. Water leaked from the manhole into the street and ultimately into the storm drainage to Herb Creek. | Electrical parts were installed and all pumps are now running. Water was pumped down in the lift station, and the area affected by the leak was cleaned and treated with lime. We notified area residents via email, and we posted yard signs throughout Elizabeth Cr. We notified EPD, Chatham County, including the Chatham County Health Department, as well as the City of Savannah. We also gave a press release to WTOC and the Savannah Morning News (was in Saturday’s edition). We have repaired the local alarm and we are ordering automatic dialers for all Chatham County lift stations. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2016-03-22 | 1 | 1 | 0 | 0 | 0 | 0
2017-04-06 | 2017-04-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 595 Peyton Rd. SW - ATL | 10 | Fax received 2017-04-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 4/7/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-23 | 2015-12-27 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 594 Industrial Way, E. Macon MH #71726 | 1292980 | Fax and email received 12/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 12/29/2015 12:00:00 AM | Upper Ocmulgee | 12/23/2015 12:00:00 AM | 2015-12-26 | 2016-11-28 | 1 | Boggy Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Hydraulic overload from the service area receiving 5.78 inches of rain from December 21-26. | Debris was removed from the area and the affected area was disinfected with lime. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-30 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2015-10-05 | 2015-10-05 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Dead end of Clinton St., at Manhole ID 66157. | 2380 | Email received by Paul Moisan on 10/06/2015 | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/6/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Ditch feeding Ocmulgee River | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this spill was grease. There are no commercial sources of sewage upstream from this location, and residential grease is not regulated. | Debris was removed and the affected area was disinfected with lime. The line has been scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly "Hot Spot" Inspection list. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-10-06 | 1 | 1 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | Golf Course | 40425 | Verbal and email notification received 9/02/2016 - 9/03/2016. | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Other |  | Natural Disaster |  | Kim Hembree | Kim Hembree | Kim Hembree | 9/3/2016 12:00:00 AM |  |  |  |  | 1 | Retention Pond | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hurricane Hermine |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-01-04 | 2015-01-04 | Cornelia, City of (Cornelia WPCP) | Habersham |  | Circle Drive | 2000 |  | Raw Sewage | Mountain District - Cartersville | GA0021504 | WWTP | Stream |  | Wet weather |  | Sam Buckles | Kathy Lewis | Cindy Nix | 1/5/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | North Fork of Mud Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain |  | 455ebb3c-eb6e-11e0-b8d8-000c29971acc | 470ba86e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | Andrew Pilgrim | 706-490-4613 | CITY OF CORNELIA
2017-03-15 | 2017-03-15 | Rockdale County (Quigg Branch WPCP) | Rockdale |  | 1060 Scott St. | 98 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/15/2017 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tributary Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1060 Scott Street | Clean Piping | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-14 | 2017-01-14 | Marietta (City of)- Sewers | Cobb | marietta | 1109 Claymore Dr | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/14/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Info in report. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-16 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-27 | 2017-11-27 | Cobb County Water System | Cobb |  | 2081 Tweleve Oaks Circle | 640 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream |  |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/27/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cobb Crew stopped the overflow at 11:30 a.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-11-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-06 | 2018-07-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1212 Perimeter Center West Atlanta GA 30346 | 1980 | manholes 18-348-s073 and 18-348-s080 spilling | Raw Sewage |  | GA0024147 | Collection System |  |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 7/6/2018 6:49:00 PM | Ocmulgee |  |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease Blockage | Pressure washed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-08 | 2017-12-08 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 1423 Stockbridge Rd, Jonesboro Manhole: 2204401 | 6000 | Fax received on 12/09/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/9/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Rum Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned back to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-11 | 0 | 1 | 1 | 0 | 0 | 0
2016-09-05 | 2016-09-05 |  |  | Decatur | 250 Seneca Street, Decatur | 500 | Notification received on September 7, 2016. | Raw Sewage | Wastewater Regulatory Program |  | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/6/2016 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Lateral line leaking | The problem was corrected on September 6, 2016 at 10:45 hours when the crew turned the water meter off, made the repair in the right-of-way and restored normal service. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-07 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-20 | 2017-03-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 273 Industrial Park Dr. - Lawrenceville | 3247 | Fax received 2017-03-20. | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 3/20/2017 12:00:00 AM |  | 3/20/2017 12:00:00 AM |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural failure - other; Debris - rocks or construction material. | Raked are and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-10 |  | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1641 Council Bluff Drive, Atlanta | 0 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Creek crossing reported leaking | Sewer main repaired |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-02 | 2016-09-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1588 Johnson Road, NW | 1620 | fax received 9/02/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 9/2/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-05 | 2018-07-05 | Brunswick-Glynn County JWSC (Academy Creek WPCP) | Glynn | Brunswick | Altamaha Canal near Harry Driggers Blvd. and Shell Road. | 2000 | On 7/9/2018 Complaint #86801 was received concerning this spill. | Raw Sewage | Coastal District | GA0025313 | Force Main | Canal | Canal | Pipe failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/5/2018 2:21:00 PM | Altamaha | 7/6/2018 12:00:00 AM | 2018-07-05 |  | 1 | Altamaha Canal | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Defective ductile iron pipe (force main). | Made repairs by replacing 21 feet of 12" defective ductile iron pipe with C-900 PVC. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2018-07-10 | 1 | 1 | 0 | 0 | 0 | 0
2015-06-02 | 2015-06-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1940 Fisher Road, SE | 160 | fax received 6/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/3/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-24 | 2016-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 424 Lindbergh Drive, NE | 12 | fax received 2/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/25/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-07 | 2015-12-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2950 Martin Luther King Jr. Drive, SW | 10 | fax received 12/08/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/8/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-06-15 | 2015-06-15 |  | Fulton | Atlanta | Hartsfield-Jackson Atlanta International Airport, College Park Lift Station No. 2 | 90000 | Bryan Heard with ERT notified 6/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Stream |  | Debris |  | Bryan Heard | Kim Hembree | Kim Hembree | 6/16/2015 12:00:00 AM |  |  |  |  | 1 | Sullivan Creek | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Cause is under investigation |  | 43f46094-eb6e-11e0-b8d8-000c29971acc | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-16 | 0 | 0 | 1 | 0 | 0 | 0 | [8 empty] | Hartsfield-Jackson Atlanta International Airport
2015-06-15 | 2015-06-15 |  | Fulton |  | Hartsfield-Jackson Atlanta International Airport, College Park Lift Station No. 2 | 90000 | Bryan Heard with ERT notified 6/15/2015 | Raw Sewage | Wastewater Regulatory Program |  | Lift Station | Stream |  | Debris |  | Bryan Heard | Kim Hembree | Kim Hembree | 6/16/2015 12:00:00 AM |  |  |  |  | 1 | Sullivan Creek | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | Cause is under investigation |  | 43f46094-eb6e-11e0-b8d8-000c29971acc | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-06-16 | 0 | 0 | 1 | 0 | 0 | 0 | [8 empty] | Hartsfield-Jackson Atlanta International Airport
2018-06-26 | 2018-06-26 | Columbus Water Works (South WRF) | Muscogee | Columbus | A bypass was installed and the overflow was stopped. | 45360 |  | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Force Main | Stream |  | Equipment failure |  |  | Juan Robles |  | 6/27/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Plug failure while performing repairs to a force main. |  |  |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-16 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-02 | 2016-11-02 | Cobb County (Marietta Water Authority - James E. Quarles WTP) | Cobb | Marietta | 763 Bonnie Dell Dr. | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/2/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure and Creek bank erosion | Marietta Water personnel quickly sealed off the leakage thus rstoring normal flow. This section of pipe is subject to erosion so support for pipe and monitoring will be established. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-11-03 | 0 | 0 | 0 | 0 | 0 | 0 | Tim Marshall |  | CITY OF MARIETTA
2016-02-18 |  |  | DeKalb |  | 4886 Wedgewood Way | 380 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pressure washed main to restore flow |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-11-23 | 2016-11-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Scottdale | 280 Hatton Drive, Scottdale | 3780 | Notification received on November 28, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/23/2016 12:00:00 AM |  |  |  |  | 0 | Indian Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:30 hours, when a repair crew pressure washed the 10" sewer main 200ft, clearing the blockage at 150ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-28 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-10 | 2016-11-10 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 5502 Amelia Lane, Rex | 14400 | Fax recieved on 11/11/2016. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 11/11/2016 12:00:00 AM |  |  | 2016-11-01 |  | 1 | Cotton Indian Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  | 0 | Heavy Grease in line. | Crews cleared the blockage and returned the flow to normal. Follow-up actions will include CCTV and grease treatment chemical to remove any remaining grease from the line. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-14 | 0 | 1 | 1 | 1 | 0 | 0
2016-01-15 | 2016-01-15 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse RD. and Sylvia Dr. | 80000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/12/2016 12:00:00 AM | Satilla |  |  |  | 0 | Rockhouse Rd. and Sylvia Dr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rains |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-26 | 2015-08-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 2899 Shallowford Road, Chamblee | 34 | Notification received on August 27, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/27/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 17:26 hours, when the clean-up crew, vacuum sewage from hole to contain the spill. While another crew completed the sewer main repair at 2230 hours and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-08-31 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-13 | 2015-01-13 | Tifton, City of (New River WPCP) | Tift | Tifton | Agrirama Lift Station | 5000 | REC CALL 1/14/2015 | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Lift Station | Canal | Canal | Power failure |  | Emily Wingo | Emily Wingo | Emily Wingo | 1/14/2015 10:10:00 AM | Suwannee | 1/14/2015 12:00:00 AM |  |  | 1 | Little River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | SCADA showed Panel and 2 pumps tripped. Storm passed through and may have caused power outage. | Reset panel and pumps | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-01-14 | 0 | 1 | 0 | 0 | 0 | 0 | Scott Murphy |  | ESG Operations, Inc. | [5 empty] | CITY OF TIFTON | 229-391-3937
2017-10-30 | 2017-10-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1375 Eastgate Ct. SE - ATL | 565 | Fax sent 2017-10-31 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 10/31/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-06 | 2017-09-06 | Columbus Water Works (South WRF) | Muscogee | Columbus | Behind FB Water Plant on Cole Dr. off Marne Rd - Columbus | 693 | Telephone call and Fax received on 09/06/2017. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Equipment failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Upatoi Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A leaking boot connecting two sections of 8-inch pipe. | The leak was repaired, and normal flow resumed. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-14 | 2016-04-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 623 Lynn Valley Road, SW | 50 | fax received 4/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/15/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-18 | 2015-11-18 | Columbus Water Works (South WRF) | Muscogee | Columbus | 1518 Cherokee Ave. | 4134 | Fax received on 11/19/2015. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Wet weather |  |  | Paul Moisan | Paul Moisan | 11/19/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Weracoba Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Due to excessive rains and hydraulic loading a manhole overflowed into Weracoba Creek. The basin is Weracoba Creek Basin. | Once the rain subsided and flow returned to normal and the overflow stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-11-20 | 0 | 0 | 0 | 0 | 0 | 1
2017-09-20 | 2017-09-20 | Cobb County Water System | Cobb |  | 1680 Little Willeo Rd | 2820 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/20/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Willeo Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Stopped Spill and limed manhole | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-09-25 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2018-01-03 | Arlington, City of (Arlington WPCP) | Calhoun | Arlington | Pond and manholes. | 10000 | Due to excessive rainfall overflows were reported at both the pond and at manholes. | Raw Sewage | Southwest District | GA0026204 | WWTP | Ground, Stream | Stream | Wet weather |  | Linda Stevens | Linda Stevens | Linda Stevens | 1/3/2017 8:00:00 AM | Flint | 1/3/2017 12:00:00 AM | 2017-01-03 | 2018-01-23 | 1 | Perry Creek | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive Rainfall | Put out warning signs at Perry Creek, also put out warning cones around any manhole that is overflowing. Start stream monitoring. | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 72b89952-7fed-43ef-a49d-acceca69b62c | 2017-01-09 | 1 | 1 | 0 | 1 | 1 | 0
2018-05-30 | 2018-05-30 | Paulding County (Pumpkinvine Creek WRF) | Paulding |  | 141 Valleyside Drive, Dallas | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0039021 | WWTP | Stream |  | Rags |  | Eric Dykes | Kathy Lewis | Katie Meade | 5/30/2018 12:00:00 AM | Coosa |  |  |  | 1 | Tributary to Rakestraw Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease build up and rags | Jet lines | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 77e9b2a3-e985-4535-b5df-da199a9c72b6 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-05-31 | 1 | 0 | 0 | 0 | 0 | 0
2016-04-16 | 2016-04-16 | Newnan Utilities (Wahoo Creek WPCP) | Coweta | Newnan | 107 Southfield Dr. | 7820 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/6/2016 12:00:00 AM |  |  |  |  | 0 | White Oak Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots and debree in line. | Jetted and root cut line with jet truck. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-01 | 0 | 0 | 0 | 0 | 0 | 0
2015-02-24 | 2015-02-24 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1178 Garibaldi Street, SW | 2 | fax received 2/25/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/25/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-24 | 2017-01-24 | Winder, City of (Cedar Creek WPCP) | Barrow | Winder | 431 Miles Patrick Road - Winder | 208000 |  | Raw Sewage | Wastewater Regulatory Program | GA0038776 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 1/25/2017 12:00:00 AM |  | 1/25/2017 12:00:00 AM | 2017-01-25 |  | 1 | Cedar Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Two issues led to the sewage spill: 1) a faulty fuse in the influent pump control panel prevented the primary pumps from activating, and 2) the starter failed to engage in an 8" backup pump, preventing it from starting. | Faulty fuse and starter have been replaced; area disinfected with powdered lime. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-30 | 0 | 1 | 1 | 0 | 0 | 0
2017-01-25 | 2017-01-27 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Intersection of Pace St, and Hog Pen Ditch Canal, Albany. | 270000 | Telephone call and email received on 01/27/2017. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Canal |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/27/2017 12:00:00 AM |  |  |  |  | 1 | Hog Pen Ditch canal | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | A roadway collapsed at the intersection of Pace Street and Hog Pen Ditch canal, and damaged a section of sewer pipe. In the early morning of 01/27/2017, the pipe collapsed and became obstructed. | Bypass pumps are being used until a contractor can repair the section. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-03-06 | 0 | 1 | 0 | 0 | 0 | 0 | Jeff Hughes | 229-883-8998 | Albany (City of)
2016-03-17 | 2016-03-17 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 944 Deercrest Circle | 1800 | fax received 3/18/2016 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 3/18/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Jones Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown | Unclogged sewer line with high pressure jet machine. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY
2016-10-11 | 2016-10-31 | Savannah, City of (President Street WRF) | Chatham | Savannah | 4018 Clinch Street | 80 |  | Raw Sewage | Coastal District | GA0025348 | N/A | Canal | Canal | Wet weather |  | Dagny Pariani | David Lyle | Hailey Harden | 10/11/2016 12:00:00 AM |  | 10/11/2016 12:00:00 AM |  |  | 1 | Springfield Canal | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hurricane Matthew caused extraneous water that caused a manhole to overflow | modified station operations, added another pump. Spill notification markers were placed at the spill site and at Springfield Canal/ West Victory Drove, and Bowles Ford Park. | 89352e56-9649-4d50-9761-577155a9c85b | f3736089-4e7b-46dd-ac91-b83d625d4fa0 | 3ddaae5c-eb6e-11e0-b8d8-000c29971acc | 2016-10-26 | 1 | 1 | 0 | 0 | 0 | 0
2016-03-02 | 2016-03-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2214 Wingate Street, SW | 264 | fax received 3/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 3/3/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the service lateral caused by the mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-25 | 2016-02-25 | Macon Water Authority (Lower Poplar WRF) | Bibb | Macon | Ocmulgee Heritage Trail, near 2nd Street Bridge, Macon MH # 66138 | 436743 | Telephone call received on 02/25/2016; fax and email received on 03/01/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024538 | Collection System | Stream | Shoreline | Rags |  | Paul Moisan | Paul Moisan | Paul Moisan | 2/25/2016 12:00:00 AM | Ocmulgee | 2/25/2016 12:00:00 AM | 2016-03-01 | 2017-02-28 | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | The cause was clogged pumps at the Main Street Lift Station. The cause of the clogs was large rags. The pumps at the station had previously been cleaned on February 18, 2016. | The maintenance department is scheduling the grinders at the Main Street Lift Station to be inspected and also will be hiring a cleaning company to assist with removing any build-up in the wet wells. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-03-02 | 1 | 1 | 0 | 1 | 1 | 0
2016-12-22 | 2016-12-22 | Columbia County (Little River WPCP) | Columbia | Evans | 457 Bartram Trail Club Dr. - Evans | 1800 |  | Raw Sewage | Wastewater Regulatory Program | GA0047775 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Hsin Yeh | 12/22/2016 12:00:00 AM |  |  |  |  | 1 | Euchee Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Build up of debris in pipe. | Unstopped with high power jet machine and removed debris. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-23 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1820 Doug Barnard PKWY - J.B. Messerly WPCP - Augusta | 1716840 | Fax sent 2017-09-12 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | WWTP | Stream |  | Power failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 9/13/2017 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | During Hurricane Irma: Treatment flows were near 80 MGD when a failure was experienced in one of the electrical feeders that powers 4 out of the 8 influent pumps. Failure was traced to the loss of one phase at a junction box. | Damaged power feed was repaired and the additional pumps were placed back into service by 12:00 AM on September 12th. There is a project underway that will remove some of the load from existing power feeders by placing one pump from each set of feeders on a new set of feeders. That project is awaiting new pumps for delivery January 2018. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-13 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-01 | 2015-12-01 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 92 Piedmont Avenue, NE | 450 | fax received 12/02/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 12/2/2015 12:00:00 AM |  |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-11-08 | 2016-12-07 | Fulton County (Camp Creek WPCP) | Fulton |  | 5200 Buffington Rd, Atlanta, GA 30349 | 45150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 11/8/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Tributary to Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and Grease | CCTV and flush with grease control. Applied inhibitors to affected area. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-13 | 2015-07-13 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Duluth | 4747 Satellite Blvd. | 2520 | fax received 7/13/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 7/13/2015 12:00:00 AM |  |  |  |  | 1 | Hopkins Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sanitary sewer main over creek |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY | 678-376-7000
2018-01-08 | 2018-01-08 | Cobb County Water System | Cobb | Marietta | 3843 Spring Meadow Dr. | 1450 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Other |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 1 | Tanyard Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Gravel | Stopped Spill and Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-12 | 2016-03-12 | Marietta (City of)- Sewers | Fulton | Marietta | 270 Willow Glen Dr. | 375 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/12/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | An unknow blockage caused a swer main to back up and leak a small amount of waste water onto the street into a nearby storm drain. | Marietta Water personnel quickly relieved the blockage by hydrojetting the sewer main and restoring normal service. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-03 | 2015-01-03 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | This is day two of an ongoing outfall spill reported by the City | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/4/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is day two of an outfall spill reported by the City. Reported TSS = 75 mg/L. Volume = 87,300,000 gallons |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-16 | 2018-04-16 | Cobb County Water System | Cobb |  | Cherry Hill Dr @ Pine Valley Rd. | 70 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/16/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Spread Lime | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-14 | 2016-01-14 |  | Rockdale |  | 1060 Scott Street | 60 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/14/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-19 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-16 | 2016-05-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1918 Delowe Place,SW | 1020 | fax received 5/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/17/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-12 | 2016-12-12 | Athens-Clarke County (Middle Oconee WPCP) | Clarke | Athens | 255 Laurel Dr. | 192 | Manhole overflowed | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/14/2016 12:00:00 AM | Oconee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line blockage due to flushable wipes | rodded sewer and inspected line | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-15 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-30 | 2016-04-30 | Cherokee County Water & Sewer Authority (Rose Creek WPCP) | Cherokee |  | 2230 Towne Lake Parkway Woodstock | 2800 |  | Raw Sewage | Mountain District - Cartersville | GA0046451 | WWTP | Stream |  | Pipe failure |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 5/2/2016 12:00:00 AM | Coosa |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | CCWSA construction crews found a large split in the pipe | CCWSA construction crews cut out the split section of pipe and replaced it with a new one. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-05-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-01 | 2016-02-01 | Cobb County MS4 | Cobb |  | 6819 Ivy Log Drive | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 2/1/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Gordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease in sewer main causing the manhole to overflow into a tributary of Gordon Creek. |  | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-23 | 2018-06-23 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 9450 Brown Road, Jonesboro | 2400 | Lift station personnel will trouble shoot to make sure we are prepared for an additional event occurring. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Lift Station | Stream | Stream | Power failure |  |  | Juan Robles | Juan Robles | 6/23/2018 1:55:00 PM | Flint | 6/23/2018 12:00:00 AM |  |  | 0 | Swamp Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Multiple. Power restored to lift station and flow returned to normal. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-26 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-19 | 2016-08-19 | Tifton, City of (New River WPCP) | Tift | Tifton | 109 Lakewood Drive, Tifton | 5000 | Email received on 08/23/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 8/23/2016 12:00:00 AM |  |  |  |  | 1 | New River Basin | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was due to a grease blockage and roots in the main line. | Hydrated lime has been spread to mitigate and sanitize the affectad area. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-08-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-08 | 2017-02-08 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 3109 Dover Dr. - Duluth | 2125 | Fax received 2017-02-08 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  | Alys Hannum | Alys Hannum | 2/8/2017 12:00:00 AM |  | 2/8/2017 12:00:00 AM |  |  | 1 | Sweetwater Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris - wipes, paper, and other products. | Raked area and spread lime; placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-05 | 2016-05-05 | Cobb County Water System | Cobb |  | 2226 Courts Drive | 90 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Unknown |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 5/5/2016 12:00:00 AM | Unknown |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Solids | The Water System was notified at 9:30 and the crew stoped the overflow at 10:15am | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-05-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-08 |  |  | DeKalb |  | 2190 Meadowcliff Drive | 40 |  | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Ground |  |  |  |  | Hsin Yeh | Hsin Yeh | 6/1/2016 12:00:00 AM |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Pump was repaired and flow was restored |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-30 | 2015-12-30 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 1/14/2016 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure caused effluent TSS to rise to 30.0 mg/L on 12/30/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-06 | 2017-10-06 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Stone Mountain | 4554 Stonegate Industrial Blvd, Stone Mountain | 100 | Notification received on October 9, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWRF | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/6/2017 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Root blockage | The problem was corrected at 08:53 hours when the first responder crew rodded the 6" sewer stub 30-ft, cleared the root blockage, unstopped the lateral and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-10 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-26 | 2017-01-26 | Gwinnett County (Crooked Creek WPCP) | Gwinnett | Norcross | Manhole behind 5991 Meadowbrook Drive - Norcross | 5819 | Fax received 2017-01-27 | Raw Sewage | Wastewater Regulatory Program | GA0026433 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/27/2017 12:00:00 AM |  | 1/26/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Jackson Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris - wipes, paper, and other products. | Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-28 | 2018-06-29 | Savannah, City of (President Street WRF) | Chatham | Savannah | Manholes at 303 West River Street and Indian St/MLK. | 7650 | Initial phone call and full emailed report received 6/29/2018. | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain, Stream | Stream | Contractor |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 6/29/2018 12:00:00 AM | Savannah | 6/29/2018 12:00:00 AM |  |  | 1 | Savannah River | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contractor maintained bypass pumps at an active construction site surcharged the City's sewer system creating a manhole overflow at 303 West River Street. Mitigation by the City created a second manhole overflow at the intersection of Indian Street and MLK. | Vac trucks removed residual sewage. Jetted the sewer line. Ensured bypass pumps operating correctly. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2018-07-02 | 0 | 1 | 0 | 0 | 0 | 1
2018-03-29 | 2018-03-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1825 Longdale Drive, Decatur GA 30032 | 1060 | manhole 15-148-s050 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Unknown |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/29/2018 4:30:00 PM | Ocmulgee | 3/29/2018 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown | pressure washed 8" main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-03 | 2016-02-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2351 Adams Drive, NW | 7100 | fax received 2/04/2016. COA Service Request No. 7519108 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 2/4/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-08-20 | 2018-08-20 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Conley | 2091 Blue Creek Court Conley GA 30288 | 960 | manhole 15-043-s145 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 8/20/2018 5:40:00 PM | Ocmulgee |  |  |  | 1 | Blue Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Pressure washed line |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-28 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-06 | 2015-01-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 1375 Peachtree Street, NE | 462 | fax received 1/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/7/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-12-06 | 2016-12-06 | Cobb County Water System | Cobb |  | 1855 Hurt Rd. | 150 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/6/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-08-11 | 2015-08-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1660 Johnson Road, NW | 3270 | fax received 8/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 8/12/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-07 | 2018-08-06 | Moultrie, City of (Moultrie WPCP) | Colquitt | Moultire | Woodridge Road SW | 4500 |  | Raw Sewage | Wastewater Regulatory Program | GA0024660 | Collection System | Ground |  | Power failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/7/2018 12:00:00 AM | Ochlockonee |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Power outage at lift station | lime disinfectant used. All contained a site |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-08-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-01-03 | 2018-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 3507 Melody Drive - Augusta | 1350 | Email sent 2018-01-04 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Grease |  |  | Alys Hannum | Alys Hannum | 1/4/2018 12:00:00 AM |  |  |  |  | 1 | Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy amounts of grease and other debris were in the line. | Used the rodder truck to auger the line. At 96’ a blockage was opened. The road was washed down and the storm drain was flushed and vacuumed. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-03-12 | 2018-03-12 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 3520 Old Lexington Road | 57500 |  | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream |  | Pipe failure |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 3/14/2018 12:00:00 AM | Oconee |  |  |  | 1 | Cedar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Fallen tree broke pipe | Installed temporary pumparound system while pipe repaired and bank stabilized |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-15 | 2016-03-15 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Intersection of Harrington Drive and Hancock Street | 400 |  | Raw Sewage | Wastewater Regulatory Program | GA0030775 | Collection System | Stream | Stream | Grease |  |  | Dagny Pariani | Dagny Pariani | 3/15/2016 3:31:00 PM | Oconee | 3/15/2016 12:00:00 AM |  |  | 1 | Tributary to Fishing Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage in the sewer line | Unstopped the sewer line, cut away roots, and treated the line with copper sulfate. Ground around the spill was raked and treated with lime. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-03-16 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF MILLEDGEVILLE
2015-07-11 | 2015-07-11 | Brunswick-Glynn County Water and Sewer Commission (Saint Simons Island WPCP) | Glynn |  | 18 West Lake Drive, St. Simons Island | 3500 |  | Raw Sewage | Coastal District | GA0021521 | Lift Station | Basin | Ditch | Equipment failure |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 7/11/2015 9:05:00 AM | Satilla | 7/11/2015 12:00:00 AM |  |  | 1 | Possible entry into state waters | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A faulty main breaker at lift station 2032 caused several manholes to over flow while the lift station was off-line. | Certified electric replaced the main breaker. Vac-con trucks recovered 300 gallons | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2015-07-21 | 1 | 1 | 0 | 0 | 0 | 0
2016-10-11 | 2016-10-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 302 East Howard Avenue, Decatur | 80 | Notification received on October 13, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 10/12/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 17:54 hours, when the contractor setup a by-pass pump to contain the spill, made the repair to the 8" sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-17 | 0 | 1 | 0 | 0 | 0 | 0
2018-03-20 | 2018-03-20 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 726 B 728 B Walton Court - Social Circle | 200 | Email sent 2018-03-21 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground | Swale | Grease |  |  | Alys Hannum | Alys Hannum | 3/21/2018 12:00:00 AM |  | 3/20/2018 12:00:00 AM |  |  | 0 | Did Not Enter State Waters | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Jetted line. As a result of jetting the line, downstream manhole ran over as well. Spill volumes were totaled. Signs posted. Lime applied. Public agencies were notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2017-04-27 | 2017-04-27 | Summerville, City of (Summerville WPCP) | Chattooga |  | 74 Maple Road Summerville | 1000 |  | Raw Sewage | Mountain District - Cartersville | GA0025704 | WWTP | Stream |  | Grease |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/27/2017 12:00:00 AM | Coosa |  |  |  | 0 | Chattooga River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease build-up in sewer line | City sewer crew cleaned up all of the spill that was on the ground and then lime was spread upon the area that contained the spill within the hour that it was reported. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-16 | 2018-05-16 | Hartwell, City of (Hartwell WPCP) | Hart | Hartwell | 402 Hodges Mill Rd Hartwell GA 30643 | 15000 | Exert from email received in attached file | Raw Sewage | Wastewater Regulatory Program | GAJ020114 | Collection System | Stream |  | Wet weather |  | Dillon Rodenbaugh | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/16/2018 12:00:00 AM | Savannah |  |  |  | 1 | Cuba Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | rain event | Cleared pump of trash | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-22 | 2016-08-22 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 16202 Waldrop cove, Decatur | 1400 | Notification received on August 23, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 8/22/2016 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The spill was contained at 13:03 hours when a crew pressure washed the sewer main, cleared the blockage, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-08-24 | 0 | 1 | 0 | 0 | 0 | 0
2016-09-12 | 2016-09-12 | Fulton County MS4 | Fulton | College Park | 5555 Bush Rd | 980 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/12/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morning Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-18 | 2016-10-18 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 27 Jefferson Place, Athens | 2625 | Initial and full report received via email on 10/19. | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Rags |  |  | Dagny Pariani | Dagny Pariani | 10/19/2016 12:00:00 AM | Oconee | 10/19/2016 12:00:00 AM |  |  | 1 | unnamed tributary to Brickyard Creek | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Disposable wipes clogged the sewer line causing a manhole to overflow | Rodded the sewer line to clear the clog. Lime applied. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-10-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2015-05-27 | 2015-05-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 301 Clifton Street, SE | 93000 | Verbal notification received 5/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 5/27/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 |  | Pipe replaced | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-22 | 2018-02-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 390 Stovall St. SE - ATL | 340 | Fax sent 2018-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/23/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill. The process to clean and disinfect the site has been initiated. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-03 | 2017-01-03 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift station in Eastman, GA. | 5000 |  | Raw Sewage | Southwest District | GA0046485 | Pump Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 1/3/2017 11:00:00 AM | Ocmulgee | 1/3/2017 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rainfall caused overflow at Legion Drive Lift Station. | PN's done on January 3, 2017. Newspaper ran PN on January 11, 2017. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2017-01-17 | 1 | 1 | 0 | 0 | 0 | 0
2017-01-08 | 2017-01-08 | Marietta (City of)- Sewers | Cobb | Marietta | 2504 Cedar canyon Rd | 1100 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System |  | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/10/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Marietta Water personnel qucikly relieved the blockage thus retoring normal service. The sewer main will be examined by CCTV to determine a possible cause. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-10 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-12 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1695 Foster Place, Macon MH ID 59454 | 3060 | Telephone call received on 09/12/2017. Fax and email received on 09/14/2017. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch | Shoreline | Grease |  | Paul Moisan | Paul Moisan | Paul Moisan | 9/12/2017 12:00:00 AM | Ocmulgee | 9/12/2017 12:00:00 AM |  |  | 1 | Walnut Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease. | Grease was removed, flow returned to normal, and the area was disinfected with lime. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-15 | 0 | 1 | 0 | 0 | 0 | 0
2018-08-08 | 2018-08-08 | Pine Mountain, Town of (Pine Mountain WPCP) | Harris |  |  | 500 |  | Raw Sewage | West Central District | GA0025691 | Lift Station | Stream | Stream | Equipment failure |  |  |  | Stephanie Edwards | 8/8/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Crawford Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 426838fe-eb6e-11e0-b8d8-000c29971acc |  | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-28 | 2016-03-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 100 | fax received 3/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/29/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The construction crew made a point repair to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-03-09 | 2015-03-09 | Rome, City of (Rome WRF) | Floyd |  | Behind 207 North Avenue | 25000 |  | Raw Sewage | Mountain District - Cartersville | GA0024112 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 3/9/2015 12:00:00 AM | Coosa |  |  |  | 0 | Burwell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to roots in the sewer main | The sewer main was thoroughly cleaned. | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-03-10 | 0 | 0 | 0 | 0 | 0 | 0 | Jeff Wenzel | 706-236-4569 | CITY OF ROME
2018-04-10 | 2018-04-10 | Rockdale County (Quigg Branch WPCP) | Rockdale | Conyers | 1169 Pine Log Rd | 540 |  | Raw Sewage | Wastewater Regulatory Program | GA0047678 | Collection System | Stream | Stream | Roots |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/16/2018 12:00:00 AM | Ocmulgee |  |  |  | 0 | Tusk Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | Removed Rotts | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-16 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-03 | 2018-05-03 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Stockbridge | 1821 Walt Stephens Road | 18900 | Fax received on 05/03/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Unknown |  |  | Hsin Yeh | Paul Moisan | 5/3/2018 12:00:00 AM |  |  |  |  | 0 | Rum Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Other | Pump flow was reestablished and flows returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-04 | 0 | 1 | 0 | 0 | 0 | 0
2016-08-11 | 2016-08-11 | Columbia County (Crawford Creek WPCP) | Columbia |  | 767 Fury's Ferry Road | 6000 | Verbal notification received 8/11/2016. WRD notified of fish kill. | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream |  | Pipe failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/11/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Jones Creek | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pipe Failure. This spill resulted in a fish kill. | Pipe repaired. WRD notified of fish kill. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | COLUMBIA COUNTY | 706.863.6928
2016-06-17 | 2016-06-18 | Marietta (City of)- Sewers | Cobb | marietta | 140 N Marietta Pkwy | 4800 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/18/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Sope Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Details in spill report | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-19 | 2015-07-20 | Dekalb County (Polebridge Creek WPCP) | DeKalb | Lithonia | 7840 Old Covington Highway, Lithonia | 3920 | Notification dated July 22, 2015, and EPD received on July 27, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0026816 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 7/22/2015 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Electrical malfunction | The problem was corrected at 14:12 hours when the crew manually turned on a pump and then made system repairs. Services were restored at that time. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2017-12-14 | 2017-12-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | atlanta | 3930 East Brookhaven Drive, Atlanta | 3440 | m/h 18-240-s084 overflowing | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream | Stream | Grease |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 12/14/2017 4:57:00 PM | Ocmulgee | 12/14/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease | pressured washed to clear blockage |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-15 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Charlene George |  | Dekalb Co Dept. Watershed Management
2015-02-08 | 2015-02-08 | Clayton County (Northeast WPCP) | Clayton | Morrow | 6220 Harvard Ct. | 4050 | REC FAX 2/10/2015 | Raw Sewage | Wastewater Regulatory Program | GA0020575 | Collection System | Stream | Stream | Grease |  |  | Emily Wingo | Emily Wingo | 2/10/2015 12:00:00 AM | Ocmulgee | 2/9/2015 12:00:00 AM |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage Follow up: will televise line and follow repairs will performed if needed |  | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-02-17 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | Clayton Co Water Authority
2017-07-26 | 2017-07-28 | Columbia County (Crawford Creek WPCP) | Columbia | Martinez | 4590 Oakley Pirkle Road - Martinez | 10000 | Email received 2017-07-28 | Raw Sewage | Wastewater Regulatory Program | GA0031984 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/28/2017 12:00:00 AM |  | 7/26/2017 12:00:00 AM | 2017-07-28 | 2018-07-31 | 1 | Crawford Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Excessive Rainfall | Monitored Area. Follow up inspection of area. Continue to look for points of inflow. Posted Signs. Began Sampling. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-07-28 | 0 | 1 | 0 | 1 | 1 | 0
2015-11-30 | 2015-11-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4748 Vermack Road, Dunwoody | 490 | Notification received on December 1, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 11/30/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:15 hours when a crew pressure washed the 8" sewer main 185" upstream, clearing the blockage and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-17 | 2017-05-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1481 Woodbine Ave. SE - ATL | 5000 |  | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 5/18/2017 12:00:00 AM |  |  |  |  | 0 | Dry Land | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was equipment failure. | Crew made repairs to the by-pass pump to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-05-23 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-27 | 2015-04-27 | Town of Thunderbolt MS4 | Chatham | Thunderbolt | 3247 Robertson Ave | 300 |  | Raw Sewage | Coastal District |  | Collection System | Other |  | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 4/27/2015 12:00:00 AM | Savannah | 4/27/2015 12:00:00 AM |  |  | 1 | Wilmington River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Force main rupture | installed earthen dam around spill, repaired sewer force main, added lime, evaluate force main for future repair/replacement | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-05-11 | 1 | 1 | 0 | 0 | 0 | 0
2017-09-23 | 2017-09-23 | Lowndes County (South Regional WPCP) | Lowndes | Valdosta | Val-Tech Road 1.2 miles south of Wiregrass Technical College - Lowndes | 25000 | Email received 2017-09-24 | Raw Sewage | Wastewater Regulatory Program | GAJ020294 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 9/24/2017 12:00:00 AM |  |  | 2017-09-25 | 2018-09-12 | 1 | Withlacoochee River | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | A split in the 16" force main that runs along Val-Tech Road. | Three pump trucks bypassed the flow as repairs were made. Lime was applied to the drainage ditch near the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-09-29 | 0 | 0 | 0 | 1 | 1 | 0
2018-03-20 | 2018-03-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 301 Wilburn St, Jonesboro | 4200 | Fax received on 03/20/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 3/20/2018 12:00:00 AM |  |  |  |  | 0 | Rum Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. Site was mitigated and work orders generated for additional work to determine the cause. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-03-20 | 0 | 1 | 0 | 0 | 0 | 0
2016-12-05 | 2016-12-07 | Albany, City of (Joshua Street WPCP) | Dougherty | Albany | Intersection of Elm & Gordon/Alley south of Gordon, Albany | 750000 | Initial email received on 12/05/2016; full report received on 12/13/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037222 | Collection System | Stream | Shoreline | Debris |  |  | Paul Moisan | Paul Moisan | 12/5/2016 12:00:00 AM |  |  |  |  | 1 | Percosin Creek tributary to Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | The cause of the spill was debris in the line, and heavy rainfall. | Jetvac was used to clean dislodge the blockage, and bypass pumps were used but were overwhelmed until the rainfall stopped. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | Jeffrey Hughes | 229-883-8998 | Albany (City of)
2016-02-01 | 2016-02-02 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1793 Briarwood Road, Brookhaven | 384 | Notification received on February 3, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 2/2/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Concrete creek crossing leaking | The problem was corrected on February 2, 2016 at 18:30 hours, when a crew built a berm around the suppoet collar with dirt to contain the spill until repair is made. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-04 | 0 | 1 | 0 | 0 | 0 | 0
2017-05-01 | 2017-05-01 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 773 Forest Pkwy, College Park | 675 | Report received on 05/04/2017. Telephone call received on 05/02/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Ground |  | 3rd party contractor |  | Paul Moisan | Paul Moisan | Paul Moisan | 5/2/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Third party contractor traveling on an acces road in an excavator made contact with the bypass sewer line. The right track of the excavator contacted the air release valve causing effluent to leave the bypass system through the two inch hole. | Effluent was removed via a vacuum truck, and lime was placed on the affected area. Concrete barricades were installed between the travel path and the roadway where air relaeas valves are located to prevent further incidents. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-05-08 | 0 | 0 | 0 | 0 | 0 | 0
2015-10-08 | 2015-10-08 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2429 Jennings Road | 2500 | fax received 10-09-2015 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Storm Drain |  | Debris |  |  | Kim Hembree | Kim Hembree | 10/9/2015 12:00:00 AM |  |  |  |  | 1 | Storm drain leading to a tributary of Rocky Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris and rags | Debris and rags removed, line resumed normal flow. Storm drains in the area were cleaned to mitigate the effects of the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-826-4792
2015-02-26 | 2015-02-27 |  | Lowndes | Valdosta | 1405 Gornto Road | 2200 | verbal and email notification received 2/26/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/26/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-26 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2018-02-22 | 2018-02-22 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 240 Franklin Road | 6900 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/22/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. The spill was stopped at 3:45 pm. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-02-26 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-10 | 2015-11-10 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Snellville | 3967 Tanglewood Road | 6300 | ERT notified 11/10/1015. CTS No. 78286 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 11/10/2015 12:00:00 AM |  |  |  |  | 1 | Jacks Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2015-01-09 | 2015-01-09 |  | Cobb |  | 4351 Clairesbrook Lane | 210 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/9/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Lake Acworth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Thie overflow occurred as a result of gravel in sewer main causing the manhole to overflow into a tributary of Lake Acworth. | The crew stoppedthe overflow at 7:15 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2820 Pierce Drive S., Macon MH ID 64565 | 1600 | Fax and email received on 12/30/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/30/2015 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the vlockage was removed, it was determined that the cause of this minor spill was grease. There are no commercial sources of grease upstream from this location and residential grease is not regulated. | Debris was removed from the area, and the affected area was disinfected with lime.This line is scheduled to be cleaned with grease emulsifier and televised. It will also be added to the weekly hot spot inspection list. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-04 | 1 | 1 | 0 | 0 | 0 | 0
2016-05-09 | 2016-05-09 | Loganville, City of (Loganville WPCP) | Walton | Loganville | Cown Drive Lift Station | 9600 | CTS No. 79796 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/10/2016 12:00:00 AM |  |  |  |  | 1 | Little Haynes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | broken main |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF LOGANVILLE
2015-02-02 | 2015-02-02 |  | DeKalb | Lithonia | 7619 Union Grove Road, Lithonia | 3465 | Notification received on February 4, 2015. | Raw Sewage | Wastewater Regulatory Program |  | WWTP | Stream |  | Vandalism |  |  | Hsin Yeh | Hsin Yeh | 2/3/2015 12:00:00 AM |  |  |  |  | 0 | Tom George Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | The problem was corrected at 1:48 hours when a crew used a goose neck in the mouth of the 10" main cleared the rock blockage and restored services. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-02-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-16 | 2017-06-16 | Cobb County Water System | Cobb |  | 350 Hartman Road | 350 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/22/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Structural Failure |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-06-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-14 | 2017-01-17 | Cobb County (Marietta Water Authority - James E. Quarles WTP) | Cobb |  | 1109 Claymore Dr. | 1200 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/14/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Rottenwood Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage and Grease | Marietta Water personnel quickly relieved the blockage by hydro jetting the sewer main thus restoring normal service. The roadway was washed down and deodorizer was applied. The sewer main will be examined by CCTV to identify any possible defects. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-15 | 2018-05-15 | Forsyth, City of (Northeast WPCP) | Monroe | Forsyth | 300 Montpelier Ave Forsyth GA | 4500 | initially thought was owned by Board of Education, but then immediately contacted EPD when clear owned by city | Raw Sewage | Wastewater Regulatory Program | GA0031801 | Collection System | Stream |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 5/17/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Slippery Rock Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Line blockage | approximately 155 linear feet of sewer line was replaced. |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-05-21 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-17 | 2015-03-17 | Etowah Water & Sewer Authority (Dawson Forest WRF) | Dawson |  | Taffer Creek Main Collection Manhole | 120000 |  | Raw Sewage | Mountain District - Cartersville | GAJ020232 | WWRF | Stream | Stream | Vandalism |  | Mansoor Alaeddini | Kathy Lewis | Mansoor Alaeddini | 3/23/2015 12:00:00 AM | Coosa |  |  |  | 0 | Taffar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A log approximately 6" in diameter and 7' long and a large tree limb were placed into a manhole. We believe this to be an act of vandalism. | Sewer line was jetted and log and limb removed. | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 45c9c4c2-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-03-24 | 0 | 0 | 0 | 0 | 0 | 0 | Tim Collins | 706-216-8474 | Etowah Water & Sewage
2016-04-13 | 2016-04-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2911 Cocklebur Road, Decatur | 20 | Notification received on April 18, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 4/13/2016 12:00:00 AM |  |  |  |  | 0 | Cobb Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:05 hours, when a crew pressured washed the private service line 85ft, cleared the blockage at 50ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-04-18 | 0 | 1 | 0 | 0 | 0 | 0
2018-07-02 | 2018-07-02 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Fern Valley Drive, Toccoa, GA | 1500 | Electronic report received on July 6, 2018. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 7/5/2018 12:00:00 AM |  |  |  |  | 0 | Ward Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Mechanical failure | Full station capabilities were restored to the station around 1:30 pm. City personnel were able to cease spillage at 9:30 am by pumping the station down. This was done by operating the station in the hand operational condition. The lift station was operated in this manner until the required component(s) could be replaces. The city will further expedite repairs by increasing the inventory of spare parts. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2018-07-09 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-04 | 2017-10-04 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forest Park | 5366 Creekview Ln, Forest Park Manhole - 22703758 | 5400 | Fax received on 10/05/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 10/5/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Upton Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Cleared blockage and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-10-06 | 0 | 0 | 1 | 0 | 0 | 0
2016-01-24 | 2016-01-24 |  | Fulton |  | 460 Elden Drive Sandy Springs 30342 | 25120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/24/2016 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-01-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-16 | 2016-03-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 354 S McDonough Street, Decatur | 700 | Notification received on March 21, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 3/16/2016 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 15:30 hours, when a crew contained the spill using the vactor, pressure washed upstream the sewer main 214ft, clearing the blockage, repair 8" sewer main and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-03-22 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | Verbal and email notification received 12/29/2015 | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 12/28/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is a major outfall spill due to a TSS violation. Date sample was taken: 12/24/2015. Reported TSS = 393 mg/l; Permit Limit = 15 mg/L. Flow volume = 91.25 MG (1:45 pm – 12:00 am) |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-03 | 2017-10-03 | Hogansville, City of (Hogansville WPCP) | Troup | Hogansville | 101 Collier Street, Hogansville, GA 30230 | 15000 | Notification received on October 5, 2017. | Raw Sewage | Wastewater Regulatory Program | GAJ020019 | WWTP | Ground |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/3/2017 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage inline causing a leak at a joint. | City crew dug a hole near a manhole and diverted the sewage to the hole and pumped the sewage back into the collection system. Lime was applied t the affected area and the hole and ditch were filled back in with dirt on the site. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-09 | 2018-08-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2640 Jonesboro Road - South River WRC - Atlanta | 31330000 | This spill is also entered as a violation. | Treated Effluent |  | GA0039012 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 8/15/2018 12:00:00 AM |  | 8/9/2018 12:00:00 AM |  |  | 1 | Chattahoochee River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | South River Major TSS Spill The 24-hour composite samples collected at South River had the following concentrations: August 10 TSS - 46 mg/L Permit Limit = 15 mg/L | Seeking additional landfill options for the removal of solids. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-22 | 0 | 0 | 0 | 0 | 0 | 1
2016-02-14 | 2016-02-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2209 Wingate Street, SW | 65 | Fax received 2/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  |  |  |  | Kim Hembree | Kim Hembree | 2/15/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-04-01 | 2018-04-01 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2499 Williamswood Court Decatur GA 30033 | 9820 | manhole 18-114-s037 | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Rags |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 4/1/2018 10:52:00 PM | Ocmulgee | 4/1/2018 12:00:00 AM |  |  | 1 | South Fork Peachtree Creek & unnamed tributary | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | rags | pressure washed main |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-04-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-06-01 | 2017-06-01 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Duluth | 3450 Venture Dr. - Duluth | 6490 | Fax received 2017-06-02 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | 3rd party contractor |  |  | Alys Hannum | Alys Hannum | 6/2/2017 12:00:00 AM |  | 6/1/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of Beaver Ruin Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Third Party Damage - Excavation/Grading | Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-06-02 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-13 | 2016-02-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1731 Pryor Road, SW | 710 | fax received 2/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/14/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-03 | 2017-02-03 | Cobb County Water System | Cobb |  | 1306 Old Powder Springs Road | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/3/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Pine Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This overflow occurred as a result of grease causing it to overflow into Pine Creek. | The Water System was notified at 4:18 p.m. and our crew stopped the overflow at 5:51 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-02-09 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-05 | 2015-01-09 |  | Terrell | Dawson | Manhole 417 & 418 Hwy 82 | 30240 | 1st notification received on 1/5/2015 by email and phone | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  |  | Sarita Banjade | Sarita Banjade | 1/5/2015 12:00:00 AM | Flint | 1/6/2015 12:00:00 AM | 2015-01-06 | 2016-01-28 | 1 | Brantley Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Section of Line Collapsed, 1.5 inches of Rainfall | 'Line was jetted twice, inspected by sewer camera. Jim Boyd Construction is on site now installing a new sewer line from manhole to manhole where sewer line collapsed. Area cleaned and limed. Creek monitoring had already started due to spill on 12/24/2014' |  | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 073cd8af-8095-429d-9136-7bfed0ac02e8 | 2015-01-13 | 1 | 1 | 0 | 1 | 1 | 0 | [8 empty] | City of Dawson | 2299954858
2017-08-27 | 2017-08-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 4901 Great Meadows Road, Lithonia | 5080 | Notification received on August 30, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 8/28/2017 12:00:00 AM |  |  |  |  | 0 | Panthers Branch | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris blockage | The problem was corrected at 23:55 hours when the crew rodded the 8-inch sewer main 222-ft, removed the blockage at 220-ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-08-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-18 | 2017-10-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 3697 Mortons Landing Drive, Ellenwood | 2640 | Notification received on October 23, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 10/18/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:50 hours when the first responder crew pressure washed the 8-inch sewer main 500-ft, clearing the blockage at 250-ft, stopping the spill and restoring normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-23 | 0 | 1 | 0 | 0 | 0 | 0
2016-05-26 | 2016-05-26 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Forrest Park | 4226 Murray Lake Circle, Forrest Park Manhole 2209496 | 1375 | Fax received on 05/26/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 5/26/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | unknown stream flowing into Murray Lake | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease. | Blockage was cleared, and flow was returned to normal. Site was cleaned and work orders generated to determine cause and televise. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-05-31 | 0 | 1 | 0 | 0 | 0 | 0
2015-01-21 | 2015-01-21 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | R.M. Clayton WRC | 0 | Voice mail notification received 1-22-2015. Email received 1-22-2015. | Treated Effluent | Wastewater Regulatory Program |  | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/22/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | This is an outfall spill from the R.M. Clayton WRC due to excessively high TSS values. The high TSS values are a result of treatment problems. Reported TSS = 108 mg/L. Volume = 69,300,000 gallons |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-12 | 2017-01-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2705 Harrington Pl, SW - ATL | 1600 | Fax received on 01/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/13/2017 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2017-11-20 | 2017-11-20 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 7334 Conkle Road - Jonesboro Manhole 2201174 | 1800 | Lines will be televised and Hydro-cleaned with De-greaser. If problem is located it will be repaired. Manhole 2201174 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | N/A | Grease |  |  | Dillon Rodenbaugh | Paul Moisan | 11/21/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Reeves Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and site remediation work orders were generated to determine cause of SSO |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-11-22 | 0 | 1 | 1 | 0 | 0 | 0 |  |  |  |  | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2015-05-12 | 2015-05-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2552 Ivydale Drive, SW | 30 | fax received 5/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 5/18/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | pump malfunction | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-13 | 2017-02-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1174 McDaniel St. SW - ATL | 10 | Fax received 2017-02-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/15/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-15 | 0 | 0 | 0 | 0 | 0 | 0
2018-05-17 | 2018-05-17 | Hall County (Spout Springs WRF) | Hall | Sterling | Off of Sleepy Lagoon in Sterling, on the Lake. | 300 | Email sent 2018-05-18 | Raw Sewage | Wastewater Regulatory Program | GA0050214 | Pump Station | Other |  | Equipment failure |  | Alys Hannum | Alys Hannum | Alys Hannum | 5/18/2018 12:00:00 AM |  |  |  |  | 1 | Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump station's transducer and backup floats failed at the same time. | Repaired. Homeowner's association informed residents. Cursory sampling of the lake for pH, DO, and fecal as a precaution. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-06-12 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-21 | 2015-04-21 | Thomaston, City of | Upson | Thomaston | 123 Kennesaw Dr., Thomaston, Georgia | 3000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/21/2015 12:00:00 AM | Flint | 4/21/2015 12:00:00 AM |  |  | 0 | Davis Hills Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill occurred due to a blockage in the sewer line. | All debris associated with the overflow has been cleaned up and the area was disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-04-22 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-03 | 2018-04-03 | Forsyth County (Fowler & Shakerag WRF) | Forsyth | Atlanta | 1278 Mountclair Dr. - Atlanta | 4000 | Email sent 2018-04-04 | Raw Sewage | Wastewater Regulatory Program | GA0038954 | Lift Station | Stream |  | Equipment failure |  |  | Alys Hannum | Alys Hannum | 4/4/2018 12:00:00 AM |  |  |  |  | 1 | James Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Leaking 6" valve @ bonnet, gasket leaking by | Diverted flow to another location, dug up and replaced 6" valve at lift station |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-20 | 2017-03-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 850 Lake Mirror Rd. SW - ATL | 266382 | Fax received 2017-03-22. Spill volume undetermined. Fax received 2017-03-20. Spill volume, affected waterbody, and correction time updated. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Alys Hannum | Alys Hannum | 3/22/2017 12:00:00 AM |  |  | 2017-03-20 | 2018-04-10 | 1 | Flint River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was a collapsed line. | Spill contained when the pump station turned the pumps off. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-23 | 0 | 0 | 0 | 1 | 1 | 0
2015-04-14 | 2015-04-14 | Savannah, City of (Georgetown WPCP) | Chatham | Savannah | 1 Fort Argyle Road - State Route 204 / I - 95 | 150 |  | Raw Sewage | Coastal District |  | WWTP | Basin | Ditch | Pipe failure |  | Steve Fox | Steve Fox | Steve Fox | 4/14/2015 12:00:00 AM | Ogeechee | 4/14/2015 12:00:00 AM |  |  | 1 | ogeechee river | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | y | 0 | Force main failure (small split) | Repaired split in force main and utilized City of Savannah Jet Vacuum Trucks to remove sewage. Spread lime on contaminated areas and samples were taken downstream from discharge. Spill notification markers were placed at the spill site. No recreational access in the area. All entities (Georgia Environmental Protection Division, Heath Dept. and media) were contacted. City of Savannah News release was sent to local Media. | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 2015-05-11 | 1 | 1 | 0 | 0 | 0 | 0
2016-02-02 | 2016-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2486 Paul Avenue, NW | 344 | fax received 2/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/3/2016 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-16 | 2015-01-16 | Cobb County MS4 | Cobb |  | 6030 River View Road | 840 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 1/16/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow occurred as a result of solids in sewer main causing the manhole to overflow into a tributary of Chattahoochee River. | The spill was stopped at 12:30 p.m. | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-29 | 2016-02-29 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3390 Fairburn Road, SW | 864 | fax received 3/01/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 3/1/2016 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-05-18 | 2017-05-18 | Savannah, City of (President Street WRF) | Chatham | Savannah | Paulsen St and East Waldburg St, Savannah, GA | 940 | Initial call and full report received via email 5/19/17. | Raw Sewage | Coastal District | GA0025348 | Collection System | Storm Drain, Stream | Stream | Unknown |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 5/19/2017 12:00:00 AM | Savannah | 5/18/2017 12:00:00 AM |  |  | 1 | Savannah River | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Exact cause of overflow unknown. Line is being televised to determine exact cause of blockage. | Bypassed sewer main to stop discharge. Vac truck cleaned area. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-05-19 | 0 | 1 | 0 | 0 | 0 | 1 | [8 empty] | CITY OF SAVANNAH | 912-651-6585
2015-12-31 | 2015-12-31 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 500 Dairy Pak Rd., Athens | 3155 | Initial email 12/31, full report faxed 1/6 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Other |  | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/7/2015 12:00:00 AM | Oconee | 12/31/2015 12:00:00 AM |  |  | 1 | wetlands to North Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Manhole overflowed during flood event | Vac truck cleaned the area of solids, and captured much of the spill before it reached the wetlands. |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2016-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-04-03 | 2017-04-03 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 1360 Pleasant Grove Drive | 5235 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Debris |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/4/2017 12:00:00 AM | Coosa |  |  |  | 0 | Schwab Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in sewer main | The blockage was cleared manually and with the use of a high pressure jet. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-04-05 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-30 | 2016-10-30 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 5547 Roberts Drive, Dunwoody | 4260 | Notification received on November 1, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Roots |  |  | Hsin Yeh | Hsin Yeh | 10/30/2016 12:00:00 AM |  |  |  |  | 0 | Ball Mill Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots | The problem was corrected at 15:10 hours, when a crew rodded the manhole 36ft, cleared the root blockage at 30, pressure washed the 8" main downstream for extra cleaning and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-11-01 | 0 | 1 | 0 | 0 | 0 | 0
2015-05-14 | 2015-05-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1455 English Street, NW | 1410 | fax received 5/15/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/15/2015 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline. | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-02-06 | 2015-02-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 337 Elizabeth Street, NE | 100 | email received 2/07/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/7/2015 12:00:00 AM |  |  |  |  | 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-06-15 | 2017-06-15 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 1000 Montreal Road RE., Clarkston | 17220 | Notification received on June 19, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 6/15/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:01 hours when the crew pressure washed the 8" sewer main 220ft, cleared the grease blockage at 220ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-06-20 | 0 | 1 | 0 | 0 | 0 | 0
2017-03-18 | 2017-03-18 | Fulton County (Big Creek WPCP) | Fulton | Sandy Springs | 1165 Perimeter Center West Sandy Springs, 30328 | 77400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024333 | Collection System |  |  | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/17/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Nancy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The manhole and sewer lines have been cleaned. The section of the system is being inspected to ensure conditions that may create future overflows have been mitigated. The area impacted by the spill is in the process of being cleaned. Inhibitors were applied to minimize odors. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-29 | 2016-03-29 | Dalton Utilities (Riverbend WPCP) | Whitfield |  | 309 Elk Street | 150 |  | Raw Sewage | Mountain District - Cartersville | GAJ020056 | WWTP | Stream |  | Roots |  | Kevin Dallmier | Kathy Lewis | Kevin Dallmier | 3/29/2016 12:00:00 AM | Coosa |  |  |  | 0 | Hamilton Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Roots infiltrating pipe/debris blockage | Dalton Utilities used a jet to clear the blockage and will also implement root control procedures in the area | 4600434e-eb6e-11e0-b8d8-000c29971acc | 4600434e-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-03-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-04 | 2016-02-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 1300 Block of North Lee Street | 38125 | Verbal/Email notification received 2/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Wet weather |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/5/2016 12:00:00 AM |  |  |  |  | 1 | One Mile Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2015-11-12 | 2015-11-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4280 Celebration Drive, SW | 5000 | fax received 11/14/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 11/14/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed a point repair to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-22 | 2015-12-22 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Ronthor Drive and Fairplay Drive - Manhole No. 1134 | 1500 | fax received 12/23/2015 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 12/23/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Cleared debris with jet machine. lime applied to site |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2016-09-09 | 2016-09-09 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Lawrenceville | 439 Northdale Road | 1239 | fax received 9/09/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 9/9/2016 12:00:00 AM |  |  |  |  | 1 | Redland Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Repair crews exposed the broken VCP main and made necessary repairs. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-09-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY
2016-11-13 | 2016-11-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1010 E. Rock Springs, Rd, NE, Atlanta | 25 | Fax received on 11/14/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/14/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-16 | 2016-01-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 526 Ross Street, SW | 700 | fax received 1/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/17/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-01-23 | 2018-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1000 Harwell Rd. NW - ATL | 572 | Fax sent 2018-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 1/24/2018 12:00:00 AM |  | 1/23/2018 12:00:00 AM |  |  | 1 | Sandy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-26 | 2017-11-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4353 Kimball Rd. SW - ATL | 2400 | Fax sent 2017-11-27 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 11/27/2017 12:00:00 AM |  | 11/26/2017 12:00:00 AM |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to control the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-25 | 2018-07-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1280 Oakland Dr. SW - Atlanta | 30 | Fax sent 2018-07-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Grease |  |  | Alys Hannum | Alys Hannum | 7/26/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and debris in the mainline | Spill was self-contained |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2015-03-12 | 2015-03-16 | Manchester, City of (Rush Creek Reservoir WTP) | Meriwether | Manchester | East Perry Street at the Dead End, Manchester, GA | 126000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 3/12/2015 12:00:00 AM | Flint | 3/17/2015 12:00:00 AM | 2015-03-17 | 2016-05-25 | 1 | tributary to Pigeon Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Grease and Debris Blockage | Cleared blockage | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-03-19 | 0 | 1 | 0 | 1 | 1 | 0
2015-02-17 | 2015-02-17 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 2874 Rivermeade Drive, NW | 441 | fax received 2/18/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 2/18/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew performed point repairs to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-12 | 2017-01-12 | Thomaston, City of | Upson | Thomaston | Bell Creek WPCP | 750 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/12/2017 12:00:00 AM | Flint |  |  |  | 0 | bell creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | Debris was removed and cleaned. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-01-19 | 0 | 0 | 0 | 0 | 0 | 0
2017-05-22 | 2017-05-22 | Forsyth County (The Manor WRF) | Forsyth |  | 3294 Watson's Bend Alpharetta | 9103 | Being handled by EECO - E Dykes | Raw Sewage | Mountain District - Cartersville | GA0050244 | WWRF | Stream |  | Equipment failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 5/25/2017 12:00:00 AM | Coosa |  |  |  | 0 | Tributary of Chicken Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Programming failure, subsequent overflow of influent pump station structure. Facility went into backwash sequence that attempted to simultaneously backwash two process trains although only being capable of completing one train at a time. This prevented influent from being pumped into the facility for the duration of this sequence until being manually corrected by the plant operator. | Programming will be modified to provide an interlock that will disallow the facility logic to attempt to backwash two membrane trains simultaneously. Alarm definitions will be updated in programming to provide notification to on call operators and supervisor. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-05-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-22 | 2017-02-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 19 Arlington Dr. NW - ATL | 50 | Fax received 2017-02-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/23/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-03 | 2016-05-03 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 4345 Kimball Road, SW | 750 | fax received 5/04/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/4/2016 12:00:00 AM |  |  |  |  | 1 | Camp Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-07-21 | 2018-07-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1475 Mecaslin St. NW - Atlanta | 3000 | Fax sent 2018-07-22. Corrections sent 2018-07-23 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Equipment failure |  |  | Alys Hannum | Alys Hannum | 7/22/2018 12:00:00 AM |  | 7/21/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | By-pass pump malfunction | Crew made repairs to the by pass pump. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-04 | 2016-08-04 | Valdosta, City of (Withlacoochee WPCP) | Lowndes | Valdosta | 900 Block of Madison Avenue | 3300 | verbal notification received 8/05/2016 | Raw Sewage | Wastewater Regulatory Program | GA0033235 | Collection System | Stream |  | Grease |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/5/2016 12:00:00 AM |  |  |  |  | 1 | Knights Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8 ft. grease blockage. | Cleared blockage | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF VALDOSTA
2016-01-13 | 2016-01-19 | Tifton, City of (New River WPCP) | Tift | Tifton | Manhole located in the backyard of 1440 Larkin Ave., Tifton | 201600 | Voice mail and email received on 01/19/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | Collection System | Ditch | Ditch | Rags |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/19/2016 12:00:00 AM |  | 1/19/2016 12:00:00 AM | 2016-01-20 |  | 1 | New River Basin | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was due to cloth rags being disposed of in the sanitary sewer. | Hydrated lime was spread to mitigate and sanitize the affected land. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-20 | 0 | 1 | 0 | 1 | 1 | 0
2017-12-09 | 2017-12-10 | Douglasville, City of (South Central WPCP) | Douglas | Douglasville | 3507 Meadowview Dr., Lithia Springs Meadowfiew Lift Station | 57000 | Email and fax received on 12/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038709 | Lift Station | Stream |  | Power failure |  |  |  | Paul Moisan | 12/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 1 | Dry Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Snow storm caused widespread power outages throughout Douglas County. The area around this lift station was without power for 24 houors. | Restoration of power allowed the pump station to resume pumping and stopped the spill |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-12-12 | 0 | 1 | 0 | 0 | 0 | 0 | Lyndsey Sargent | 770-949-7617 | Douglasville-Douglas County Water and Sewer Authority
2015-04-14 | 2015-04-15 |  | Emanuel | Swainsboro | Manhole near Lift Station No. 12 | 6000 | Verbal notification from the City received 4/15/215. Email confirmation of the spill received 4/15/2015. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Storm Drain |  | Power failure |  | Kim Hembree | Kim Hembree | Kim Hembree | 4/15/2015 12:00:00 AM |  |  |  |  | 1 | Storm Drain to Lake Luck | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The breaker for Lift Station No. 12 was tripped and the pumps turned off. The City is still investigating why the breaker tripped. | Pumps were turned back on. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-04-16 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SWAINSBORO
2017-04-21 | 2017-04-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3136 Martin L. King Jr. Dr. SW - ATL | 6330 | Fax received 2017-04-24 | Raw Sewage | Wastewater Regulatory Program | GA0039012 |  | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 4/24/2017 12:00:00 AM |  | 4/21/2017 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-04-25 | 0 | 0 | 0 | 0 | 0 | 0
2016-09-30 | 2016-09-30 | Chatsworth, City of (Judson Vick WPCP) | Murray |  | 1890 Duvall Road, Chatsworth | 7358 |  | Raw Sewage | Mountain District - Cartersville | GA0032492 | WWTP | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 10/1/2016 12:00:00 AM | Coosa |  |  |  | 0 | Mill Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A line failure on the 8 inch PVC force main leaving the Highway 411 Lift Station | Repairs were initiated immediately and vacuum trucks were utilized for pumping and hauling. | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2016-11-14 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-06 | 2017-10-06 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Rosedale Street, Toccoa | 500 | Notification received through fax on October 11, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP | Stream |  | Natural Disaster |  |  | Hsin Yeh | Hsin Yeh | 10/9/2017 12:00:00 AM |  |  |  |  | 0 | Toccoa Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Tree fallen across a sewer main. | City stopped the leak and pipe was repaired at 8:20 PM on October 6, 2017. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-12 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-09 | 2015-11-09 | Woodstock, City of (Rubes Creek WPCP) | Cherokee |  | Springfield Park | 2100 |  | Raw Sewage | Mountain District - Cartersville | GA0026263 | WWTP | Stream |  | Debris |  | Ebony Johnson | Kathy Lewis | Ebony Johnson | 11/9/2015 12:00:00 AM | Coosa |  |  |  | 0 | Rubes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | unknown obstruction in line | Jetted line to clear obstruction, vacuumed up as much sewage as possible and limed affected area. CCTV Inspection revealed a piece of PVC in the line. | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 0d8395d2-67c5-4815-8244-e3d9adcdaa41 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Hooper | 770-592-6006 | CITY OF WOODSTOCK
2017-12-06 | 2017-12-06 | Cobb County Water System | Cobb |  | 2498 Bay Berry Dr. | 170 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/6/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Olley Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water System was notified at 12:37 p.m. and the crew stopped the overflow at 1:45 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-06 | 0 | 0 | 0 | 0 | 0 | 0
2015-09-18 | 2015-09-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1600 Carlisle Street, NW | 160 | fax received 9/20/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Unknown |  |  | Kim Hembree | Kim Hembree | 9/20/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-02-11 | 2016-02-11 | Hazlehurst, City of (Bully Creek WPCP) | Jeff Davis | Hazlehurst | Manhole at Cloversett Apartments. | 27000 |  | Raw Sewage | Coastal District | GA0036765 | Collection System |  | Ditch | Hydraulic Overload |  | Bill Hawthorne | Bill Hawthorne | Bill Hawthorne | 2/4/2016 8:45:00 AM | Ocmulgee | 2/4/2016 12:00:00 AM | 2016-02-04 |  | 1 | Ocmulgee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Heavy rainfall over-loaded several lift stations causing a manhole to overflow. | Keep lift stations pumping at full capacity. | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 2016-02-11 | 1 | 1 | 0 | 0 | 0 | 0
2018-01-26 | 2018-01-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 50 | occurred on Snapfinger WPCP | Unknown | Wastewater Regulatory Program | GA0024147 | Collection System | Storm Drain |  |  |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 1/26/2018 10:26:00 PM | Ocmulgee |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vactor overfilled causing sewer to spill out of defective pipe on truck, spilled into storm drain and entered retention pond | Drained vactor down to stop spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-01-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-16 | 2016-03-16 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | Railroad Lift Station | 30 | verbal notification received 3/17/2016 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System | Ground |  | Debris |  | Kim Hembree | Kim Hembree | Kim Hembree | 3/17/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | Cleared blockage | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF SOCIAL CIRCLE
2017-04-08 | 2017-04-08 | Chatsworth, City of (Judson Vick WPCP) | Murray |  | 1890 Duvall Road Chatsworth | 1661 |  | Raw Sewage | Mountain District - Cartersville | GA0032492 | WWTP | Stream |  | Pipe failure |  | Tracy Feltman | Kathy Lewis | Tracy Feltman | 4/9/2017 12:00:00 AM | Coosa |  |  |  | 1 | MIll Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failure of Sewer Force Main | Repairs were started immediately and vacuum trucks were used for pumping and hauling | beec5611-d9d5-4915-abe3-0869ce733561 | beec5611-d9d5-4915-abe3-0869ce733561 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-06 | 2016-12-06 | Thomaston, City of | Upson | Thomaston | Pine Lake Drive | 2000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 12/6/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Town Branch/Pine Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and roots. | This lined is scheduled to be cleaned and televised. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-12-13 | 0 | 0 | 0 | 0 | 0 | 0
2017-07-25 | 2017-07-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3714 Roswell Rd. NE - ATL | 100 | Fax received 2017-07-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 7/26/2017 12:00:00 AM |  | 7/25/2017 12:00:00 AM |  |  | 1 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-20 | 2018-07-20 | Macon Water Authority (Rocky Creek WPCP) | Macon | Macon | 1701 Walnut Street, MH ID 66937 | 7625 |  | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Hydraulic Overload |  |  | Juan Robles |  | 7/20/2018 12:00:00 AM |  |  |  |  | 0 | Vineville Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Hydraulic overload due to heavy rains. | MWA Sewer Conveyance crews increased the pumping speed and the manhole stopped overflowing. |  |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-12 | 2017-09-12 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 113 Ingleside Dr., Jonesboro | 1800 | Fax received on 09/12/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 9/12/2017 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Rum Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Pipe failure. | Repaired line - performed temporary point repair and return flow to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-09-13 | 0 | 1 | 1 | 0 | 0 | 0 | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2016-12-06 | 2017-12-06 | Cobb County Water System | Cobb |  | 154 Silver Mine Trail | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/24/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The Water system was notified at 9:34 p.m. and the Cobb Crew stopped the over flow at 10:17 p.m. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-12-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-16 | 2016-01-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Dunwoody | 4051 Candler Lake West, Dunwoody | 7350 | Notification received on January 19, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/16/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 16:45 hours, when a crew pressure washed the 10" sewer main 200ft, cleared the grease blockage and restored flow to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2015-04-06 | 2015-04-06 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 680 New Town Circle, SE | 220 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 4/7/2015 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-10-14 | 2017-10-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3604 N. Stratford Rd. NE - ATL | 1360 | Email sent 2017-10-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 10/15/2017 12:00:00 AM |  | 10/14/2017 12:00:00 AM |  |  | 1 | Proctor Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2018-08-07 | 2018-08-07 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2900 Landrum Dr. SW - Atlanta | 3120 | Fax sent 2018-08-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 8/8/2018 12:00:00 AM |  | 8/7/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-21 | 2018-07-21 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | 2582 Spring Cast Dr. - Buford | 1268 | Fax sent 2018-07-22 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Force Main | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/22/2018 12:00:00 AM |  | 7/21/2018 12:00:00 AM |  |  | 1 | Unnamed Trib. of Sherwood Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Cracked Force main | Repairs made. Raked area and spread lime. Placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-24 | 2016-04-25 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 2936 Bicketts Ridge, Macon GM ID 17991 | 3240 | Email received on 04/27/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Shoreline | Pipe failure |  |  | Paul Moisan | Paul Moisan | 4/27/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Bowman Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken sewer main. | Debris was removed from the area, and the affected area was disinfected with lime. The repair was made to the line. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-28 | 0 | 1 | 0 | 0 | 0 | 0
2017-09-18 | 2017-09-18 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2786 Pontiac Circle, Atlanta | 18000 | Notification received at September 21, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 9/18/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Storm event / I&I | The problem was corrected September 14, 2017 at 11:30 hours when the crew placed a full circle clamp around the 10-inch creek crossing line, until permanent repairs can be made by contractors. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-09-22 | 0 | 1 | 0 | 1 | 0 | 0
2018-07-27 | 2018-07-27 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1055 Fairburn Rd. SW - Atlanta | 935 | Fax sent 2018-07-30 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Pipe failure |  |  | Alys Hannum | Alys Hannum | 7/30/2018 12:00:00 AM |  | 7/27/2018 12:00:00 AM |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | Crew made repairs to the mainline to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-31 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-16 | 2017-08-16 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1600 Kissingbower Rd. (#M0247) - Augusta | 2940 | Email received 2017-08-18 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Contractor |  |  | Alys Hannum | Alys Hannum | 8/18/2017 12:00:00 AM |  |  |  |  | 1 | Tributary to Raes Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The overflow was caused by a contractor cleaning sewer gravity mains. When the contractors were attempting to remove a large root ball, a large portion of the root ball fell back into the manhole, flowing down the pipe, creating a blockage. | Utilities C&M was contacted. The sewer gravity main was augered combined with other efforts in order to remove the root ball from the sewer gravity main and manhole. Lime was spread in the affected area. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-08-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 19 Cannon Drive (Manhole #1391) - Social Circle | 200 | Fax received 2017-01-24 | Raw Sewage | Wastewater Regulatory Program | GA0026107 | Collection System |  |  | Debris |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/23/2017 12:00:00 AM |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Paper blockage | Cleaned blockage with jet machine. Lime applied to spill site. Signs posted and proper agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2018-06-16 | 2018-06-16 |  | Douglas | Douglasville | WSA Sewer Line 8612-4165 Prestley Mill Rd, Douglasville, GA 30135 | 900 |  | Raw Sewage |  |  | Collection System | Stream | Stream | Pipe failure |  |  | Juan Robles | Juan Robles | 6/16/2018 12:00:00 AM |  |  |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Crack in bottom of aerial ductile iron sewer line. | Crews were dispatched and installed a temporary wrap around the repair. A permanent repair is underway. Crews cleaned and disinfected the area. Signs were posted. Notification given to Health Department and local media. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-29 | 0 | 1 | 0 | 0 | 0 | 0
2018-05-14 | 2018-05-14 | Cobb County Water System | Cobb |  | 4863 Wilkie Way | 120 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | ADMINTEST ADMINTEST | Reginald Williamson | Reginald Williamson | 5/14/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Clark Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Stopped spill and jet cleaned line and spread lime | 818e42fa-456d-4a87-86dd-1c458efac1b0 | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-25 | 2018-06-25 | Cobb County Water System | Cobb |  | 3040 Wayward Drive | 260 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 6/25/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Morgan Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-22 | 2016-01-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 75 Abington Court, NW | 25 | fax received 01/23/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/23/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to remove the blockage. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-04-29 | 2015-04-29 | Cochran WPCP | Bleckley | Cochran | Cochran WPCP. | 0 |  | Secondary Effluent | Wastewater Regulatory Program | GA0032107 | WWTP | Stream |  | Equipment failure |  |  | Paul Moisan | Paul Moisan | 5/15/2015 12:00:00 AM | Ocmulgee |  |  |  | 1 | Jordon Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Equipment failure at facility caused daily effluent TSS to be 34.4 mg/L on 04/29/2015. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 0 | 0 | 0 | 0 | 0 | 0
2015-01-04 | 2015-01-04 | CITY OF ATLANTA - SOUTH RIVER WRC | Fulton | Atlanta | Intrenchment Creek WRC, 1510 Key Road SE, Atlanta | 716240 | ERT contacted 1/04/2015. CTS Nos. 75614 and 75615. According to Kris Garcia, two overflows occurred within two hours of each other. This is why the spill was reported twice to ERT. Total volume = 716,240 gallons. | Raw Sewage | Wastewater Regulatory Program |  | WWRF | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 1/4/2015 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Overflow occurred from the Intrenchment Creek WRC, which is permitted under the City of Atlanta South River WRC, GA0039012. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-14 | 2017-02-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 2135 American Industrial Way, Chamblee | 2580 | Notification received on February 15, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 2/14/2017 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 13:34 hours when the crew pressure washed the 8" sewer main 60ft between manholes, cleared the blockage at 59ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-02-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-02-17 | 2017-02-18 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1249 Donald Lee Hollowell Pkwy. NW - ATL | 25 | Fax received 2017-02-20 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/20/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-20 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-21 | 2016-01-21 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 1179 Matthews Place, Macon MH # 20207 | 1200 | Fax received on 01/22/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream |  | Equipment failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/22/2016 12:00:00 AM | Upper Ocmulgee |  |  |  | 1 | Sabbath Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this spill was a washed out exposed sewer main. | The sewer main was replaced, and sewage is no longer escaping. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-25 | 1 | 1 | 0 | 0 | 0 | 0
2017-07-13 | 2017-07-13 | Dallas, City of (Pumpkinvine Creek WPCP) | Paulding |  | Butler Industrial Drive | 4950 |  | Raw Sewage | Mountain District - Cartersville | GA0039241 | WWTP | Stream |  | Equipment failure |  | Eric Dykes | Kathy Lewis | Eric Dykes | 7/14/2017 12:00:00 AM | Coosa |  |  |  | 0 | Griffin Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Customers back flow assembly service lid not properly affixed to the back flow body | City crews cleaned the entire area affected by spill. City crew is working now to camera the effected line to check conditions. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-08-07 | 0 | 0 | 0 | 0 | 0 | 0
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 377 Lawton Street, SW | 300 | fax received 11/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Hydraulic Overload |  |  | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-16 | 2015-09-16 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 2201 Briarcliff Road, Atlantqa | 7752 | Notification received on September 18, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/17/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Broken main | The problem was corrected at 22:45 hours, when the vactor truck crew vacuum the sewer main upstream, contain the spill and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-04-20 | 2018-04-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1176 Chattahoochie Av. NW - Atlanta | 1 | Fax sent 2018-04-21 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Ground |  | Unknown |  | Alys Hannum | Alys Hannum | Alys Hannum | 4/21/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Unknown; this is not a city problem. | None; this is not a city problem. | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-04-24 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-19 | 2016-01-19 | Columbus Water Works (South WRF) | Muscogee | Columbus | 29th Ave at Clover Lane | 100 | Voice mail received on 01/19/2016. Fax and email received on 01/20/2016. | Raw Sewage | Wastewater Regulatory Program | GA0020516 | Collection System | Stream |  | Pipe failure |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/19/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Bull Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | A split in the pipe at the bell connection caused a drip into Bull Creek. | Once the pipe was repaired, the overflow stopped. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-20 | 0 | 1 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Jonesboro | 805 Jester's Lake Drive, Jonesboro | 280500 | Fax received on 12/28/2015 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 12/28/2015 12:00:00 AM | Flint | 12/25/2015 12:00:00 AM |  |  | 1 | Jester's Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | Inflow/Infiltration. | Multiple lines will be inspected for source of inflow and infiltration to resolve capacity issues. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2015-12-28 | 0 | 1 | 1 | 0 | 0 | 0
2015-02-26 |  | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Legion Drive Lift Station in Eastman, GA. | 0 |  | Raw Sewage | Southwest District | GA0046485 | Lift Station | Ground, Stream | Stream | Wet weather |  | Jay Howell | Jay Howell | Jay Howell | 2/26/2015 10:00:00 AM | Ocmulgee | 2/26/2015 12:00:00 AM |  |  | 1 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall and I & I in collection system. |  | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2015-03-03 | 1 | 1 | 0 | 0 | 0 | 0
2015-05-04 | 2015-05-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1350 Tower Hill Street | 8500 | ERT contacted 5/04/2015. CTS No. 76654 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 5/4/2015 12:00:00 AM |  |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Damaged sewer line |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-31 | 2015-12-31 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 6790 Browns Mill Lake Road, Lithonia | 1640 | Notification received on January 5, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/31/2015 12:00:00 AM |  |  |  |  | 0 | Browns Mill Lake | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | The problem was corrected at 09:58 hours, when a crew rodded the sewer main 188' downstream and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-01-05 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellenwood GA 30294 | 450 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 2/6/2018 5:53:00 PM | Ocmulgee |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm event | Check vault when storm event was over to find that the sewer succeeded and stopped the spill |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-02-07 | 0 | 0 | 0 | 0 | 0 | 0
2016-12-15 | 2016-12-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 174 Moury Ave. SW, ATL | 3555 | Fax received on 12/16/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/16/2016 12:00:00 AM |  |  |  |  | 1 | South River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-12-19 | 0 | 0 | 0 | 0 | 0 | 0 | James Mitchell | 678-414-2466 | ATLANTA, CITY OF
2017-01-02 | 2017-01-03 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | Virginia & Coleman - Augusta | 246000 | Fax received 2017-01-03, update received 2017-01-10 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Hsin Yeh | 1/3/2017 12:00:00 AM |  | 1/3/2017 12:00:00 AM | 2017-01-05 |  | 1 | Tributary to Mid-City | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | System surcharge due to flash flooding caused highly diluted wastewater to begin running out of several manholes by 11:00 AM on January 2, 2017. | Line is being monitored until normal flow resumes. Notifications posted. |  | d80f500b-2416-4653-adb7-23760952ef3b | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-20 | 0 | 0 | 0 | 0 | 0 | 0
2018-09-09 | 2018-09-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1300 Joseph E Boone Blvd - Atlanta | 5 | Fax sent 2018-09-10 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 9/10/2018 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-09-11 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-29 | 2016-01-04 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | Behind 1854 Canterbury Rd., Macon GM ID # 7338 | 774000 | Fax and email received on 01/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Ditch |  | Hydraulic Overload |  | Paul Moisan | Paul Moisan | Paul Moisan | 1/1/2016 12:00:00 AM | Upper Ocmulgee | 12/29/2015 12:00:00 AM | 2015-12-29 | 2016-11-28 | 1 | Ditch feeding Rocky Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of this spill was hydraulic overload and a broken sewer main. MWA service area received 12.62 inches of rain for the month of December 2015. | Debris was moved from the area and area was disinfected with lime. After the water in the drainage ditch receded, it was discovered that the sewage was escaping through a broken sewer main. A contractor was called to make the repair and a by-pass was set up. MWA will continue its search for inflow and infiltration into its sewer system through its CCTV and flow monitoring investigations and will develop rehabilitation projects based on this information and contractor conducted sewer evaluations. | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-01-07 | 1 | 1 | 0 | 1 | 1 | 0 | Anthony Hopkins |  | MACON WATER AUTHORITY
2016-10-15 | 2016-10-15 | Columbia County (Crawford Creek WPCP) | Columbia | Evans | 899 Fury's Ferry Road, Evans, GA 30809 | 9000 |  | Raw Sewage | Wastewater Regulatory Program | GA0031984 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Kim Hembree | 10/16/2016 12:00:00 AM |  |  |  |  | 0 | Jones Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Split in force main | Repaired split by replacing a section of pipe. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2015-07-24 | 2015-07-24 | Rockdale County (Almand Branch WPCP) | Rockdale |  | 1201 Old Covington Hwy | 2240 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/24/2015 12:00:00 AM | Ocmulgee |  |  |  | 0 | Boar Tusk Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Damage Manhole | Repair Manhole | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-07-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-21 | 2016-03-21 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 4080 | fax received 3/22/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Kim Hembree | Kim Hembree | 3/22/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Collapsed mainline | The crew used construction material to repair the pipe |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-24 | 2015-12-24 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 161 Hood Circle, Decatur | 5000 | Notification received on December 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/24/2015 12:00:00 AM |  |  |  |  | 0 | Sugar Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 14:56 hours, when the rain subsided and returned to normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-11-04 | 2017-11-04 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 2419 Greenway Decatur GA 30035 | 1140 | Unable to pressure wash 5 feet past manhole 15-131-s077 Four notices placed on site | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Debris |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 11/4/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Cobbs Creek | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rocks at bottom of invert, restricting flow | Pressure washed sewermain |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2017-12-04 | 0 | 1 | 0 | 0 | 0 | 0 | Joseph Sims |  | Dekalb County Department of Watershed Management
2018-04-26 | 2018-04-26 | Fulton County (Big Creek WPCP) | Fulton | Roswell | 835 Roswell Creek Circle Roswell, 30076 | 3720 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Vandalism |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 4/26/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Big Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Vandalism | Remove debris, video inspecte and secure ring and covers. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-04-30 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-17 | 2018-07-17 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Morrow | 460 Mai Street (manhole 230282204) | 4600 |  | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Stream | Grease |  |  | Juan Robles | Juan Robles | 7/18/2018 12:00:00 AM | Ocmulgee | 7/18/2018 12:00:00 AM |  |  | 0 | Poole Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage due to grease. | Blockage was cleared. Lines will be televised and degreaser applied. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-07-18 | 0 | 1 | 0 | 0 | 0 | 0
2016-04-09 | 2016-04-09 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 48 Warren Street, NE | 896 | Fax received 4/10/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/10/2016 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-22 | 2016-06-22 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 234 Washington Street, SW | 25 | fax received 6/23/2016. fax states "The spill has not been contained." | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 6/23/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-06-01 | 2016-06-01 | Pembroke, City of (Pembroke WPCP) | Bryan |  |  | 6000 |  | Raw Sewage | Coastal District | GA0038377 | Lift Station | Stream | Stream | Power failure |  | Beth Stevenson | Cliff Swiger | Cliff Swiger | 6/1/2016 10:00:00 AM | Ogeechee | 6/1/2016 12:00:00 AM | 2016-06-01 |  | 1 | Mill Creek to Ogeechee River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 67692807-818f-496b-9fb6-018f0decdb42 | 67692807-818f-496b-9fb6-018f0decdb42 | 2016-06-02 | 1 | 1 | 0 | 0 | 0 | 0
2015-07-23 | 2015-07-23 | Savannah, City of (President Street WRF) | Chatham |  |  | 7800 | Estimated discharge: 40gpm x 195 mins=7800 gallons | Raw Sewage | Coastal District | GA0025348 | Collection System | Ground, Storm Drain | Canal | Roots |  | Beth Stevenson | Beth Stevenson | Steve Fox | 7/24/2015 8:00:00 AM | Savannah |  |  |  | 1 | Musgrove Canal | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Force main failure caused by roots of a large pine tree. | Turned stations off and utilized both City contracted and City of Savannah jet-vacuum trucks to handle sewage flows coming into lift station to stop flow through the force main; blocked traffic on I-16 east bound ramp at Chatham Pkwy; removed and cut down pine tree, excavated and repaired force main. Blocked flows to the storm main that drains eventually to the Musgrove Canal to the Springfield Canal with sand bags on Chatham Center Drive and bypassed flows from storm system to City of Savannah sanitary sewer collection system. Spill notifications will be placed at spill site and at storm system drainage system to lake at 2003 Chatham center Drive. GAEPD, Health Dept., and City Public Information Office contacted. | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | a102bbee-93cc-11e1-9b1d-12313d2b7a91 | 646e0b4d-944a-4ad1-9a8d-d0953fcfd6ea | 2015-07-24 | 1 | 1 | 0 | 0 | 0 | 0
2015-12-08 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Intrenchment Creek WRC | 22500 | Verbal notification received 1/06/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 1/6/2016 12:00:00 AM |  |  |  |  | 1 | Intrenchment Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Outfall No. 3 plug failure. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-20 | 2017-07-20 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Norcross | 1700 Treehouse Pkwy - Norcross | 4498 | Fax received 2017-07-21 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream | Stream | Grease |  |  |  | Alys Hannum | 7/21/2017 12:00:00 AM |  | 7/20/2017 12:00:00 AM |  |  | 1 | Unnamed Tributary of North Fork Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease, Debris | Raked area and spread lime, placed signs at spill and waterway. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d |  | 2017-07-21 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-20 | 2016-03-20 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 225 Huntington Road, NE | 2450 | fax received 3/21/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 3/21/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | Replaced the equipment on the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-06-11 | 2018-06-11 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1615 Melanie Court Decatur GA 30032 | 13449 | manhole 15-184-s004 spilling | Raw Sewage | Wastewater Regulatory Program | GA0024147 | Collection System | Stream |  | Wet weather |  |  | Dillon Rodenbaugh | Dillon Rodenbaugh | 6/12/2018 12:00:00 AM | Ocmulgee |  |  |  | 1 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm event | Wait until storm event passed |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-06-14 | 0 | 0 | 0 | 0 | 0 | 0
2015-05-14 | 2015-05-14 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 190 5th Street, NW | 243 | fax received 5/14/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Ground |  | Grease |  |  | Kim Hembree | Kim Hembree | 5/14/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-01-25 | 2017-01-26 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3310 W Roxboro Rd NE - ATL | 5568 | Fax received on 01/27/2017. Update received 2017-02-07 Update 2017-11-14: Spill volume updated from 3204 to 5568. Spill date updated from Jan 26 to Jan 25. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/27/2017 12:00:00 AM |  |  | 2017-01-27 |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | the cause of the spill was a partially collapsed mainline. | Construction section made a point repair to contain the spill at 1:40 PM on 2017-01-27. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-30 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-23 | 2016-08-23 | Thomaston, City of | Upson | Thomaston | 107 Avenue N. | 1270 |  | Grease Washwater | Wastewater Regulatory Program |  |  | Stream | Stream | Debris |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/23/2016 12:00:00 AM | Flint |  |  |  | 0 | Bell Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the overflow was grease. | Debris will beremoved from the surronding area and the area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2018-06-24 | 2018-06-24 | Cobb County Water System | Cobb |  | 359 Farm Place Ct NE | 140 |  | R-2 Water | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 7/24/2018 12:00:00 AM | Chattahoochee |  |  |  | 0 | Noonday Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2018-07-03 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-25 | 2015-12-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Tucker | 2803 Henderson Road, Tucker | 7440 | Notification received on December 28, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 12/25/2015 12:00:00 AM |  |  |  |  | 0 | Lake Erin | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 18:50 hours, when a crew pressure washed the 8" sewer main 300ft, clearing the blockage and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-29 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-04 | 2016-05-04 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 39 Rogers Street, NE | 895 | fax received 5/06/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/6/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-01-23 | 2015-01-23 |  | Turner | Ashburn | Rockhouse Road and Sylvia Dr. | 90000 | Stream sampling of Hat Creek has begun. | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 1/23/2015 12:00:00 AM | Suwannee |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The heavy flows were caused by a 3.0 inch rain and saturated soils across the collection system. |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-01-27 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1219 Hill Street, SE | 900 | fax received 2/25/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/25/2016 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | debris and collapsed mainline | The crew used a hydraulic pressure cleaner to contain the spill |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-02-06 | 2017-02-06 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2304 Ewing St. SW - ATL | 15 | Fax received 2017-02-07 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Operator error |  |  | Alys Hannum | Paul Moisan | 2/7/2017 12:00:00 AM |  |  |  |  | 0 | Did not reach State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by the city crew jet rodding the mainline. | The site has been cleaned |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-08 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-12 |  | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | Winn Park | 0 | EPD notified by Chattahoochee River Keepers on August 11, 2016, during an unrelated meeting. This is a spill from a private line. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Private Lateral | Stream |  | Other |  | Kim Hembree | Kim Hembree | Kim Hembree | 8/17/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary to Clear Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Two residents had illicit sanitary sewer connections to the City's stormwater system. | The illicit flow will be bypassed to a sanitary sewer line until the connections are closed. | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-11-02 | 2015-11-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 230 Scott Street, NW | 6 | fax received 11/03/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 11/3/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-02-13 | 2018-02-13 | Cedartown, City of (Cedartown WPCP) | Polk |  | Cave Springs sewer pump station on N Cave Springs Road | 6000 |  | Raw Sewage | Mountain District - Cartersville | GA0024074 | WWTP | Stream |  | Debris |  | Eric Dykes | Kathy Lewis | Eric Dykes | 2/14/2018 12:00:00 AM | Coosa |  |  |  | 0 | Skeeter Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Pump became stopped up by a baseball | Had to take pump down and clean it, had problems getting pump back together, other back up pump overheated. | d96cd7db-2512-49bb-ac16-6128b6c19eaa | d96cd7db-2512-49bb-ac16-6128b6c19eaa | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2018-02-26 | 0 | 0 | 0 | 0 | 0 | 0
2016-02-02 | 2016-02-02 | Thomaston, City of | Upson | Thomaston | Golden Living Lift Station, 310 Ave F | 3500 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Pipe failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/2/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of this minor spill was a broken sewer main. | The affected area was clean and disinfeted. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-02-03 | 0 | 0 | 0 | 0 | 0 | 0
2017-01-23 | 2017-01-23 | Cedartown, City of (Cedartown WPCP) | Polk |  | E Ellawood Avenue | 900 |  | Raw Sewage | Mountain District - Cartersville | GA0024074 | WWTP | Stream |  | Debris |  | Mick Smith | Kathy Lewis | Mick Smith | 1/24/2017 12:00:00 AM | Coosa |  |  |  | 0 | Tanyard Branch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Partial blockage of rags and debris in the main sewer line and heavy rain fall in the past 48 hours | Cleared the partial blockage will monitor daily for the remainder of the week and monitor weekly going forward | 4265e0af-00af-4b96-982e-53f807bc3994 | 4265e0af-00af-4b96-982e-53f807bc3994 | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2017-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | R.M. Clayton WRC | 0 | EPD received notification of the violation in the followup letter received on 2/23/2016. | Treated Effluent | Wastewater Regulatory Program | GA0039012 | WWRF | Stream |  | Hydraulic Overload |  | Kim Hembree | Kim Hembree | Kim Hembree | 2/23/2016 12:00:00 AM | Chattahoochee |  |  |  | 1 | Chattahoochee River | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | This is an outfall spill due to BOD violation. Date sample taken: 12/24/2015. BOD permit limit = 25 mg/L; Reported Value = 39 mg/L. Total volume = 182.19 MG |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-03-25 | 2017-03-25 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1145 Cahaba Dr. SW - ATL | 5000 | Fax received Sunday 2017-03-26 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Alys Hannum | 3/26/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-06-02 | 2016-06-02 | Gwinnett County (F. Wayne Hill WRC) | Gwinnett | Buford | F. Wayne Hill WRC Influent Pump Station | 3160 | fax received 6/03/2016 | Raw Sewage | Wastewater Regulatory Program | GA0038130 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 6/3/2016 12:00:00 AM |  |  |  |  | 1 | Unnamed Tributary of Ivy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | SCADA telemetry failure |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | GWINNETT COUNTY | 678-232-5732
2017-04-10 | 2017-04-10 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 4577 Elam Church Rd, College Park | 12600 | Fax received on 04/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Pipe failure |  |  |  | Paul Moisan | 4/11/2017 12:00:00 AM | Upper Ocmulgee |  | 2017-04-11 |  | 1 | Conley Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The cause of the spill was pipe failure. | The line was repaired. Washout was repaired and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f |  | 2017-04-11 | 0 | 1 | 0 | 1 | 0 | 0
2018-07-16 | 2018-07-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 424 Lindbergh Dr. NE - Atlanta | 7550 | Fax sent 2018-07-17 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 7/17/2018 12:00:00 AM |  | 7/16/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Rain-induced | Spill was self-contained. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-07-17 | 0 | 0 | 0 | 0 | 0 | 0
2016-04-11 | 2016-04-11 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3136 Martin Luther King Jr. Drive, SW | 1245 | fax received 4/12/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/12/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-09-13 | 2016-09-13 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Clarkston | 3954 Memorial College Ave., Clarkston | 2120 | Notification received on September 15, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 9/13/2016 12:00:00 AM |  |  |  |  | 0 | Snapfinger Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected on September 13, 2016 at 12:45 hours when a crew pressure washed the 8" sewer main 240ft, removed the blockage at 184ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-09-15 | 0 | 1 | 0 | 0 | 0 | 0
2015-07-16 | 2015-07-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1263 Glenwood Avenue, SE | 570 | fax received 7/17/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 7/17/2015 12:00:00 AM |  |  |  |  | 1 | Sugar Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-09-27 | 2015-09-27 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1576 Nantahalla Court, Atlanta | 10 | Notification received on September 29, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Equipment failure |  |  | Hsin Yeh | Hsin Yeh | 9/28/2015 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8" aerial crossing leak at the flange. | The problem was corrected at 23:45 hours, when a crew plugged the manhole to stop the leak from the aerial crossing, set repair the crossing and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-09-29 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-13 | 2017-02-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | College Park | 4566 Elam Church Road, College Park MH No. 2198193 | 5400 | Fax received on 02/13/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Roots |  |  | Paul Moisan | Paul Moisan | 2/13/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Conley Creek | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was roots and grease. | Blockage was cleared, and flow returned to normal. Line will be televised to determine if any repair work is needed. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-14 | 0 | 1 | 1 | 0 | 0 | 0
2016-08-01 | 2016-08-04 | Thomaston, City of (Bell Creek WPCP) | Upson | Thomaston | Moore's Crossing Lift Station | 2550 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Equipment failure |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/1/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 | Unnamed Tributary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The spill was caused by a portable bypass pump (rented) that failed to automatically start because of water in the fuel. | Debris will be removed from the surronding area and the area was disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-26 | 2016-05-26 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Atlanta | 1357 Brookforest Drive, Atlanta | 2560 | Notification received on May 31, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 5/26/2016 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease and Roots | The problem was corrected at 9:40 hours, when a crew pressure washed the main 310ft, turned the blockage loose at 35ft, washed, disinfected the area and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-06-15 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-21 | 2017-01-23 | Social Circle, City of (Little River WPCP) | Walton | Social Circle | 187 Vine Circle (WWTP Outfall) - Social Circle | 947976 | Fax received 2017-01-24 | Treated Effluent | Wastewater Regulatory Program | GA0026107 | WWTP | Stream | Stream | Wet weather |  |  | Alys Hannum | Alys Hannum | 1/24/2017 12:00:00 AM |  | 1/23/2017 12:00:00 AM | 2017-01-23 |  | 1 | Little River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Hydraulic overload | Started motors in basin as soon as possible. Stream monitoring program started 2017-01-23. Signs posted and proper agencies notified. |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-10-11 | 2017-10-11 | Cobb County Water System | Cobb |  | 2215 Creekway Drive | 880 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/11/2017 12:00:00 AM | Chattahoochee |  |  |  | 0 | Barnett Creek Lake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | stopped spill | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-18 | 0 | 0 | 0 | 0 | 0 | 0
2015-12-24 | 2015-12-24 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 377 Lawton Street, SW | 2480 | fax recieved 12/25/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/25/2015 12:00:00 AM |  |  |  |  | 1 | Proctor Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Excessive rain. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-29 | 2015-12-29 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Lithonia | 5090 Klondike Road, Lithonia | 7975 | Notification received on December 30, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP |  |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 12/30/2015 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event | The problem was corrected at 16:00 hours, when a crew rechecked manhole after the rain receded, noticing the flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-12-31 | 0 | 0 | 0 | 0 | 0 | 0
2016-01-25 | 2016-01-25 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 1071 Dunbarton Trace, Brookhaven | 2050 | Notification received on January 26, 2016. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 1/25/2016 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris | The problem was corrected at 11:30 hours, when a crew pressured washed the 8" sewer main 230ft clearing the blockage at 10ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-02-02 | 0 | 1 | 0 | 0 | 0 | 0
2016-02-24 | 2016-02-24 | Ashburn, City of (Airport WPCP) | Turner | Ashburn | Rockhouse Rd. and Sylvia Dr. | 120000 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 2/24/2016 12:00:00 AM | Satilla |  |  |  | 0 | Hat Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy Rain | The facility replaced two pumps. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-28 | 2017-03-02 | Sardis,City of (Sardis WPCP) | Burke | Sardis | Effluent outfall of wastewater treatment plant | 166297 | Stream monitoring ceased and superseded by the 4/3/2017 - 4/5/2017 effluent major spill. | Treated Effluent | Northeast District - Augusta | GA0020893 | WWTP | Stream | Stream |  |  | Delaine Scott | Delaine Scott | Delaine Scott | 3/13/2017 12:00:00 AM | Savannah | 3/13/2017 12:00:00 AM | 2017-03-13 |  | 1 | Chandler's Branch/Brier Creek | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | The weekly max BOD effluent limitation was exceeded by greater than 50% resulting in a major effluent spill of treated wastewater. The exceedance was due to the construction upgrades at the treatment plant effluent structure. In order to construct the new/upgraded effluent structure, the treatment pond levels had to be significantly lowered, resulting in insufficient BOD reduction. | Stream monitoring initiated. Public notification posted at City Hall on 3/13/17; notification to the Burke Co. Health Department on 3/13/17; and notification published in the Burke County True Citizen newspaper on 3/15/17. | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | ea148df7-7501-4fd8-8b37-3c3b5895dc06 | 2017-03-13 | 1 | 1 | 0 | 1 | 1 | 0
2018-07-21 | 2018-07-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1665 Snapfinger Road Decatur GA 30032 | 26400 |  | Raw Sewage | Wastewater Regulatory Program | GA0024147 |  | Stream |  | Wet weather |  |  | Dillon Rodenbaugh |  | 7/21/2018 5:29:00 PM |  |  |  |  | 1 | Cobbs Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Wet Weather and sewer main plugged for repairs | Pulled plug out of main to unstop line and restore flow |  |  | 7c4cea05-f09f-4f0a-b5b3-88ce2875d2e9 | 2018-07-24 | 0 | 0 | 0 | 0 | 0 | 0
2017-10-23 | 2017-10-23 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Brookhaven | 2741 Tryon Place, Brookhaven | 300 | Notification received on October 27, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 10/23/2017 12:00:00 AM |  |  |  |  | 0 | North Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Storm Event / I&I | The problem was corrected at 14:00 hours when the first responder crew waited on the storm event to subside, and the flow returned normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-10-30 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-10 | 2017-01-10 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2288 Cottage Grove Ave, SE - ATL | 10 | Fax received on 01/11/2017. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 1/11/2017 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | The crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | Eleanor Burks |  | ATLANTA, CITY OF
2016-04-04 | 2016-04-04 | United States Army Hunter Army Airfield WWTP | Chatham | Savannah |  | 10500 | Due to the response of the Jet-Vac Truck only 6000 gallons of sewage mad it to Waters of the State. This is considered a minor spill. | Raw Sewage | Coastal District | GA0027588 | Collection System | Other | Stream | Debris |  | John Kalp | John Kalp | John Kalp | 4/5/2016 2:50:00 PM | Ogeechee | 4/4/2016 12:00:00 AM |  |  | 1 | Forest River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | yes | 0 | the sanitary spill occurred at bldg 8675 on Hunter Army Airfield. It was determined that the spill was caused by a blockage in the sanitary collection system. the blockage caused a backup within the system and a sanitary manhole overflowed(no solids released) onto the surrounding vegetation. The overflow ultimately discharged into a storm water drop inlet that discharged to Waters of the State. See document section | A berm was constructed to prevent further discharge in to storm water collection system and utilized the Jet-Vac truck to clear the blockage. Mitigation included the removal of wastewater puddles from the vegetated area; applied agricultural lime for disinfection; and posted signs to warn the public. | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 3fb616c6-eb6e-11e0-b8d8-000c29971acc | 2016-04-07 | 1 | 1 | 0 | 0 | 0 | 0
2018-02-02 | 2018-02-02 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1150 Collier Rd. NW - ATL | 1500 | Fax sent 2018-02-03 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Alys Hannum | Alys Hannum | 2/3/2018 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-08-14 | 2017-08-14 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Riverdale | 5751 Riverdale Road - Riverdale Manhole - 2213640 | 4800 | Fax received on 08/15/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream | Shoreline | Grease |  |  | Paul Moisan | Paul Moisan | 8/15/2017 12:00:00 AM | Flint |  |  |  | 1 | Flint River | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-08-18 | 0 | 1 | 1 | 0 | 0 | 0 | Charles Ecton |  | CLAYTON COUNTY WATER AUTHORITY
2016-04-01 | 2016-04-01 | Tifton, City of (New River WPCP) | Tift | Tifton | Tift Regional Wastewater Treatment Plant, Tifton 31.445361, -83.478106 | 16800 | Email received on 04/04/2016. | Raw Sewage | Wastewater Regulatory Program | GA0048470 | WWTP | Stream | Shoreline | Hydraulic Overload |  |  | Paul Moisan | Paul Moisan | 4/4/2016 12:00:00 AM |  |  | 2016-04-04 | 2017-04-24 | 1 | Tributary of New River | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | Rainfall event of April 1-2, 2016. |  |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-04-05 | 0 | 1 | 0 | 1 | 1 | 0
2017-01-14 | 2017-01-14 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 3408 Pheasant Court, Decatur | 1720 | Notification received on January 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 1/14/2017 12:00:00 AM |  |  |  |  | 0 | Shoal Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 11:19 hours when the crew rodded the manhole 105 ft downstream, cleared the blockage at 99 ft and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-24 | 0 | 1 | 0 | 0 | 0 | 0
2015-09-30 | 2015-09-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1715 Northside Dr. NW | 128 | Fax received 10-01-2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Dagny Pariani | Kim Hembree | 10/1/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 89352e56-9649-4d50-9761-577155a9c85b | 2015-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-17 | 2015-12-17 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 171 Whiteford Avenue, NE | 7320 | fax received 12/18/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 12/18/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This was a rain induced spill. |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-12-17 | 2015-12-17 | Athens-Clarke County (North Oconee WPCP) | Clarke | Athens | 143 Strickland Ave., Athens | 1955 | Initial email 12/17, full report faxed 12/18 | Raw Sewage | Wastewater Regulatory Program | GA0021725 | Collection System | Stream | Stream | Wet weather |  |  | Dagny Pariani | Dagny Pariani | 12/17/2015 12:00:00 AM | Oconee | 12/17/2015 12:00:00 AM |  |  | 1 | un-named tributary to North Oconee River | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Surcharge due to major rain event | Vac truck removed spillage until surcharge stopped |  | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2015-12-21 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Unified Government of Athens-Clarke County | 706-613-3481
2017-07-12 | 2017-07-12 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Decatur | 1116 McConnell Drive, Decatur | 800 | Notification received on July 17, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Hsin Yeh | 7/12/2017 12:00:00 AM |  |  |  |  | 0 | South Fork Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease blockage | The problem was corrected at 14:24 hours, when a first responder crew pressure washed the 8 inch sewer main 185 feet upstream, removed the debris/grease blockage at 100 feet, and restored normal flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-17 | 0 | 1 | 0 | 0 | 0 | 0
2015-11-16 | 2015-11-16 | Baldwin, City of (Baldwin WPCP) | Habersham |  | 584 Walden Street | 600 | Area was treated with lime and public notice signs were placed at the spill site as well as above and below the spill site area of the creek | Raw Sewage | Mountain District - Cartersville | GA0033243 | WWTP | Stream |  | Debris |  | Brian Koehler | Kathy Lewis | Brian Koehler | 11/17/2015 12:00:00 AM | Chattahoochee |  |  |  | 1 | South Fork of Little Mud Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage in the sewer line | The blockage in the line was removed | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 4828ee5a-eb6e-11e0-b8d8-000c29971acc | 452173e4-eb6e-11e0-b8d8-000c29971acc | 2015-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | Scott Barnhart | 706-778-6341 | City of Baldwin
2016-01-23 | 2016-01-23 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2006 Delowe Drive, SW | 1000 | fax received 1/24/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/24/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-12 | 2018-05-12 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Ellenwood | 5564 Hwy 42 | 3200 | Fax received 5/13/2018 | Raw Sewage | Wastewater Regulatory Program | GA0038423 | WWTP | Stream |  | Grease |  |  | Hsin Yeh | Paul Moisan | 5/13/2018 12:00:00 AM |  |  |  |  | 0 | Upton Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease | Shot line and returned flow to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | d80f500b-2416-4653-adb7-23760952ef3b | 2018-05-14 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-28 | 2016-01-28 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2020 Alison Court, SW | 4750 | fax received 1/29/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Kim Hembree | Kim Hembree | 1/29/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Atlana
2018-06-05 | 2018-06-05 | Douglasville-Douglas County Water & Sewer Authority (Northside WPCP) | Douglas | Douglasville | Red Lodge Lift Station - 2797 Red Lodge Way, Douglasville, GA 30135 | 8700 |  | Raw Sewage | Wastewater Regulatory Program | GA0030350 | Lift Station | Other |  | Equipment failure |  |  | Juan Robles | Juan Robles | 6/6/2018 7:33:00 AM | Chattahoochee | 6/5/2018 12:00:00 AM |  |  | 0 | Gilberts Branch | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Failure of motor starter in the electrical panel that shorted out pump breakers and other electrical components. | - Mechanics/electricians were dispatched to the site and repaired electrical components inside the control panel. - Crews cleaned and disinfected the area around the manhole where the spill occurred. - Signs were posted in the area to notify residents and the public of the spill. - Notification given to EPD, the Health Department, and local media. |  | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | bcdfb198-48ad-4ddc-9115-cb2fb017cce4 | 2018-06-07 | 0 | 1 | 0 | 0 | 0 | 0
2016-01-30 | 2016-01-30 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 199 Camden Road, NE | 7630 | fax received 1/31/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Equipment failure |  |  | Kim Hembree | Kim Hembree | 1/31/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Bypass pump failure | The crew repaired the bypass pump |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-07-12 | 2015-07-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1776 Johnson Road, NE | 581 | fax received 7/12/2015 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Kim Hembree | Kim Hembree | 7/12/2015 12:00:00 AM |  |  |  |  | 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | grease and debris | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2016-04-13 | 2016-04-13 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 2480 Madrid Drive South | 600 | fax received 4/15/2016 | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 4/15/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Butler Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-19 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA
2017-12-13 | 2017-12-13 | Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | Clayton | Rex | 3213 Glen Hollow Drive, Rex Manhole: 2215222 | 1200 | Fax received on 12/14/2017. | Raw Sewage | Wastewater Regulatory Program | GA0038423 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 12/14/2017 12:00:00 AM | Ocmulgee |  |  |  | 1 | Panther Creek | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | Grease | Blockage was cleared and flow returned to normal. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-12-18 | 0 | 1 | 1 | 0 | 0 | 0 | Lamar Hamlin |  | CLAYTON COUNTY WATER AUTHORITY
2016-04-01 | 2016-04-01 | Augusta, City of (J.B. Messerly WPCP) | Richmond | Augusta | 1301 New Savannah Road | 21600 | fax received 4/02/2016. | Raw Sewage | Wastewater Regulatory Program | GA0037621 | Collection System | Stream |  | Wet weather |  |  | Kim Hembree | Kim Hembree | 4/2/2016 12:00:00 AM |  |  |  |  | 1 | Tributary to Mid-City | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Excessive rain |  |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF AUGUSTA | 706-513-3199
2017-01-21 | 2017-01-21 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Ellenwood | 4124 Flakes Mill Road, Ellemnwood | 110550 | Notification received on January 24, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Wet weather |  |  | Hsin Yeh | Hsin Yeh | 1/22/2017 12:00:00 AM |  |  |  |  | 0 | South River | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | Storm Event | The problem was corrected at 22:30 hours when the heavy rain stopped and the sewer flow returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-01-26 | 0 | 1 | 0 | 0 | 0 | 0
2015-10-31 | 2015-10-31 | Dekalb County (Snapfinger Creek WPCP) | DeKalb | Chamblee | 1680 Remington Road, Chamblee | 1050 | Notification received on November 2, 2015. | Raw Sewage | Wastewater Regulatory Program | GA0024147 | WWTP | Stream |  | Other |  |  | Hsin Yeh | Hsin Yeh | 10/31/2015 12:00:00 AM |  |  |  |  | 0 | Nancy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Fallen tree. | The problem was corrected at 13:30 hours, when a crew repaired the main with a full circle clamp, stopped the leak, cleaned up the tree debris from the creek and restored regular flow. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2015-11-02 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Commerce, City of (Northside WPCP) | Jackson | commerce | Manhole B-122 | 1000 | Dryland Spill | Raw Sewage | Wastewater Regulatory Program | GA0026247 | Collection System | Other |  | Wet weather |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 9/11/2017 12:00:00 AM | Oconee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | I/I |  | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2017-10-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-05-15 | 2016-05-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2013 Claude Street, NW | 3225 | fax received 5/16/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 5/16/2016 12:00:00 AM |  |  |  |  | 1 | Peachtree Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-05-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2018-05-14 | 2018-05-14 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1505 Chattahoochee Ave. NW - Atlanta | 416 | Fax sent 2018-05-15 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Alys Hannum | 5/15/2018 12:00:00 AM |  | 5/14/2018 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Debris in the mainline | Crew used a hydraulic pressure cleaner to contain the spill |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-05-22 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-13 | 2016-10-13 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2008 Campbellton Road, S.W., Atlanta | 280 | Fax received on 10/14/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Grease |  |  | Paul Moisan | Paul Moisan | 10/14/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was grease and debris in the main line. | The site was cleaned and disinfected. This area was placed on periodic inspection schedule to determine the need for upgrading, etc. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2018-02-04 | 2018-02-04 | Loganville, City of (Loganville WPCP) | Walton | Loganville | 1149 Chandler Haulk Road - Loganville | 7200 | Email received 2018-02-05 | Raw Sewage | Wastewater Regulatory Program | GA0020788 | Collection System | Stream |  | Wet weather |  |  | Alys Hannum | Alys Hannum | 2/5/2018 12:00:00 AM |  |  |  |  | 1 | Little Haynes Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Inflow and Infiltration | Unknown |  | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2018-02-06 | 0 | 0 | 0 | 0 | 0 | 0
2017-02-08 | 2017-02-08 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 1782 Cheshire Bridge Rd. NE - ATL | 9860 | Fax received 2017-02-09 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Alys Hannum | Paul Moisan | 2/9/2017 12:00:00 AM |  |  |  |  | 0 | Did Not Enter State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill at 11:30 PM. The process to clean and disinfect the site has been initiated. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-02-10 | 0 | 0 | 0 | 0 | 0 | 0
2015-04-28 | 2015-04-30 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2979 Masseyville Road | 2100 | REC CALL 4/29/2015. REC EMAIL 4/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/29/2015 8:50:00 AM | Ocmulgee | 4/28/2015 12:00:00 AM |  |  | 1 | Boggy Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. | Debris has been removed and the affected area is being disinfected with lime. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-30 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5669
2015-04-28 | 2015-04-30 | Macon Water Authority (Rocky Creek WPCP) | Bibb | Macon | 2979 Masseyville Road | 2100 | REC CALL 4/29/2015. REC EMAIL 4/29/2015. | Raw Sewage | Wastewater Regulatory Program | GA0024546 | Collection System | Stream | Stream | Grease |  | Emily Wingo | Emily Wingo | Emily Wingo | 4/29/2015 8:50:00 AM | Ocmulgee | 4/28/2015 12:00:00 AM |  |  | 1 | Boggy Branch | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | After the blockage was removed, it was determined that the cause of this minor spill was grease. | Debris has been removed and the affected area is being disinfected with lime. | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | a798bbbf-b30c-466e-9ac7-1ae30ae77a96 | 2015-04-30 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | MACON WATER AUTHORITY | 478-464-5694
2017-09-11 | 2017-09-12 | Vidalia, City of (Swift Creek WPCP) | Toombs | Vidalia | 2505 Vann Rd. Vidalia, GA 30474 | 102000 | Robbie Akins sent in a memo to the EPD office on September 14th 2017. He states they have begun the pubic notification process. This part Swift Creek is not on the 303(d) list. | Raw Sewage | Coastal District | GA0025488 | Lift Station | Stream | Stream | Natural Disaster |  | Bill Hawthorne | Brett Berry | Brett Berry | 9/12/2017 12:00:00 AM | Altamaha | 9/15/2017 12:00:00 AM | 2017-09-15 | 2018-09-15 | 1 | Swift Creek | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Lift stations lost power throughout the city of Vidalia due to power outages caused by Hurricane Irma. | N/A | 3f13ac88-eb6e-11e0-b8d8-000c29971acc | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 91d74c2a-ab08-44d3-9b9c-81c0cd32b281 | 2017-09-19 | 1 | 0 | 0 | 0 | 0 | 0
2015-01-26 | 2015-01-26 | CITY OF ATLANTA - R. M. CLAYTON WRC | Fulton | Atlanta | 3746 Melvin Drive, SW | 340 | fax received 1/27/2015 | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 1/27/2015 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2015-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2015-10-15 | 2015-10-15 | Cobb County MS4 | Cobb |  | 1360 Cameron Glen Dr. | 190 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream |  | Grease |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 10/15/2015 12:00:00 AM | Chattahoochee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Grease in 15" Clay Main | Spread Lime at spill area | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2015-10-16 | 0 | 0 | 0 | 0 | 0 | 0
2016-10-10 | 2016-10-10 | Toccoa, City of (Eastanollee Creek WPCP) | Stephens | Toccoa | Clark Street and Braswell Street, Toccoa | 100 |  | Raw Sewage | Wastewater Regulatory Program | GA0021814 | WWTP |  |  | Debris |  |  | Hsin Yeh | Hsin Yeh | 10/11/2016 12:00:00 AM |  |  |  |  | 0 | Toccoa Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Blockage | City personnel utilized the vacuum truck to jet the line at the manhole. The blockage was cleared and the flow quickly returned to normal. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2016-10-21 | 0 | 1 | 0 | 0 | 0 | 0
2016-11-15 | 2016-11-15 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 2353 Burroughs Ave., SE, ATL | 272 | Fax received on 11/16/2016. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Ground |  | Debris |  |  | Paul Moisan | Paul Moisan | 11/16/2016 12:00:00 AM |  |  |  |  | 0 | Did not make it to State Waters | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | the crew used a hydraulic pressure cleaner. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2016-11-18 | 0 | 0 | 0 | 0 | 0 | 0
2017-09-11 | 2017-09-11 | Port Wentworth, City of (Port Wentworth WPCP) | Chatham | Port Wentworth | Intersection of Osteen Street and Armadale Road, Port Wentworth, GA | 3800 | Initial phone call 9/14, official volume estimate received 9/21. | Raw Sewage | Coastal District | GA0038814 | Collection System | Canal |  | Natural Disaster |  | Dagny Pariani | Dagny Pariani | Dagny Pariani | 9/14/2017 12:00:00 AM | Savannah |  |  |  | 0 | Phillips Canal | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Heavy rainfall during Hurricane Irma resulted in an overflowing manhole at the intersection of Osteen and Armadale. | The spill stopped of its own accord. The City applied lime to the area. Drainage ditches in this area feed the Phillips Canal which flows to the Savannah River. | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 89352e56-9649-4d50-9761-577155a9c85b | 2017-09-22 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | City of Port Wentworth | 912-401-0572
2016-02-12 | 2016-02-12 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 3560 Adkins Road, NW | 2000 | fax received 2/13/2016 | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream |  | Debris |  |  | Kim Hembree | Kim Hembree | 2/13/2016 12:00:00 AM |  |  |  |  | 1 | Utoy Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | The crew used a hydraulic pressure cleaner to contain the spill. |  | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 5cdd9d43-9d91-4613-8814-35f2cb97aea3 | 2016-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | CITY OF ATLANTA
2017-07-24 | 2017-07-24 | Milledgeville, City of (Milledgeville WPCP) | Baldwin | Milledgeville | Intersection of Harrington Dr and S Irwin St | 1600 | Five day letter notification letter received on July 24, 2017. | Raw Sewage | Wastewater Regulatory Program | GA0030775 | WWTP |  |  | Operator error |  |  | Hsin Yeh | Hsin Yeh | 7/24/2017 12:00:00 AM |  |  |  |  | 0 | Fishing Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Street Department Hit (machinery) 8" sewer main | Built a containment wall to contain the sewer spill on July 24, 2017 at 10:35 AM, repaired pipe on Juy 24, 2017 at 12:00 PM. |  | d80f500b-2416-4653-adb7-23760952ef3b | d80f500b-2416-4653-adb7-23760952ef3b | 2017-07-24 | 0 | 1 | 0 | 0 | 0 | 0
2017-01-17 | 2017-01-20 | Fort Valley, City of (Fort Valley WPCP) | Peach | Fort Valley | Railroad behind cemetery beside Bluebird Body Company, Fort Valley | 17280 | Email received on 01/18/2017. | Raw Sewage | Wastewater Regulatory Program | GA0031046 | Collection System | Stream |  | Pipe failure |  |  | Paul Moisan | Paul Moisan | 1/18/2017 12:00:00 AM |  |  | 2017-01-24 |  | 1 | Bay Creek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 12" clay pipe under railroad tracks failed. | A contractor was called in when first notified (01/19), and repaired the spill |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 2017-02-28 | 0 | 0 | 0 | 0 | 0 | 0
2016-08-17 | 2016-08-17 | Thomaston, City of | Upson | THomaston | 180 DOT Drive | 250 |  | Raw Sewage | Wastewater Regulatory Program |  | Collection System | Stream | Stream | Operator error |  | Reginald Williamson | Reginald Williamson | Reginald Williamson | 8/17/2016 12:00:00 AM | Ocmulgee |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | This discharge occurred when the facility staff setup a portable pump and inadvertently forgot to secure the discharge hose. | Debris was removed from the area and the affected area has been disinfected with lime. | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 33e4b44c-ee02-11e0-b8d8-000c29971acc | 2016-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2017-03-16 | 2017-03-16 | Atlanta, City of (R.M Clayton, Utoy Creek, and South River WRCs) | Fulton | Atlanta | 196 Montgomery Ferry Dr. NE - ATL | 2925 | Fax received 2017-03-17. | Raw Sewage | Wastewater Regulatory Program | GA0039012 | Collection System | Stream | Stream | Debris |  |  | Alys Hannum | Paul Moisan | 3/17/2017 12:00:00 AM |  | 3/16/2017 12:00:00 AM |  |  | 1 | Peachtree Creek | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | The cause of the spill was debris in the mainline. | Crew used a hydraulic pressure cleaner to contain the spill. |  | f66c40b5-c44c-469c-9511-6d209e6ebb6f | 1c349d21-bd7e-4a44-b736-f5f5a1547d2d | 2017-03-21 | 0 | 0 | 0 | 0 | 0 | 0
2018-07-09 | 2018-07-09 | Eastman, City of (Sugar Creek WPCP) | Dodge | Eastman | Industrial Park Lift Station in Eastman, GA. | 300 | Reported by Terry Hardeman, Operator, by phone this date. | Raw Sewage | Southwest District | GA0046485 | Grease Interceptor | Ground | N/A | Equipment failure |  | Jay Howell | Jay Howell | Jenna Detar | 7/9/2018 9:15:00 AM | Ocmulgee |  |  |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Small overflow from lift station. Cause due to pump failure. Staff repaired pump immediately and limited the duration of the event to approx. two (2) hours. Waters stayed on-site and did not discharge off the property, into any ditchway or state water. | Fixed pump at lift station, picked up visible waste and applied area with lime. | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | c55a0890-1b00-4f2f-a100-212b30005169 | 40cb8afa-eb6e-11e0-b8d8-000c29971acc | 2018-07-09 | 1 | 0 | 0 | 0 | 0 | 0