## Sheet1
Posting Date | 2025-03-12
FACILITY_NAME | BEGIN_DATE | COUNTY | CITY | OVERFLOW_LOCATION | QUANTITY_GALLONS | OVERFLOW_TYPE | PERMIT_NUMBER | SPILL_SOURCE | CAUSE | RIVER_BASIN | WATERWAY_IMPACTED | LATITUDE | LONGITUDE | IS_ENTERED_WATERWAY | IS_OVERFLOW_MODE
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-11 | DeKalb | Clarkston | 3878 Nielson Ct Clarkston 30021 | 50 | Raw Sewage | GA0024147 | Collection System | Found 6in clean out surcharging with evidenced of an overflow due to a vandalism | Ocmulgee | Did Not Enter State Waters | 33.809885 | -84.230699 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-11 | DeKalb | Lithonia | 2040 Young Rd Lithonia 30058 | 1700 | Raw Sewage | GA0024147 | Collection System | Found evidence of a spill at manhole #16-060-s074 caused by a grease blockage | Ocmulgee | Pole Bridge Creek | 33.739202 | -84.175344 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-10 | DeKalb | Ellenwood | 4457 Equity Ct Ellenwood 30294 | 5800 | Raw Sewage | GA0024147 | Collection System | Found the 4in force main spilling into corn creek caused by broken section of the main | Ocmulgee | Corn Creek | 33.649654 | -84.216543 | N | 1
CHEROKEE COUNTY WATER & SEWER AUTHORITY (ROSE CREEK WPCP) | 2025-03-09 | Cherokee | Woodstock | 7081 Hickory Flat Highway Woodstock | 18870 |  | GA0046451 | WWTP | Blockage in sewer line | Coosa | Unnamed tributary to Mill Creek | 34.166280 | -84.411840 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-06 | DeKalb | Lithonia | 5476 Winslow Crossing Lithonia 30038 | 10 |  | GA0024147 | Collection System | Found evidence of an overflow at the 4in private cleanout caused by an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.691857 | -84.165750 | N | 1
Utilities, Inc. of Georgia (Big Canoe WPCP) | 2025-03-06 | Pickens | Jasper | Inside gates at Buckskull Facility 34.459425, -84.289426 | 50 |  | GA0030252 | WWTP | Weather related wind broke skimmer basket and fell into clarifier and stopped sweep arm | Coosa | Did not enter state waters | 34.459425 | -84.289426 | N | 1
Dallas, City of (Pumpkinvine Creek WPCP) | 2025-03-06 | Paulding | Dallas | Near 151 West Paulding Blvd. Dallas, GA 30132 | 1500 |  | GA0039241 | WWTP | Force main failure | Coosa | Did not enter state waters | 33.921990 | -84.861720 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-03-05 | Fulton | South Fulton | 5300 Fulton Industrial Blvd. | 750 | Raw Sewage | GA0024333 | Collection System | Line Failure due to Storm Debris | Chattahoochee | Utoy Creek | 33.742891 | -84.562319 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-03-05 | Cobb | Marietta | 2404 Mirrabeau CT, Marietta, GA 30066 | 420 | Raw Sewage | GA0026140 | Collection System | Rags | Chattahoochee | Little Noonday Creek | 34.007039 | -84.512774 | N | 1
Douglasville-Douglas County Water & Sewerage Authority (South Central WPCP) | 2025-03-05 | Douglas | Douglasville | 5864 West Yeager Rd. | 42000 | Raw Sewage | GA0038709 | Pump Station | Heavy storm in area caused power outages and breakers to trip at the pump station | Chattahoochee | Little Bear Creek | 33.647821 | -84.762708 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-03-05 | Fulton | Union City | 7430 Oakley Road Union City, GA 30291 | 980 | Raw Sewage | GA0024333 | Collection System | Grease and Debris Accumilation | Chattahoochee | Tributary of Morning Creek | 33.564362 | -84.533156 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-05 | DeKalb | Chamblee | 3041 Northeast Expressway Chamblee 30341 | 7640 | Raw Sewage | GA0024147 | Collection System | Found 8in main sewer spilling into North Fork Peachtree Creek due to bank erosion | Chattahoochee | North Fork Peachtree Creek | 33.866963 | -84.295467 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-04 | DeKalb | Atlanta | 3330 Northlake Parkway, Atlanta, 30345 | 3180 | Raw Sewage | GA0024147 | Collection System | Found manhole #18-210-p129 spilling into storm drain due to a grease blockage | Ocmulgee | Henderson Mill Creek | 33.851853 | -84.255827 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-04 | DeKalb | Stone Mountain | 5508 Stonehaven Way Stone Mountain 30087 | 0 | Raw Sewage | GA0024147 | Collection System | Found evidence of an overflow from a septic tank leaking due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.793136 | -84.174154 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-03-04 | Fulton | Alpharetta | 12655 Edison Dr. Alpharetta, GA 30005 | 9760 | Raw Sewage | GA0024333 | Collection System | Root Intrusion | Chattahoochee | Morning Creek | 34.087356 | -84.252324 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-03-03 | Cobb | Marietta | 1210 Kennestone Cir | 270 | Raw Sewage | GA0026140 | Collection System | Debris | Chattahoochee | Noonday Creek | 33.985138 | -84.552820 | N | 1
Cumming, City of (Bethelview Road WPCP) | 2025-03-03 | Forsyth | Cumming | 3410 Castleberry Village | 4050 | raw sewage | GA0046019 | Collection System | PVC pipe, rocks, grease, and flushable wipes causing a partial blockage | Chattahoochee | Orr Creek | 34.200013 | -84.158238 | N | 1
Gwinnett County Board of Commissioners (F. Wayne Hill WRC) | 2025-03-02 | Gwinnett | Lawrenceville | 158 Paper Mill Rd- Lawrenceville | 1763 | raw sewage | GA0038130 | Collection System | debris- rocks or construction material | Upper Ocmulgee | unnamed tributary of Shoal Creek | 33.956449 | -83.971947 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-03-02 | Cobb | Marietta | 1792 County Services Pkwy; 790 gallons; Olley Creek | 790 | Raw Sewage | GA0026140 | Collection System | Grease | Chattahoochee | Olley Creek | 33.916686 | -84.585728 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-03-01 | Cobb | Marietta | 900 Shaw Park Rd NE | 740 | Raw Sewage | GA0026140 | Collection System | Rags | Chattahoochee | Noonday Creek | 34.030923 | -84.523366 | N | 1
Carrollton, City of (Carrollton WPCP) | 2025-02-28 | Carroll | Carrollton | 116 Brock St. | 2310 | Raw Sewage | GAJ020126 | Collection System | Debris caused overflow. CTS #111919 | Tallapoosa | Unnamed tributary to Buffalo Creek | 33.548770 | -85.077364 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-28 | DeKalb | Tucker | 4259 Drayton Woods Club Tucker 30084 | 24150 | Raw Sewage | GA0024147 | Collection System | Found manhole 18-140-s210 surcharging due to an unknown blockage in 15in sewer main, causing sewer to spill intermittently into South Fork Peachtree Creek through sewer main joint. | Ocmulgee | South Fork Peachtree Creek | 33.824795 | -84.213629 | N | 1
Warner Robins, City of (Sandy Run Creek WPCP) | 2025-02-28 | Houston | Warner Robins | 358 Old Perry Rd | 400 | raw sewage | GA0030325 | Collection System |  | Flint | did not enter state waters | 32.536370 | -83.606773 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-02-27 | Fulton | Johns Creek | 10145 Haynes Bridge Road | 1880 | Raw Sewage | GA0024333 | Collection System | Grease Accumilation | Chattahoochee | Tributary to Big Creek | 34.030093 | -84.269483 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-27 | DeKalb | Chamblee | 2747 Shallowford Rd Chamblee 30341 | 1700 | Raw Sewage | GA0024147 | Collection System | Found manhole #18-246-s041 spilling into North Fork Peachtree Creek due to a grease blockage | Chattahoochee | North Fork Peachtree Creek | 33.867450 | -84.297255 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-27 | DeKalb | Stone Mountain | 4355 Autumn Hill Dr Stone Mountain 30083 | 21150 | Raw Sewage | GA0024147 | Collection System | Found 8in creek crossing broken and spiling into Snapfinger Creek due to a structural defect | Ocmulgee | Snapfinger Creek | 33.755725 | -84.222658 | N | 1
Dallas, City of (Pumpkinvine Creek WPCP) | 2025-02-26 | Paulding | Dallas | Between MH# 5556 and 5496– Near 225 Brookside Dr. Dallas, GA 30132 | 600 |  | GA0039241 | WWTP | Joint failure on the main sewer line. | Coosa | Griffin Creek | 33.920890 | -84.823690 | N | 1
Rome, City of (Rome WRF) | 2025-02-26 | Floyd | Rome | Behind 22 Tamassee Lane (Tamassee Lane Apartments) | 5000 |  | GA0024112 | WWTP | Vandalism. Upon our arrival our crew jetted the main and got the line flowing enough to stop the overflow. We discovered that there were limbs, pieces of concrete, and a section of 12 inch plastic pipe obstructing the flow. | Coosa | Did not enter state waters | 34.275430 | -85.233190 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-26 | DeKalb | Tucker | 2101 Tucker Industrial Road, Tucker, 30084 | 10 |  | GA0024147 | Collection System | Found 4in private clean out surcharging with evidence of an overflow due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.845325 | -84.202716 | N | 1
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-02-26 | Clayton | Jonesboro | 1110 Battlecreek Rd. | 14520 | Raw Sewage | GA0038423 | Collection System | Roots/Grease/Non-flushables caused blockage | Flint | Jester Creek | 33.553526 | -84.356160 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-26 | DeKalb | Decatur | 1712 Scott Boulevard Decatur 30033 | 18895 | Raw Sewage | GA0024147 | Collection System | Found evidence of a private sewer spill at manhole 18-062-p107 due to an unknown blockage | Ocmulgee | South Fork Peachtree Creek | 33.798120 | -84.283530 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-02-26 | Cobb | Kennesaw | 691 Ernest W. Barrett Pkwy NW | 130 | Raw Sewage | GA0026140 | Collection System | Gravel | Chattahoochee | Noonday Creek | 34.006405 | -84.572050 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-26 | DeKalb | Decatur | 1745 Angelique Dr Decatur 30033 | 10 | Raw Sewage | GA0024147 | Collection System | Found evidence of an overflow coming from ground surface due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.833127 | -84.303466 | N | 1
Columbus Water Works (South WRF) | 2025-02-26 | Muscogee | Columbus | 798 Omega Dr. | 459 | Raw Sewage | GA0020516 | Collection System | Debris caused overflow | Chattahoochee | Tiger Creek | 32.459607 | -84.880027 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-25 | DeKalb | Decatur | 2870 Raleigh Ct Decatur 30034 | 50 | Raw Sewage | GA0024147 | Collection System | Found evidence of an overflow at the private septic tank caused by an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.706560 | -84.217398 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-02-25 | Fulton | South Fulton | 8027 Spence Road South Fulton, GA 30218 | 244800 | Raw Sewage | GA0024333 | Collection System | Power/Mechanical Failure at Pump Station | Chattahoochee | Whitewater Creek | 33.561258 | -84.563236 | N | 1
Griffin, City of (Shoal Creek - Blanton Mill WPCP) | 2025-02-25 | Spalding | griffin | 415 South Pine Hill Rd | 2250 | raw sewage | GAJ020036 |  | grease and rags | Flint | tributary to Shoal Creek | 33.235077 | -84.310488 | N | 1
Locust Grove, City of (Indian Creek WPCP) | 2025-02-24 | Henry | Locust Grove | 4225 Strong Rock Pkwy | 5208 |  | GA0038849 | Collection System | Electrical Failure | Ocmulgee | Did not reach State waters. | 33.342069 | -84.127656 | N | 1
Perry, City of (Frank Satterfield Road WWTF) | 2025-02-24 | Houston | Perry | Perimeter Rd - SSO from manhole | 70 | Raw Sewage | GA0021334 | Collection System | Rags | Ocmulgee | Fannie Gresham Creek | 32.468623 | -83.734237 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-24 | DeKalb | Decatur | 3778 Guilford Ct Decatur 30034 | 1200 | Raw Sewage | GA0024147 | Collection System | Found manhole 15-037-s038 spilled into South River due to debris (rags) blockage | Ocmulgee | South River | 33.671110 | -84.247996 | N | 1
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-02-24 | Clayton | Riverdale | 5503 Riverdale Rd. | 10000 | Raw Sewage | GA0038423 | Collection System | Grease caused overflow | Flint | Camp Creek | 33.605574 | -84.437349 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-02-24 | Cobb | Kennesaw | 1750 Shiloh Road | 1290 | Raw Sewage | GA0026140 | Collection System | Grease | Chattahoochee | Proctor Creek | 34.061431 | -84.605385 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-24 | Fulton | Atlanta | 1315 S Ponce De Leon Ave NE | 100 | raw sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Did Not Enter State Waters | 33.773631 | -84.347211 | N | 1
Gwinnett County Board of Commissioners (F. Wayne Hill WRC) | 2025-02-23 | Gwinnett | Lawrenceville | 2945 Cruse Rd- Lawrenceville | 9801 | raw sewage | GA0038130 | Collection System | debris- wipes, paper, and other products | Chattahoochee | unnamed tributary of Sweetwater Creek | 33.937144 | -84.093879 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-23 | DeKalb | Atlanta | 1452 Wilford Dr Atlanta 30319 | 128 | Raw Sewage | GA0024147 | Collection System | Found 4in cleanout spilling into the storm drain due to an unknown blockage in 8in sewer main | Ocmulgee | North Fork Peachtree Creek | 33.862473 | -84.339837 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-22 | DeKalb | Lithonia | 6428 Castle Downs Trace Lithonia 30058 | 60 | Raw Sewage | GA0024147 | Collection System | Found evidence of a sewer spill that came from 4in R.O.W. cleanout due to roots blockage | Ocmulgee | Swift Creek | 33.747191 | -84.136259 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-22 | DeKalb | Stone Mountain | 1600 Autumn Hurst Ct Stone Mountain 30088 | 205 | Raw Sewage | GA0024147 | Collection System | Found manhole 16-004-s030 spilling into Barbashela Creek due to a grease blockage | Ocmulgee | Barbashela Creek | 33.748405 | -84.204175 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-21 | DeKalb | Chamblee | 3453 Pierce Dr Chamblee Ga 30341 | 520 | Raw Sewage | GA0024147 | Collection System | Found sewer spilling from broken lateral due to debris (rags) blockage in 8in sewer main | Chattahoochee | Nancy Creek | 33.892033 | -84.313955 | N | 1
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-02-21 | Clayton | Atlanta | 251 Charles W Grant Pkwy | 9675 | Raw Sewage | GA0038423 | Collection System | Grease/roots caused blockage. | Flint | Mud Creek | 33.640731 | -84.398532 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-21 | DeKalb | Clarkston | 629 Ridgecreek Dr Clarkston 30021 | 240300 | Raw Sewage | GA0024147 | Collection System | Found manhole #18-045-s008 spilling into Indian Creek due to an unknown blockage | Ocmulgee | Indian Creek | 33.794907 | -84.251370 | N | 1
Columbus Water Works (South WRF) | 2025-02-21 | Muscogee | Columbus | 8125 Marne Rd. | 356 | Raw Sewage | GA0020516 | Collection System | A blockage in the main was the cause of a spill into the Armory Creek in the Lower Upatoi Creek Basin. | Chattahoochee | Armory Creek | 32.372286 | -84.922687 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-21 | DeKalb | Lithonia | 2582 Kelly St Lithonia 30058 | 0 | Raw Sewage | GA0024147 | Collection System | Found private manhole spilling into pine mountain creek due to a grease blockage | Ocmulgee | Pine Mountain Creek | 33.710468 | -84.100496 | N | 1
Broxton, City of (Broxton WPCP) | 2025-02-19 | Coffee | Broxton | Meadow (Lisa) Lane Lift Station | 50000 |  | GAJ020124 | Pump Station | Debris was clogging the pumps causing the pumps to short circuit. | Satilla | Unnamed Tributary to Little Red Bluff Creek | 31.631607 | -82.904456 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-19 | DeKalb | Stone Mountain | 5100 E Ponce De Leon Stone Mountain Ga 30083 | 1080 | Raw Sewage | GA0024147 | Collection System | Found manhole #18-140-s01 with evidence of a sewer spill due to a grease blockage | Ocmulgee | South Fork Peachtree Creek | 33.820483 | -84.211501 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-02-19 | Cobb | Marietta | 1400 Marietta Country Club Dr., 120 gallons; Noonday Creek | 120 | Raw Sewage | GA0026140 | Collection System | Gravel | Chattahoochee | Noonday Creek | 33.991912 | -84.624253 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-18 | Fulton | Atlanta | 3057 Delmar Ln NW | 2150 |  | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Sandy Creek | 33.755804 | -84.490130 | N | 1
Augusta, City of (J.B. Messerly WPCP) | 2025-02-18 | Richmond | Augusta | 2260 Wrightsboro Rd | 555 | raw sewage | GA0037621 | Collection System | grease and rags of debris | Savannah | Oates Creek | 33.466030 | -82.021074 | N | 1
Smyrna (City of)- Sewers | 2025-02-18 | Cobb | Smyrna | 3464 Vinings North Trail | 5000 | Raw Sewage | GAU060035 | Collection System | Blockage in manhole | Chattahoochee | Nickajack Creek | 33.928279 | -84.559990 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-18 | DeKalb | Lithonia | 7153 Woodstone Dr Lithonia 30058 | 50 | Raw Sewage | GA0024147 | Collection System | Found 4in private clean out surcharging with evidence of an overflow due to an unknown blockage | Ocmulgee | Pole Bridge Creek | 33.778473 | -84.106878 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-18 | Fulton | Atlanta | 890 Curran St NW | 176 | raw sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Peachtree Creek | 33.778985 | -84.409043 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-17 | DeKalb | Decatur | 2557 Columbia Dr Decatur 30034 | 100 | Raw Sewage | GA0024147 | Collection System | County contractor bypass pump spilled into storm drain due to a damaged sewer hose | Ocmulgee | Cobb Fowler Creek | 33.712590 | -84.262790 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-17 | DeKalb | Decatur | 4236 Liffey Lane Decatur 30034 | 100 | Raw Sewage | GA0024147 | Collection System | Found 4in private clean out overflowing due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.696150 | -84.225996 | N | 1
Cobb County Water System (R.L. Sutton WRF) | 2025-02-17 | Cobb | Marietta | 2932 Canton Rd NE, Marietta, GA 30066 | 110 | Raw Sewage | GA0026140 | Collection System | Grease | Chattahoochee | Noonday Creek | 33.997850 | -84.523936 | N | 1
Douglasville-Douglas County Water & Sewerage Authority (South Central WPCP) | 2025-02-16 | Douglas | Douglasville | 3434 Pinemont Dr. | 8000 |  | GA0038709 | Collection System | Heavy storms in area caused widespread power outages. Generator transfer switch malfunctioned and did not switch to generator power correctly. Mechanic had to manually switch to backup power when he arrived on site. | Chattahoochee | Anneewakee Creek | 33.712680 | -84.718044 | N | 1
Warner Robins, City of (Sandy Run Creek WPCP) | 2025-02-16 | Houston | Warner Robins | 213 Rusty Road | 500 | raw sewage | GA0030325 | Collection System | blocked force main | Flint | did not enter state waters | 32.591480 | -83.650603 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-16 | Fulton | Atlanta | 595 Peyton Rd SW | 20 | raw sewage | GA0039012 | Collection System | rain induced | Chattahoochee | Did Not Enter State Waters | 33.740082 | -84.483020 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-16 | DeKalb | Decatur | 3230 Boring Rd Decatur 30034 | 34006 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole #15-070-s016 spilled into Shoal Creek during heavy rain event | Oconee | Shoal Creek | 33.684165 | -84.258608 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-16 | DeKalb | Decatur | 3391 Warbler Dr Decatur 30034 | 36995 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole #15-091-s039 spilled into Cobbs Creek during heavy rain event | Ocmulgee | Cobbs Creek | 33.691752 | -84.259473 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-02-14 | Fulton | Roswell | 575 Riverside Road Roswell, GA 30075 | 509480 |  | GA0024333 | Collection System | Mechanical/Power Failure at Wastewater Treatment Plant Big Creek | Chattahoochee | Chattahoochee River | 34.006521 | -84.346648 | N | 1
Rockdale County Water Resources (Quigg Branch WPCP) | 2025-02-14 | Rockdale | Conyers | 1325 HWY 212 | 18900 | Raw Sewage | GA0047678 | Collection System | Ragging and debris | Ocmulgee | Bailey Creek | 33.559106 | -84.033140 | N | 1
Ashburn, City of (Airport WPCP) | 2025-02-14 | Turner | Ashburn | Rockhouse Rd and Sylvia Dr. | 5000 | Raw Sewage | GA0025852 | Collection System | Infiltration entering the wastewater system | Suwannee | Hat Creek | 31.691673 | -83.632582 | N | 1
Columbus Water Works (South WRF) | 2025-02-14 | Muscogee | Columbus | 514 Hartsock Loop | 266 | Raw Sewage | GA0020516 | Collection System | Debris in a main resulted in a discharge into Armory Creek. The basin is Lower Upatoi Creek Basin. | Chattahoochee | Armory Creek | 32.362071 | -84.927735 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-14 | Fulton | Atlanta | 3581 Revere Rd SW | 602 | raw sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Utoy Creek | 33.707539 | -84.506779 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-14 | DeKalb | Decatur | 4001 Dogwood Farm Road Decatur 30034 | 846100 | Raw Sewage | GA0024147 | Collection System | Rainwater entered the sewer system during the heavy rain event on 2/12/2025 causing manhole 15-031-s001 to spill into Snapfinger Creek | Ocmulgee | Snapfinger Creek | 33.665528 | -84.220825 | N | 1
Peachtree City Water & Sewerage Authority (Larry B. Turner WRF) | 2025-02-13 | Fayette | peachtree city | Village Green Frisbee Park Willowbend RD | 2000 |  | GA0035777 | Collection System | very Heavy rain at time of manhole surcharge | Flint | unnamed creek to Lake Peachree | 33.399908 | -84.585944 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 |  |  | 2646 Defoors Ferry Rd NW | 1150 |  | GA0039012 | Collection System | rain induced | Chattahoochee | Peachtree Creek |  |  | N | 1
Clarkesville, City of (Clarkesville WPCP) | 2025-02-13 | Habersham | Clarkesville | 307 Mary St Manhole to the right side of property | 7800 |  | GA0032514 | WWTP | MAJOR RAIN event caused flooding which caused sever Infiltration and Inflow of sewer line that dumps into a sewer trunk main that was submerged under flood waters from soque river inside of city park, address 221 Sam Pitts Circle | Chattahoochee | Soque River | 34.620190 | -83.525850 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 255 South Columbia Dr Decatur 30030 | 392 |  | GA0024147 | Collection System | Flow monitoring data showed that manhole 15-234-s145 spilled into Shoal Creek during a heavy rain event on 2/13/2025 | Ocmulgee | Shoal Creek | 33.769424 | -84.296988 | N | 1
Dalton Utilities - Riverbend Land Application Site | 2025-02-13 | Whitfield | Tunnel Hill | Old Cottonwood Mill Road, Tunnel Hill Dalton Utilities Pump Station | 1500 |  | GAJ020056 | WWTP | Pump failure | Coosa | Tanyard Creek | 34.833350 | -85.057930 | N | 1
Gwinnett County Board of Commissioners (F. Wayne Hill WRC) | 2025-02-13 | Gwinnett | Norcross | 6624 Dawson Blvd | 9810 |  | GA0038130 | Collection System | debris | Chattahoochee | North Fork Peachtree Creek | 33.908397 | -84.228678 | N | 1
Cedartown, City of (Cedartown WPCP) | 2025-02-13 | Polk | Cedartown | In the field 50 yards East of the intersection of Spruce St. and W. Fairmount Ave. | 4000 |  | GA0024074 | WWTP | Entire sewer system was overwhelmed and flooded out by heavy rains. | Coosa | Did not enter state waters | 34.018240 | -85.263660 | N | 1
Douglasville-Douglas County Water & Sewerage Authority (South Central WPCP) | 2025-02-13 | Douglas | Douglasville | 3279 Twin Peaks Dr. | 31500 |  | GA0038709 | Lift Station | Major Storm and flooding caused high sewer flows and gravity sewer line did not have the capacity to carry them. This is the 20” gravity line that is carrying bypass flows from Southside Lift Station while force main work is ongoing. | Chattahoochee | Anneewakee Creek | 33.689370 | -84.681980 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Clarkston | 3902 Memorial College Avenue Clarkston 30021 | 49674 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole #18-068-s055 spill during heavy rain event on 2/13/2025 | Ocmulgee | Snapfinger Creek | 33.796944 | -84.239542 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Atlanta | 1078 Beech Haven Rd Atlanta 30324 | 738 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data shows that manhole 18-108-s007 spilled into North fork Peachtree creek during rain event on 2-13-2025 | Ocmulgee | North Fork Peachtree Creek | 33.820060 | -84.355797 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 4531 Riverwood Forest Court Decatur 30035 | 141885 | Raw Sewage | GA0024147 | Collection System | Found broken 8in sewer main creek between manhole 15-130-s002 and manhole 15-130-s003 | Ocmulgee | Snapfinger Creek | 33.721992 | -84.215525 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 1496 Country Squire Dr Decatur 30033 | 36442 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole 18-147-085 spilled into Burnt Fork Creek during a heavy rain event on 2/13/2025 | Ocmulgee | Burnt Fork Creek | 33.824456 | -84.283021 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 2313 Springdale Rd SW | 600 | Raw sewage | GA0039012 | Collection System | debris in the mainline | Upper Ocmulgee | South River | 33.691530 | -84.417168 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 2665 Colgan Ct SE | 221 | raw sewage | GA0039012 | Collection System | debris in the mainline | Upper Ocmulgee | Sugar Creek | 33.747827 | -84.302462 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 595 Peyton Rd SW | 200 | raw sewage | GA0039012 | Collection System | rain induced | Chattahoochee | Utoy Creek | 33.740082 | -84.483020 | N | 1
Columbus Water Works (South WRF) | 2025-02-13 | Muscogee | Columbus | 5601 Gateway Dr. | 923 | Raw Sewage | GA0020516 | Lift Station | Hydraulic loading due to excessive rain caused a sanitary sewer overflow that resulted in a discharge into Bull Creek Tributary. The basin is Cooper Creek Basin. | Chattahoochee | Bull Creek Tributary | 32.526435 | -84.888616 | N | 1
Fulton County Department of Public Works (Big Creek WRF) | 2025-02-13 | Fulton | Roswell | 910 Oakhaven Drive | 5550 | Raw Sewage | GA0024333 | Collection System | Heavy Rains Caused the creek to overflow their banks and inundate the sewer system along rocky creek | Chattahoochee | Rocky Creek | 34.086766 | -84.390213 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Ellenwood | 4124 Flakes Mill Rd | 99000 | Raw Sewage | GA0024147 | Collection System | Manhole #15-035-s836 spilling due to heavy inflow and infiltration. | Ocmulgee | South River | 33.665424 | -84.234350 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Doraville | 3001 McCall Dr Doraville 30340 | 290025 | Raw Sewage | GA0024147 | Collection System | Found manhole 18-313-s072 spilling due to an unknown blockage | Chattahoochee | North Fork Peachtree Creek | 33.897189 | -84.267896 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 596 Peyton Rd SW | 596 | raw sewage | GA0039012 | Collection System | rain induced | Chattahoochee | Utoy Creek | 33.739577 | -84.479262 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 2556 Defoors Ferry Rd NW | 2650 | raw sewage | GA0039012 | Collection System | rain induced | Chattahoochee | Peachtree Creek | 33.821996 | -84.443206 | N | 1
Stockbridge, City of (Stephen D. Peurifoy WPCP) | 2025-02-13 | Henry | Stockbridge | 100 Stapleton Dr. Stockbridge, GA 30281 | 46500 | Raw Sewage | GA0023337 | Collection System | Infiltration from 4.4 inches of rain in a twelve-hour period | Ocmulgee | Brush Creek | 33.556669 | -84.229269 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Stone Mountain | 988 Fellsridge Ct Stone Mountain Ga 30083 | 3880 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data shows that manhole #18-092-s044 spilled during heavy rain event on 2-13-2025 | Ocmulgee | Snapfinger Creek | 33.807129 | -84.207943 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Lithonia | 2340 Cherokee Valley Drive Lithonia 30058 | 10 | Raw Sewage | GA0024147 | Collection System | Found evidence of an overflow at 4in private cleanout due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.721221 | -84.148430 | N | 1
LaGrange, City of (Long Cane Creek WPCP) | 2025-02-13 | Troup | LaGrange | 1514 Old Hutchinson Mill Rd. [Long Cane WPCP] | 3300 | Raw Sewage | GA0036951 | WWTP | Excessive sludge blanket in the secondary clarifiers flowed to the filters and lead to overflow from filters. Overflow spill mostly drained to a drop inlet which discharged into the plant influent and the rest infiltrated into the ground. None of the spill flowed into a creek. | Chattahoochee | Did Not Enter State Waters | 32.970443 | -85.078786 | N | 1
Stockbridge, City of (Stephen D. Peurifoy WPCP) | 2025-02-13 | Henry | Stockbridge | 678 Fairhaven Blvd. Stockbridge, GA 30281 | 2375 | Raw Sewage | GA0023337 | Collection System | Infiltration from 4.4 inches of rain in a twelve-hour period | Ocmulgee | Tributary of Reeves Creek | 33.541358 | -84.239073 | N | 1
Fayetteville, City of (Whitewater Creek WPCP) | 2025-02-13 | Fayette | fayetteville | 190 Price Road, Fayetteville Georgia | 4500 | raw sewage | GA0035807 | Lift Station | The overflow was due to a blown fuse at the transformer and some infiltration of storm flow from the recent rain we received. Please note that no start time was available. The spill estimate is based on the area impacted. | Flint | did not enter state waters | 33.425582 | -84.456708 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Tucker | 3924 Roman Ct Tucker 30084 | 536 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole 18-167-s028 spilled into South Fork Peachtree Creek | Ocmulgee | South Fork Peachtree Creek | 33.836724 | -84.238570 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 1809 Brewer Blvd SW | 200 | raw sewage | GA0039012 | Collection System | rain induced | Upper Ocmulgee | South River | 33.704945 | -84.415258 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 4474 Riverwood Forest Court Decatur 30035 | 141885 | Raw Sewage | GA0024147 | Collection System | Found 8in sewer main broken between manhole 15-130-s002 and manhole 15-130-s003 spilling Snapfinger Creek | Ocmulgee | Snapfinger Creek | 33.722657 | -84.207108 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 1160 Peachtree Battle Ave NW | 596 | raw sewage | GA0039012 | Collection System | collapsed mainline | Chattahoochee | Peachtree Creek | 33.825070 | -84.428437 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 2359 Harrington Dr Decatur 30033 | 158567 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole 18-101-s073 into south fork peachtree creek during heavy rain event on 2/13/2025 | Ocmulgee | South Fork Peachtree Creek | 33.807247 | -84.296582 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Lithonia | 4664 Flat Bridge Rd Lithonia | 2395453 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole #11-251-s012 and 11-251-s010 spilled into Pole Bridge Creek during a heavy rain event | Ocmulgee | Pole Bridge Creek | 33.645574 | -84.160638 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-13 | Fulton | Atlanta | 1494 Memorial Dr SE | 4330 | raw sewage | GA0039012 | Collection System | rain-induced | Upper Ocmulgee | Sugar Creek | 33.748003 | -84.340828 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-13 | DeKalb | Decatur | 217 Green St Decatur 30030 | 2070 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole 15-214-s003 and 15-214-s005 spilled into Shoal Creek during heavy rain event on 2/13/2025 | Ocmulgee | Shoal Creek | 33.761932 | -84.304110 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Lithonia | 4557 Meadow Creek Path Lithonia 30038 | 3425625 |  | GA0024147 | Collection System | Flow monitoring data showed manhole 15-034-s090, 15-034-s134a, and 15-034-s170 spilled into snapfinger creek | Ocmulgee | Snapfinger Creek | 33.669500 | -84.217926 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 2646 Defoors Ferry Rd NW | 2040 |  | GA0039012 | Collection System | rain-induced | Chattahoochee | Peachtree Creek | 33.821622 | -84.446090 | N | 1
Monroe, City of (Jack's Creek WPCP) | 2025-02-12 | Walton | Monroe | 590 Vine St- Vine St Pump Station | 189000 |  | GA0047171 | Lift Station | surcharge because of rain | Oconee | tributary to Alcovy River | 33.764529 | -83.721039 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 3391 Warbler Dr Decatur 30034 | 570592 |  | GA0024147 | Collection System | Flow monitoring data showed manhole 15-091-s039 spilled into Cobbs Creek during a heavy rain event. | Ocmulgee | Cobbs Creek | 33.691752 | -84.259473 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 169 Woodbine Cir SE | 2390 |  | GA0039012 | Collection System | rain-induced | Upper Ocmulgee | Sugar Creek | 33.749394 | -84.341330 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 2556 Defoors Ferry Rd NW | 1025 |  | GA0039012 | Collection System | rain-induced | Chattahoochee | Peachtree Creek | 33.821996 | -84.443206 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 1828 Giben Rd SW | 3000 |  | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Did Not Enter State Waters | 33.705766 | -84.402978 | N | 1
Paulding County Board of Commissioners (Coppermine Road WRF) | 2025-02-12 | Paulding | Dallas | 678 Due West Rd. 1st manhole South of Due West Lift Station. | 9000 |  | GA0038865 | WWRF | Excessive flows during peak | Coosa | Possum Creek | 33.962530 | -84.780080 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 3230 Boring Road Decatur 30034 | 473421 |  | GA0024147 | Collection System | Flow monitoring data showed manhole 15-070-s016 spilled into Shoal Creek during a heavy rain event | Ocmulgee | Shoal Creek | 33.684165 | -84.258608 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 611 3rd Ave Decatur 30030 | 32533 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole #15-213-s050 spilled into Sugar Creek during a heavy rain event on 2-12-2025 | Ocmulgee | Sugar creek | 33.756991 | -84.318903 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 2711 Fairlee Drive, Decatur 30032 | 312453 | Raw Sewage | GA0024147 | Collection System | Found manhole #15-184-s002 and manhole #15-184-s806 spilled into Shoal Creek due to a heavy rain event. | Ocmulgee | Shoal Creek | 33.746614 | -84.289300 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Pine Lake | 429 Magnolia Drive Pine Lake 30072 | 300 | Raw Sewage | GA0024147 | Collection System | found 4in private cleanout surcharging with evidence of an overflow due to an unknown blockage | Ocmulgee | Did Not Enter State Waters | 33.787469 | -84.205280 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 3075 Thrasher Cir Decatur 30032 | 302323 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole 15-136-s038 spilled into shoal creek | Ocmulgee | Shoal Creek | 33.717343 | -84.274292 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | atlanta | 1707 childerlee lane atlanta 30329 | 11582 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole 18-157-s026 spilled into north fork peachtree creek | Ocmulgee | North Fork Peachtree Creek | 33.831839 | -84.334573 | N | 1
Columbus Water Works (South WRF) | 2025-02-12 | Muscogee | Columbus | 5187 Kingsberry Ln. | 447 | Raw Sewage | GA0020516 | Collection System | Debris caused a stop-up in a main that resulted in a discharge into Bull Creek Tributary. The basin is Mill Branch Basin. | Chattahoochee | Bull Creek Tributary | 32.478283 | -84.903788 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 2480 Miriam Lane Decatur 30032 | 270191 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data shows manhole 15-136-s013 spilled into Shoal Creek during a heavy rain event on 2/13/2025 | Ocmulgee | Shoal Creek | 33.722715 | -84.265853 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 1157 Regis Rd SE | 300 | raw sewage | GA0039012 | Collection System | debris in mainline | Chattahoochee | Did Not Enter State Waters | 33.690459 | -84.353075 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 3549 Panthersville Rd Decatur 30034 | 593557 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed manhole #15-073-s006 and manhole #15-073-s010 spilled during heavy rain event on 2/13/2025 | Ocmulgee | South River | 33.682702 | -84.283160 | N | 1
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-02-12 | Clayton | Forest Park | 4343 Sierra Dr. | 23350 | Raw Sewage | GA0038423 | Collection System | Severe rain and flooding caused a hydraulic overload on the sanitary sewer collection system. Crews documented the event for correct reporting. | Ocmulgee | Poole Creek | 33.636045 | -84.366263 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 2223 Pinewood Dr Decatur 30032 | 19100 | Raw Sewage | GA0024147 | Collection System | found manhole #15-150-s080 spilled into Doolittle Creek | Ocmulgee | Doolittle Creek | 33.726684 | -84.309483 | N | 1
Winder, City of (Cedar Creek WPCP) | 2025-02-12 | Barrow | Winder | Fort Yargo State Park | 10000 | Raw Sewage | GA0038776 | Collection System | extreme amount of rainfall during short period of time that led to infiltration in the sewer system | Oconee | Fort Yargo Lake | 33.968321 | -83.732403 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 489 Sterling St NE | 900 | Raw Sewage | GA0039012 | Collection System | rain-induced site | Chattahoochee | Did Not Enter State Waters | 33.767531 | -84.347047 | N | 1
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-02-12 | Fulton | Atlanta | 354 Leland Ter NE | 25 | Raw Sewage | GA0039012 | Collection System | debris and grease in the mainline | Chattahoochee | Did Not Enter State Waters | 33.763587 | -84.316385 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Decatur | 2925 Misty Waters Dr Decatur 30032 | 56715 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data showed that manhole 15-136-s057 spilled into shoal creek during a heavy rain event | Ocmulgee | Shoal Creek | 33.718022 | -84.279410 | N | 1
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-02-12 | DeKalb | Lithonia | 5106 Klondike Rd, Lithonia, 30038 | 407452 | Raw Sewage | GA0024147 | Collection System | Flow monitoring data shows that manhole 11-218-s003 and 11-218-s004 spilled in to Pole Bridge Creek caused by I&I from the recent rain event. | Ocmulgee | Pole Bridge Creek | 33.629871 | -84.136692 | N | 1