Hurricane Irma Incidents - 2 |  | Hurricane Irma had catastrophic statewide impacts, including historic rainfall, unprecedented river surges and flooding. JEA is continuing damage assessment of its water, wastewater and reuse systems. JEA is providing updates as assessments are completed. For more information go to jea.com. JEA has identified the following incidents that resulted during these extreme conditions. I. Sanitary Sewer Overflow Incidents: a. Incident Address: 7150 Civic Club Road, Jacksonville FL 32219 at approximately 12:00 am on 9/11/17 JEA identified a lift station causing a release to Little Trout River. Amount to be determined. b. Incident Address: 7732 Merrill Road, Jacksonville FL 32211 at approximately 12:00 am on 9/11/17 JEA identified a lift station causing a release to Strawberry Creek. Amount to be determined. c. Incident Address: 847 Hickory Hill, Jacksonville FL 32221 at approximately 12:00 am on 9/11/17 JEA identified a lift station causing a release from a lift station to Wills Branch Creek. Amount to be determined. d. Incident Address: 220 Mercer Circle S., Jacksonville FL 32217 at approximately 12:00 am on 9/11/17 JEA identified a manhole overflow into Christopher Creek. Approximately 29,700 gallons. e. Incident Address: San Jose Blvd and Morvenwood Rd, Jacksonville FL 32210 at approximately 12:00 am on 9/11/17 JEA identified a manhole overflow release to storm drain to St. Johns River. Approximately 1,000 gallons. f. Incident Address: 3421 Indian Creek Blvd, Jacksonville FL 32259 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing release to marsh. Amount to be determined. g. Incident Address: 74 Baisden Rd., Jacksonville FL 32218 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing a release into a tributary to Broward River. Approximately 100 gallons. h. Incident Address: 111247 Beacon Dr., Jacksonville FL 32225 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing a release into the St. Johns River. Approximately 110,000 gallons. i. Incident Address: 8052 Arlington Expressway, Jacksonville FL 32211 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing a release into Strawberry Creek. Approximately 17,000 gallons. j. Incident Address: 4526 Detaille St., Jacksonville FL 32209 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing a release to Ribault River. Approximately 190,000 gallons. k. Incident Address: 12583 Arrowleaf Dr., Jacksonville FL 32225 at approximately 12:00 am on 9/11/17 JEA identified power outage at a lift station causing a release to pond connecting to Mt. Pleasant Creek. Approximately 19,100 gallons. l. Incident Address: 5565 Bristol Bay Ln., Jacksonville FL 32244 at approximately 12:00 am on 9/11/17 JEA identified manhole overflow to storm drain causing a release to pond connecting to Little Ortega River. Amount to be determined. m. Incident Address: 8104 Argyle Forest Blvd., Jacksonville FL 32244 at approximately 12:00 am on 9/11/17 JEA identified a lift station causing a release to a swamp to the Ortega River. Approximately 25,000 gallons. See https://www.jea.com/environment/environmental_incident_reporting/ for more details. | 09/13/2017 06:33 PM | JEA | 21 W Church St.; Jacksonville FL; 32206 |  | Alan Tablada | Manager, Environmental Incident Response | tablas@jea.com | (904) 703-0425 |  | Environmental | Alan Tablada | (904) 703-0425 |  | tablas@jea.com | 09/11/2017 12:00 AM |  | Duval, St. Johns |  | N | 30.330532 | -81.657198 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=443
Manhole Overflow - 2326 Seton Lane | 20177489 | CITY MANHOLE OVERFLOWING DUE TO LIFT STATION FAILURE. LIFT STATION 19 WAS RESPONDED TO BY CITY STAFF AND WAS IN HIGH WELL STATUS. STAFF FOUND DAMAGED TELEMETRY CONTROL UNIT. TELEMETRY CONTROL UNIT WAS REPLACED AND LIFT STATION BEGAN PUMPING. HURRICANE IRMA, WHICH GENERATED WIDESPREAD POWER OUTAGES AND DAMAGE TO PHYSICAL PROPERTY, THOUGHT TO BE THE CAUSE. | 09/13/2017 05:38 PM | FL0026603 - Lift Station #19 | 12760 Indian Rocks Rd.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/12/2017 10:45 AM | 09/12/2017 11:00 AM | Pinellas |  | N | 27.896956 | -82.833124 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=442
City of Cape Canaveral 601 Thurm Blvd. Cape Canaveral, FL | 20177447 | Approximately 180,764 gallons of partially treated Raw sludge was spilled at the City of Cape Canaveral Water Reclamation Facility due to a flooded intermediate pumping station. Initial Report: On September 10, 2017 at approximately 1330 ET the intermediate pumping station became overwhelmed with flow from the heavy rain bands coming off of Hurricane Irma. This caused the plant lift station #13 to backup overflowing into the plant parking area and the Plant Operation building 1st floor. The spill was contained to the plant site. When the rain ceased the parking area manholes were open and the spill was drain back into the plant. The building cleanout was opened to drain the building spill back through the plant. On September 11, 2017 1330 ET the intermediate pumping station resumed normal operations. | 09/13/2017 05:36 PM | City of Cape Canaveral Water Reclamation Facility | 601 Thurm Blvd.; Cape Canaveral FL; 32920 |  | June A. Clarl | Water Reclamation Plant Supervisor | J.Clark@cityofcapecanaveral.org | (321) 868-1240 | 405 | Operator Of the Facility | Ralph Lotspeich | (321) 868-1240 |  | R.Lotspeich@cityofcapecanaveral.org | 09/10/2017 01:30 PM | 09/11/2017 01:30 PM | Brevard |  |  | 28.392172 | -80.617712 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=441
PCU DS168 9.11.17 | 20177250 | Manholes overflowed associated to pump station 168 located at 6990 125th Street N. Started at 9/11/17 @ 10:00 and ceased at 9/12/17 at 06:14. Generators in place and/or rotated until power was restored - debris clean-up as needed. Waterway Affected: Intracoastal Waterway & retention pond.Samples met state surface water bacteriological criteria. Signs have been removed. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount: 259,725 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions. (DEP Incident #440) tied to DEP Incident # 376 Pump Station 168 Power Outage - calls from 13030 Poinsettia Avenue 6719 121st Street North 6910 121st Street North 13310 72nd Terrace North | 09/13/2017 05:31 PM | South Cross Bayou AWRF (FL0040436) | 7401 54th Avenue North, St Petersburg, FL 33709-1374; St Petersburg FL; 33709 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:15 AM | 09/12/2017 06:15 AM | Pinellas |  | N | 27.833929 | -82.806153 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=440
Private System Manhole Overflow - Eastwood Shores Condos |  | THE PRIVATE MANHOLE AT BUILDING 500 OF EASTWOOD SHORES CONDOMINIUMS WAS OVERFLOWING INTO THE STORM WATER CHANNEL AND PROCEEDING TO BAY WATERS NEAR THE FISHING PIER. HURRICANE IRMA CAUSED POWER OUTAGES TO THE AREA AND THIS PRIVATE LIFT STATION LOST POWER. STAFF WILL CONTINUE TO MONITOR THIS CONTINUOUS OVERFLOW UNTIL POWER IS RESTORED TO THE LIFT STATION AND THE OVERFLOW CEASES. SAMPLES WILL BE TAKEN AND SIGNS POSTED. | 09/13/2017 05:21 PM | Eastwood Shores Condominium - Private System | 1883 Lichen Lane; Largo FL; 33760 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 02:20 PM |  | Pinellas |  |  | 27.927606 | -82.716168 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=439
Manhole Overflow - Sun Point Place Apartments |  | THE PRIVATE MANHOLE LOCATED BESIDE THE PRIVATE LIFT STATION WAS OVERFLOWING INTO THE LARGO NATURE PRESERVE. HURRICANE IRMA CAUSED POWER OUTAGE TO THE GENERAL AREA AND THE LIFT STATION LOST POWER. STAFF CALLED THE PROPERTY MANAGER, BUT WAS UNABLE TO REACH HER BY PHONE. AWAITING POWER RESTORATION TO THE AREA. MONITORING SITUATION UNTIL POWER IS RESTORED. SAMPLES WILL BE TAKEN AND SIGNS POSTED. | 09/13/2017 05:12 PM | Private Owner | 701 East Bay Drive; Largo FL; 33770 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 11:35 AM | 09/11/2017 09:30 PM | Pinellas |  |  | 27.916008 | -82.777185 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=438
EWRF 4; 9-11-2017 | 20177226 | On September 11th at approximately 7:45 pm, plant Influent flow increased to over 40 MGD peak hourly flows. This in turn caused high flows throughout the Plant and subsequently caused the Phase III Automatic Backwash Filters to overflow into the plant¿s sanitary sewer system which became surcharged. This caused a nearby man hole to overflow in front of Clarifiers 7&8. At the time of the overflow, Clarifiers 7&8 were draining back to the lift station. Approximately 6,000 gallon of return activated sludge pushed out of the manhole onto the drive way where it was contained. Plant staff stopped draining the clarifiers and recovered the return activated sludge with the help of a vactor truck crew and washed down the area with 3,000 gallons of water. | 09/13/2017 04:57 PM | OCU East Water Reclamation Facility | 1621 S. Alafaya Trail; Orlando FL; 32828 |  | Laura Woodbury | Sr. Eng, OCU Field Services | laura.woodbury@ocfl.net | (407) 836-6826 |  | Sr Eng, Field Services | Mark Robinson, Assistant Manager, WRD | (407) 254-6791 |  | Mark.Robinson@ocfl.net | 09/11/2017 07:45 PM | 09/11/2017 08:45 PM | Orange |  |  | 28.524294 | -81.201978 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=437
Lift Station #3 Overflow | 20177450 | Due to Hurricane Irma the City of Cocoa Beach still doesn't have power to many of our Lift Stations. We have crews going to each station and pumping them down with portable generators. Our crew was at Lift Station #14 pumping it down when other crew members noticed Lift Station #3 overflowing. (Lift Station #14 pumps into Lift Station #3). Lift Station #3 was receiving FPL power so crews headed to Lift Station #14. The crew was unaware that during transport to Lift Station #14, Lift Station #3 lost FPL power. The pumps at Lift Station #14 were on for 30 min and we estimate a flow of 1500 Gallons of sewage was spilled out of Lift Station #3 onto the road at 13 Street South. | 09/13/2017 04:51 PM | Lift Station #3 | Corner of 13 Street South and South Orlando Avenue; Cocoa Beach FL; 32931 |  | Brad Kalsow | Operations Manager | bkalsow@cityofcocoabeach.com | (321) 868-3321 |  | Operator Of the Facility | Brad Kalsow | (321) 868-3321 |  | bkalsow@cityofcocoabeach.com | 09/13/2017 01:35 PM | 09/13/2017 02:05 PM | Brevard |  |  | 28.294961 | -80.609875 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=436
Manhole Overflow - 4054 Church Creek Pt. | 20177342 | HURRICANE IRMA CAUSED CITY OF LARGO LIFT STATION 15 TO LOSE POWER. THE BACKUP GENERATOR DID NOT COME ON AS EXPECTED, RESULTING IN AN OVERFLOW OF AN UPSTREAM MANHOLE. STAFF REPLACED THE GENERATOR AND THE OVERFLOW STOPPED. STAFF ARE INVESTIGATING THE REASON THE BACKUP GENERATOR FAILED TO OPERATE AS PLANNED. SAMPLES WILL BE COLLECTED AND SIGNS WILL BE POSTED. | 09/13/2017 04:50 PM | FL0026603 - Lift Station #15 | 3476 Adrian Ave.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 12:10 PM | 09/11/2017 02:10 PM | Pinellas |  |  | 27.898612 | -82.828711 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=435
Manhole Overflow - 1942 Cove Drive | 20177340 | HURRICANE IRMA CAUSED CITY OF LARGO LIFT STATION #15 TO LOSE POSER . THE BACKUP GENERATOR DID NOT COME ON AND THEREFORE A MANHOLE UPSTREAM OVERFLOWED. STAFF REPLACED THE GENERATOR AT LS 15 AND THE OVERFLOW CEASED. STAFF ARE ALSO INVESTIGATING WHY THE BACKUP GENERATOR FAILED TO COME ON AS EXPECTED. SAMPLES WILL BE COLLECTED AND SIGNS POSTED. | 09/13/2017 04:41 PM | FL0026603 - Lift Station #15 | 3476 Adrian Ave.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 12:05 PM | 09/11/2017 02:05 PM | Pinellas |  |  | 27.899379 | -82.827927 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=434
Manhole Overflow - 3884 Anglers Lane | 20177343 | HURRICANE IRMA CAUSED LIFT STATION 15 TO LOSE POWER AND BACKUP GENERATOR DID NOT COME ON WHICH CAUSED THE UPSTREAM MANHOLE(S) TO OVERFLOW. STAFF CHANGED OUT THE GENERATOR AND GOT THE LIFT STATION RUNNING AGAIN. STAFF IS LOOKING INTO THE CAUSE FOR GENERATOR FAILING TO START. | 09/13/2017 04:34 PM | FL0026603 - Lift Station #15 | 3476 Adrian Ave.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 11:35 AM | 09/11/2017 02:00 PM | Pinellas |  |  | 27.900027 | -82.826005 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=433
Manhole Overflow - 3884 Anglers Lane | 20177343 | HURRICANE IRMA CAUSED LIFT STATION 15 TO LOSE POWER AND BACKUP GENERATOR DID NOT COME ON WHICH CAUSED THE UPSTREAM MANHOLE(S) TO OVERFLOW. STAFF CHANGED OUT THE GENERATOR AND GOT THE LIFT STATION RUNNING AGAIN. STAFF IS LOOKING INTO THE CAUSE FOR GENERATOR FAILING TO START. | 09/13/2017 04:34 PM | FL0026603 - Lift Station #15 | 3476 Adrian Ave.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 11:35 AM | 09/11/2017 02:00 PM | Pinellas |  |  | 27.900027 | -82.826005 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=432
PCU DS-021 9.11.17 | 20177771 | Manholes overflowed associated to pump station 021 located at 10137 118th Avenue N., Largo. Started started at 11:01 ended at 11:30 on 9/11/17. Samples were collected on 9/12/17 ~ 1230 PM and signs posted; bacteriological results passed. Generators in place and/or rotated until power was restored - debris clean-up as needed. Waterway Affected: Lake Seminole. Spill amount: 29,755 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Pump Station 021 Power Outage - calls from 11755 101st Street 10136 118th Avenue | 09/13/2017 04:29 PM | South Cross Bayou AWRF (FL0040436) | 7401 54th Avenue North, St Petersburg, FL 33709-1374; St Petersburg FL; 33709 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:00 AM | 09/11/2017 11:30 AM | Pinellas |  | N | 27.878624 | -82.779256 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=431
Manhole Overflow - 1754 Indian Rocks Road | 20177336 | HURRICANE IRMA CASUED LIFT STATION 15 TO LOSE POWER. BACKUP GENERATOR DID NOT COME ON AS EXPECTED AND MANHOLE OVERFLOWED INTO WATERWAY. STAFF WERE ABLE TO CHANGE THE GENERATOR OUT AND GET THE STATION WORKING AGAIN, CAUSING THE OVERFLOW TO STOP. SAMPLES WILL BE COLLECTED AND SIGNS POSTED. | 09/13/2017 04:26 PM | FL0026603 - Lift Station #15 | 3476 Adrian Ave.; Largo FL; 33774 |  | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 09/11/2017 10:40 AM | 09/11/2017 02:00 PM | Pinellas |  |  | 27.901008 | -82.824428 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=430
Berth 13 Manifold Release, Port Everglades |  | On September 13th, 2017 at 0300 in Berth 13 of Port Everglades, Florida, a gasket failed on the manifold valve causing discharge to intercostal waterway. The activity was shutdown immediately with a discharged volume of less than 25 gallons. The spill contractor was notified while the location of discharge was cleaned. Proper authorities were contacted. To finalize, the U.S. Coast Guard inspected and approved the cleanup efforts. The vessel commenced pumping thereafter. | 09/13/2017 04:20 PM | South Florida Petroleum Services, LLC. | Berth 13, Port Everglades, Florida; Hollywood FL | Port Everglades, Berth 13 | Riley Boyle | Environmental & Regulatory Compliance Administrator | riley.boyle@vecenergy.com | (954) 278-9142 |  | Authorized Representative | Richard Vogel | (954) 278-9131 |  | richard.vogel@vecenergy.com | 09/13/2017 03:00 AM | 09/13/2017 03:05 AM | Broward |  |  | 26.091313 | -80.122703 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=429
loxahatchee river district | 20177325 | 2 inch force main was broke due to Hurricane Irma event; large tree when fell the root system pulled and broke pvc force main; when reported the section of force main was isolated by underground valve; area was caution taped off and lime disinfection; repair is pending; no visible sewage made to waterway and no storm basins present; was contained to small street and effected property | 09/13/2017 04:08 PM | loxahatchee river district | 2500 jupiter park drive; jupiter FL; 33458 |  | kevin skellenger | field superintendent | kevin.skellenger@lrced.org | (561) 747-5709 | 130 | field superintendent | albrey arrington | (561) 747-5700 |  | albrey@lrecd.org | 09/10/2017 12:00 AM | 09/11/2017 10:00 AM | Palm Beach |  |  | 26.953659 | -80.120853 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=428
Lift Station #2- Country Club Dr. | 20177334 | Hurricane IRMA caused a power outage at Lift Station #2, which caused two City manholes located upstream, to overflow. | 09/13/2017 04:02 PM | City of Largo WWRF | ; Largo FL | City Manhole #19-5095 and # 19-6010; located about 100 yards apart from each other off Country Club Dr. | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 09/11/2017 07:45 AM | 09/11/2017 09:10 AM | Pinellas |  |  | 27.913837 | -82.770583 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=427
Event 127 | 20177434 | Large amounts of debris came into the main plant lift station at once causing the pumps to rag up and the wastewater to spill out of a manhole and into a storm drain leading to Lake Conine. Staff installed a bypass pump and started working on clearing debris from the station. Cleaned up spill areas and spread lime. Ordered a larger bypass pump to pump the lift station to the headwork's during the lift station recovery process. | 09/13/2017 03:46 PM | Wastewater Treatment Plant # 2 | 2746 Motor Pool Road; Winter Haven FL; 33881 |  | Terry Carver | Wastewater Superintendent | Tcarver@mywinterhaven.com | (863) 291-5766 |  | Operator Of the Facility | Terry Carver | (863) 291-5766 |  | tcarver@mywinterhaven.com | 09/12/2017 10:00 AM | 09/12/2017 11:30 AM | Polk |  |  | 28.055378 | -81.72909 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=426
Treated Etoniah Creek Water Release to Wetlands | 20177403 | A cooling tower overflowed when an air valve failed in an open position due to a lockout at a nearby unloading station. The overflow consisted of approximately 3,000 gallons of treated Etoniah Creek water. The cooling tower water ran into a storm drain, a ditch and wooded area before reaching the storm water outfall to a nearby wetland. There is no associated risk to public health and safety or to the environment. | 09/13/2017 03:21 PM | Georgia-Pacific Consumer Operations LLC | 215 County Road 216; Palatka FL; 32177 |  | Ashleigh Thomas | Environmental Engineer | ashleigh.thomas@gapac.com | (386) 227-8166 |  | Environmental Engineer | Ashleigh Thomas | (386) 227-8166 |  | ashleigh.thomas@gapac.com | 09/13/2017 11:15 AM | 09/13/2017 11:45 AM | Putnam |  |  | 29.685746 | -81.677047 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=425
9130 Cypress Hollow Dr. |  | Lift Station was out of power, causing sewage to back up into road from 2 manholes and a cleanout. | 09/13/2017 03:09 PM | Cypress Hollow | 9130 Cypress Hollow Drive; Palm Beach Gardens FL; 33418 - 4524 | Northlake Boulevard to Cypress Hollow development. | Brent Weidenhamer | Wastewater Department Manager | bweidenhamer@sua.com | (561) 627-2900 | 494 | Wastewater Department Manager of Seacoast Utility | Brent Weidenhamer | (561) 627-2900 |  | bweidenhamer@sua.com | 09/13/2017 09:00 AM | 09/13/2017 10:30 AM | Palm Beach |  |  | 26.831707 | -80.137592 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=424
LS # 18 - Coastal Place 9/12/17 IRMA |  | Report of one manhole overflowing/seeping out from cover in front of 616 Parsons Terr. was reported on 9/12/17 at 8:12am. We immediately dispatched Vac truck to respond and start vacuuming out of LS # 18. On site by 8:45am, and continued vacuuming down station wet well to the bottom. Spillage immediately stopped after vacuuming out first load. We estimate 100-200 gallons max may have seeped out - very small neighborhood station. We will spread HTH, wash down and vacuum up wash down, today. | 09/13/2017 02:12 PM | City of Dunedin Lift Station # 18 - | 616 Parsons Terr; Dunedin FL; 34698 | Off of Keene Rd., turn west onto Coastal Place, south onto Parsons Terr. | Lance H. Parris | Wastewater Collection System Superinrtendent | Lparris@dunedinfl.net | (727) 298-3256 | 1624 | Operator Of the Facility | Lance H. Parris | (727) 298-3256 |  | lparris@dunedinfl.net | 09/12/2017 08:00 AM | 09/12/2017 09:00 AM | Pinellas |  |  | 28.009107 | -82.765942 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=423
Turbid Water Release | 20177294 | Stormwater from Hurricane Irma overwhelmed the capacity of a stormwater ditch. The ditch released an unknown quantity of turbid stormwater into an adjacent reclamation area connected to Brushy Creek. A turbidity measurement of the water in Brushy Creek at the closest accessible location downstream (approximately 1 mile) showed no turbidity impacts. Upon discovery of the release, measures were taken to stop the discharge from the ditch into the reclamation area. | 09/13/2017 02:00 PM | Mosaic - South Pasture Mine | 2220 Mineview Road; Bowling Green FL; 33834 |  | Scott Lehr | Manager, EHS Regulatory and Compliance | scott.lehr@mosaicco.com | (813) 500-6779 |  | Company Authorized Representative | Heather Nedley, Public Affairs & Community Manager | (863) 263-3100 |  | heather.nedley@mosaicco.com | 09/12/2017 10:50 AM | 09/12/2017 01:25 PM | Hardee |  |  | 27.562529 | -82.006637 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=422
TWA Lift Stations Outages Hurricane Irma 9-13-17 |  | Please see the list below, which includes dates, times, and locations of lift stations which experienced power outages due to Hurricane Irma. An undetermined amount of raw wastewater discharged on the ground. There may be potentially affected areas beyond the installation location. The public is advised to minimize contact with standing water as the full impact cannot be determined due to Hurricane Irma and the volume of storm recovery activities. Date Time Location Lift Station # 9/12/2017 10:57 AM 1700 Kenyon Circle 137 9/12/2017 11:00 AM 1430 Dogwood Court 47 9/12/2017 11:00 AM 1420 Dogwood Court 47 9/12/2017 11:15 AM 1401 Hiawatha Drive 33 9/12/2017 11:17 AM 30 Trotters Circle 18 9/12/2017 11:18 AM No Address 7 9/12/2017 11:21 AM Scrub Brush Court 25 9/12/2017 11:21 AM 515 Basil Court 88 9/12/2017 11:27 AM 770 Country Woods 81 9/12/2017 11:31 AM Pebble Point 88 9/12/2017 11:32 AM Kissimmee Bay Blvd. 69 9/12/2017 11:43 AM 753 Madiera Court 15 9/12/2017 11:44 AM 2708 Rivkin Drive 4 9/12/2017 12:15 PM 360 Sorrento Street 51 9/12/2017 12:51 PM 1038 Lake Berkley Drive 159 9/12/2017 12:52 PM 768 Del Prado 17 9/12/2017 2:14 PM Brighton Landings 5 9/12/2017 2:14 PM 2610 Deck Avenue 26 9/12/2017 2:17 PM 3530 Forest Ridge Lane 131 9/12/2017 2:29 PM 313 Morgan Way 4 9/12/2017 2:55 PM 149 Grand Canal Drive 116 9/12/2017 2:59 PM Bill Beck Blvd and Osceola Parkway 121 9/12/2017 3:06 PM Seratoga Subdivision 178 9/12/2017 3:19 PM 768 Del Prado 17 9/12/2017 3:22 PM Casanove Street 117 9/12/2017 3:23 PM 508 Basil Court 88 9/12/2017 4:17 PM 3366 Sandy Shore Lane 25 9/12/2017 4:49 PM 4947 Harold Stanley Drive 105 9/12/2017 4:53 PM 800 block of Grand Canal Drive 117 | 09/13/2017 01:55 PM | TWA South Bermuda/Cypress West/Lake Marion/Walnut WRF's | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5000 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5000 |  | environmental@tohowater.com | 09/12/2017 10:55 AM |  | Osceola, Polk |  |  | 28.324275 | -81.422876 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=421
407124 | 20177399 | WASD Incident #: 407124 Version: 1 Version Type: Preliminary Incident Version Created On: 09/13/17 12:31 PM Job Order #: 1003496291 Location of Discharge: 11331 SW 224 ST UNINCORPORATED MIAMI-DADE 33170 Reported by WASD Employee? Yes Employee ID: 00209637 Employee Title: PIPEFITTER SUPERVISOR Reported by: CHARLES DAVIS Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: East and West On: 224 ST Discharge Caused by Asset Type: Gravity Main Contractor Involved? No Discharge Due to/Caused by: Gravity Main Blocked Other Cause Additional Discharge Cause: DEBRIS Pipe Material: VCP (Vetrified Clay Pipe) Pipe Size in inches: 8 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Sunny Estimated Quantity of Sewage Released in Gallons: 3,000 Estimated Time Release Started: 09/13/17 08:30 AM Estimated Time Action Taken at Site: 09/13/17 08:45 AM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 09/13/17 10:00 AM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 09/13/17 08:45 AM Spill Recovered? Yes Recovered Amount in Gallons: 2,800 AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone MORGAN #2017-7399 09/13/17 12:54 PM RER RER Compliance Desk Phone NANCY 09/13/17 12:54 PM WASD WASD Jose Cueto Phone NOTIFIED 09/13/17 12:54 PM DEP DEP Notification Group E-mail 09/13/17 12:54 PM DOH DOH Notification Group E-mail 09/13/17 12:54 PM EPA EPA Notification Group E-mail 09/13/17 12:54 PM HMS Hazardous Materials Subcommittee Group E-mail 09/13/17 12:54 PM RER RER Notification Group E-mail 09/13/17 12:54 PM SFWM SFWM Notification Group E-mail 09/13/17 12:54 PM WASD WASD Interdepartmental Personnel E-mail 09/13/17 12:54 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Cynthia Carter (CCARTE) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.5590671354084 Longitude: -80.3746177570704 09/13/17 12:54 PM Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/13/2017 01:54 PM | Miami-Dade W&S Collection System | 11331 SW 224 ST ; Miami FL; 33170 |  | Charles Davis | Pipefitter Supervisor | charles.davis@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/13/2017 08:30 AM | 09/13/2017 10:00 AM | Miami-Dade |  |  | 25.558868 | -80.374906 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=420
LS # 31 - 2595 Indigo Dr. 9/12/17 IRMA |  | Report of one MH overflowing in front of 2699 Bellhurst Dr. received at 2:15pm on 9/12/17. Dispatched for generator that was being jockeyed from station to station. Generator set up and running by 3:30pm and light overflow of manhole stopped, with no further spillage. We estimate approx. 300 - 400 gallons max. Working on spreading HTH, washing down and vacuum up area, today. | 09/13/2017 01:48 PM | City of Dunedin Lift Station # 31 - 9/12/17 IRMA | 2699 Belhurst Dr. / LS #31; Clearwater FL; 34698 | Turn south off of Main St. / SR 580 onto Colony Dr., and west onto Bellhurst Dr. | Lance H. Parris | Wastewater Collection System Superinrtendent | Lparris@dunedinfl.net | (727) 298-3256 | 1624 | Operator Of the Facility | Lance H. Parris | (727) 298-3256 |  | lparris@dunedinfl.net | 09/12/2017 02:00 PM | 09/12/2017 03:30 PM | Pinellas |  |  | 28.018795 | -82.753434 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=419
L.S.52 Victoria Square, DeLand, untreat. domestic WW spill |  | Lift Station #52 (Victoria Square) located at 195 Dodge Avenue, DeLand, FL lost power during Hurricane Irma. Upon power-up, a surge of untreated domestic wastewater of less than 1,000 gallons intruded into a nearby business. | 09/13/2017 01:46 PM | DeLand/ Wiley M. Nash WRF | 1101 South Amelia Avenue; DeLand FL; 32724 |  | Alex Konoval | Deputy Utilities Director/ Environmental Compliance | konovala@deland.org | (386) 626-7254 |  | Deputy Utilities Director/ Environmental Comp. | James V. Ailes (Utilities Director) | (386) 626-7250 |  | ailesj@deland.org | 09/12/2017 04:00 PM | 09/12/2017 04:30 PM | Volusia |  |  | 28.996241 | -81.305251 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=418
LS # 4 Santa Barbara Dr. / Cevera 9/12/17 IRMA |  | 2 manholes upstream of Lift Station # 4 at intersection of Santa Barbara and Cevera Dr. overflowed approx. 200-300 gallons due to power outages following Irma. Immediately ran Vac truck to site to vacuum down MH, until by pass pumping could get set up. We will complete spreading of HTH, washing down and vacuuming up around this intersection today | 09/13/2017 01:31 PM | City of Dunedin Lift Station # 4 | 1688 Santa Barbara Dr. ; Dunedin FL; 34698 | Bayshore Blvd (Alt 19) to Cevera Dr. west to Santa Barbara - in intersection | Lance H. Parris | Wastewater Collection System Superinrtendent | Lparris@dunedinfl.net | (727) 298-3256 | 1624 | Operator Of the Facility | Lance H. Parris | (727) 298-3256 |  | lparris@dunedinfl.net | 09/12/2017 09:00 AM | 09/12/2017 10:30 AM | Pinellas |  |  | 28.031968 | -82.789715 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=417
LS # 20 Solon/Cottonwood 9/11/17 IRMA |  | North side of Solon Ave., between Beechwood Ct. and Cottonwood Terr. 3 manholes upstream of lift station were bubbling out fairly lightly, before we could get by pass pump set up following storm event, when lift station #20 lost power, during Hurricane Irma. We're estimating 500 - 700 gallons leaked out around manhole covers. We will complete spreading of HTH, washing down and vacuuming up areas around the 3 manholes today. | 09/13/2017 01:11 PM | City of Dunedin Lift Station # 20 | 1814 Solon Ave. ; Dunedin FL; 34698 | North side of Solon Ave., between Beechwood Ct. and Cottonwood Terr. 3 manholes upstream of lift station. | Lance H. Parris | Wastewater Collection System Superinrtendent | Lparris@dunedinfl.net | (727) 298-3256 | 1624 | Operator Of the Facility | Lance H. Parris | (727) 298-3256 |  | lparris@dunedinfl.net | 09/11/2017 08:00 AM | 09/11/2017 11:00 AM | Pinellas |  |  | 28.030518 | -82.753278 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=416
L.S.50 Lakeshore Trails, DeLand, untreat. domestic WW spill |  | Lift Station #50 (Lakeshore Trails) located at 7754 Royal Fern Circle/ Winterberry and Lift Station #85 (Lakes of DeLand) lost power during Hurricane Irma. A breach from a nearby stormwater line, fed by a cresting stormwater pond, also contributed to an already critical situation. When power was restored untreated domestic wastewater was released into a small residential area, the amount of which is impossible to be determined at this time. After speaking with the Lift Station Maintenance Superintendent, an amount of much less than 1,000 gallons was determined. Updated 09-28-17. | 09/13/2017 12:06 PM | DeLand/ Wiley M. Nash WRF (FL0020303) | 1101 South Amelia Avenue; DeLand FL; 32724 |  | Alex Konoval | Deputy Utilities Director/ Environmental Compliance | konovala@deland.org | (386) 626-7254 |  | Deputy Utilities Director/ Environmental Comp. | James V. Ailes (Utilities Director) | (386) 626-7250 |  | ailesj@deland.org | 09/12/2017 05:00 PM | 09/12/2017 05:30 PM | Volusia |  | N | 29.091615 | -81.304958 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=415
6423 River Point Drive | 20177390 | Gravity sewer blockage at 6423 River Point Drive. Blockage was cleared. 288 gallons sewer released. Vacuumed remaining sewer volume. Applied lime to affected area. Warning signs posted. No waterways affected. | 09/13/2017 10:57 AM | Fleming Island WWTP | 1770 Radar Road; Fleing Island FL; 32003 |  | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Plant Manager | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 09/11/2017 11:35 PM | 09/12/2017 02:00 AM | Clay |  |  | 30.077241 | -81.696326 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=414
L.S.15 Plymouth Place, DeLand, untreat. domestic WW spill |  | Lift station #15 (Plymouth Place) located at 1015 New Bedford Avenue, DeLand, FL overflowed during Hurricane Irma during power outage. Amount of spillage was less than I,000 gallons. Responded quickly and corrected with portable generator to restore power. The spillage affected residences located at 860 and 880 North Kansas Avenue. | 09/13/2017 10:47 AM | DeLand/ Wiley M. Nash WRF (FL0020303) | 1101 South Amelia Avenue; DeLand FL; 32724 |  | Alex Konoval | Deputy Utilities Director/ Environmental Compliance | konovala@deland.org | (386) 626-7254 |  | Deputy Utilities Director/ Environmental Comp. | James V. Ailes (Utilities Director) | (386) 626-7250 |  | ailesj@deland.org | 09/12/2017 10:20 AM | 09/12/2017 11:00 AM | Volusia |  | N | 29.046149 | -81.286226 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=413
800 S. Semoran Bvld., Winter Park, FL. | 1190047 | On September 12, 2017 at 1417 ET, ERTS reported a Distribution transformer release at the Winter Park Point Apartment Complex; 800 S Semoran Blvd, Winter Park, FL 32792. It was reported that due to Hurricane Irma, a Duke Energy pole was snapped at the top allowing for the transformer to dangle from the power lines. A one gallon release of non-PCB mineral oil to a nearby drainage ditch resulted from the damaged transformer. Booms and pads are in place. Because the ditch is an engineered storm water swale, the report of the release to the NRC and the State Watch Office were courtesy calls. At 1426 P.O. Kevin Williams with the NRC took receipt of the call and issued report number 1190047. Please reference SWO Incident number above. | 09/13/2017 10:45 AM | Winter Park Pointe Apartments | 800 S. Semoran Blvd.; Winter Park FL; 32792 |  | Devin Barzilay | Environmental Spill Coordinator | Devin.Barzilay@Duke-Energy.com | (352) 573-6473 |  | Environmental Spill Coordinator | Duke Energy Corporate Communications | (888) 266-3853 |  | Duty-CorpComm@Duke-Energy.com | 09/12/2017 02:15 PM |  | Orange |  |  | 28.568929 | -81.32969 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=412
City of Ocala - 4000 Block of SW 43rd Ct | 20177377 | Location: 4000 Block of SW 43rd Ct. Statement of Trouble: lift station and manhole surcharging. Corrective action: rerouted sewer to another force main. Approximately 1,000 gallons of sewage surcharged from the system. The affected area was sanitized with HTH and cleaned with the Vac-con truck. | 09/13/2017 10:35 AM | City of Ocala - WRF #3 - FLA190268-001 | 1805 NE 30th Ave, Bldg 600; Ocala FL; 34470 |  | Ronald Moore | Collection Foreman | RBMoore@Ocalafl.org | (352) 351-6776 |  | Collection Foreman | Joan Anderson | (352) 351-6652 |  | JAnderson@Ocalafl.org | 09/12/2017 01:30 PM | 09/12/2017 02:00 PM | Marion |  |  | 29.148019 | -82.193974 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=411
407068 | 20177381 | WASD Incident #: 407068 Version: 2 Version Type: Supplementary Incident Version Created On: 09/13/17 08:57 AM Job Order #: 1003496162 Location of Discharge: 3661 NW 33 ST UNINCORPORATED MIAMI-DADE 33142 Additional Location Description: MIAMI JAI ALAI PRIVATE LIFT STATION Reported by WASD Employee? Yes Employee ID: 00008954 Employee Title: WATER DISTRIBUTION SUPVR Reported by: FLOYD PINCKNEY Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: East On: NORTH RIVER DRIVE Discharge Caused by Asset Type: Private Lift Station Private Lift Station: MIAMI JAI ALAI PRVT LIFT STAT Contractor Involved? No Discharge Due to/Caused by: Private Lift Station Broken Other Cause Additional Discharge Cause: DUE TO NON STANDARD MATERIAL Pipe Material: PVC (Polyvinyl Chloride) Pipe Size in inches: 4 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? Yes Number of Storm Drain(s) Impacted: 1 Distance in Feet to Storm Drain(s): 250 Direction: East Did Discharge Go into Surface Water? No Weather Conditions: Clear Estimated Quantity of Sewage Released in Gallons: 50,190 Estimated Time Release Started: 09/12/17 06:43 PM Estimated Time Action Taken at Site: 09/12/17 07:30 PM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 09/12/17 08:00 PM Spill Contained? Yes Area Cleaned? No Area Disinfected? No Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 09/12/17 07:30 PM Spill Recovered? No AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone MORGAN:2017-7381 09/13/17 09:21 AM RER RER Compliance Desk Phone JENNIFER NOTIFIED 09/13/17 09:21 AM WASD WASD Jose Cueto Phone NOTIFIED 09/13/17 09:21 AM DEP DEP Notification Group E-mail 09/13/17 09:21 AM DOH DOH Notification Group E-mail 09/13/17 09:21 AM EPA EPA Notification Group E-mail 09/13/17 09:21 AM HMS Hazardous Materials Subcommittee Group E-mail 09/13/17 09:21 AM RER RER Notification Group E-mail 09/13/17 09:21 AM SFWM SFWM Notification Group E-mail 09/13/17 09:21 AM WASD WASD Interdepartmental Personnel E-mail 09/13/17 09:21 AM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Cynthia Carter (CCARTE) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.8058994137433 Longitude: -80.2555258653664 09/13/17 09:21 AM * Fields on red are the ones that changed from previous version Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/13/2017 10:17 AM | Miami-Dade W&S Collection System | 3661 NW 33 ST ; Miami FL; 33142 | Private Lift Station | Floyd Pinckney | WDS | floyd.pinckney@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/12/2017 06:45 PM | 09/12/2017 08:00 PM | Miami-Dade |  |  | 25.806218 | -80.254228 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=410
Southwest Regional Utility Service Area (SWRUSA) | 20177351 | The incident occurred at the following locations: Lift Station #34; 410 West Christina Boulevard in Lakeland. Lift Station #148; 300 Whisperwood Drive in Lakeland. Lift Station #233; Sundance Village in Lakeland. Lift Station #270; 6160 Stoney Creek Lane in Lakeland. Lift Station #284; Krenson Woods Rd in Lakeland. Lift Station #99; 1875 Shepherd Road in Lakeland. The incident occurred when the lift stations lost power due to Hurricane Irma resulting in overflows. An undetermined amount of raw wastewater discharged on the ground. There were no reported affected areas beyond the installation location. The public is advised to minimize contact with standing water in the vicinity of the installation as the full impact cannot be determined due to Hurricane Irma and the volume of storm recovery activities. Lift Station #34 was brought back online at approximately 11:12 AM on September 12, 2017. Lift Station #148, #233, #270, #284 & #99 were pumped down to prevent a recurrence. PCU notified the Department via email on September 11, 2017 at 7:03 PM. State Watch Office was contacted at 4:45 PM on September 12, 2017 and the incident numbers were issued on September 13, 2017 as follows: Lift Station #34; 410 Christina Blvd in Lakeland; (Incident # 2017-7351), Lift Station #148; 300 Whisperwood Dr in Lakeland; (Incident # 2017-7361), Lift Station # 233; Sundance Village in Lakeland; (Incident # 2017-7362), Lift Station #270; 6160 Stoney Creek Lane in Lakeland; (Incident #2017-7363), Lift Station # 284; Krenson Woods Rd in Lakeland; (Incident #2017-7366) and Lift Station #99; 1875 Shepherd Rd in Lakeland; (Incident #2017-7368). PCU was notified on October 2, 2017 about evidence of another spill from a manhole located at 525 Quail Hollow Court in Lakeland. Further investigation confirmed that the spill occurred due to power outages at near-by Lift Station #33 and #34 because of Hurricane Irma. The raw wastewater seeped out of the manhole and flowed into a near-by pond. The affected area was cleaned up and signs were posted around the pond as a precaution. Sampling of the pond will occur within the next few days. State Watch Office was notified with the updated information at 5:20 PM on October 2, 2017 and was noted under Incident #2017-7351. | 09/13/2017 10:13 AM | Southwest Regional WWTF; FLA 012954 | 2000 4th Street; Mulberry FL; 33860 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 09/11/2017 10:50 AM | 09/11/2017 07:05 PM | Polk |  | N | 27.94818 | -81.962937 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=409
Northwest Regional Utility Service Area (NWRUSA) | 20177369 | The incident occurred at the following locations: Lift Station #67; 6325 1/2 Pearce Road in Lakeland. The wastewater also backed up into three homes located on Rosalynn Lane. Lift Station # 72; 1399 Marcum Road in Lakeland. The incident occurred when the lift station lost power due to Hurricane Irma resulting in an overflow. An undetermined amount of raw wastewater discharged on the ground. There may be potentially affected areas beyond the installation location. The public is advised to minimize contact with standing water in the vicinity of the installation as the full impact cannot be determined due to Hurricane Irma and the volume of storm recovery activities. The lift station was brought back online at approximately on September 12, 2017. PCU notified the Department via email on September 11, 2017 at 7:03 PM. A generator is currently in route to Lift Station # 72 to pump it down. State Watch Office was contacted at 4:45 PM on September 12, 2017 and the incident numbers were issued on September 13, 2017 as follows: Lift Station #67; 6325 1/2 Pearce Road in Lakeland; (Incident # 2017-7369) and Lift Station # 72; 1399 Marcum Road in Lakeland; (Incident # 2017-7371). | 09/13/2017 09:52 AM | Northwest Regional WWTF; FLA 178667 | 8950 N. Campbell Rd; Lakeland FL; 33810 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4124 |  | markaddison@polk-county.net | 09/11/2017 10:50 AM | 09/11/2017 07:05 PM | Polk |  |  | 28.123962 | -81.956062 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=408
407074 | 20177367 | WASD Incident #: 407074 Version: 3 Version Type: Supplementary Incident Version Created On: 09/13/17 12:25 AM Job Order #: 1003496172 Location of Discharge: 1721 SW 94 AVE UNINCORPORATED MIAMI-DADE 33165 Reported by WASD Employee? Yes Employee ID: 00209637 Employee Title: PIPEFITTER SUPERVISOR Reported by: CHARLES DAVIS Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: East and West On: SW 94 AVENUE Discharge Caused by Asset Type: Force Main Contractor Involved? No Discharge Due to/Caused by: Force Main Broken Other Cause Additional Discharge Cause: ANGULAR CRACK Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? Yes Number of Storm Drain(s) Impacted: 1 Distance in Feet to Storm Drain(s): 150 Direction: South Did Discharge Go into Surface Water? No Weather Conditions: Clear Estimated Quantity of Sewage Released in Gallons: 26,052 Estimated Time Release Started: 09/12/17 06:30 PM Estimated Time Action Taken at Site: 09/12/17 06:45 PM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 09/12/17 07:45 PM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Wash Down Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 09/12/17 06:45 PM Spill Recovered? No AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone WOODY//2017-7367 09/13/17 12:44 AM RER RER Compliance Desk Phone LOUISE 09/13/17 12:44 AM WASD WASD Jose Cueto Phone SPOKE W/ @ 12:43AM 9/13/17 09/13/17 12:44 AM DEP DEP Notification Group E-mail 09/13/17 12:44 AM DOH DOH Notification Group E-mail 09/13/17 12:44 AM EPA EPA Notification Group E-mail 09/13/17 12:44 AM HMS Hazardous Materials Subcommittee Group E-mail 09/13/17 12:44 AM RER RER Notification Group E-mail 09/13/17 12:44 AM SFWM SFWM Notification Group E-mail 09/13/17 12:44 AM WASD WASD Interdepartmental Personnel E-mail 09/13/17 12:44 AM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Charvonte Osborne (E318782) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.7536065206332 Longitude: -80.3478083835376 09/13/17 12:44 AM * Fields on red are the ones that changed from previous version Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/13/2017 09:48 AM | Miami-Dade W&S Collection System | 1721 SW 94 AVE ; Miami FL; 33165 |  | Charles Davis | Pipefitter Supervisor | charles.davis@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/12/2017 06:30 PM | 09/12/2017 07:45 PM | Miami-Dade |  |  | 25.753123 | -80.348141 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=407
Lift Station ##196; 160 Adrienne Rd in Haines City | 20177371 | The incident occurred when the lift station lost power due to Hurricane Irma resulting in an overflow. An undetermined amount of raw wastewater discharged on the ground. There may be potentially affected areas beyond the installation location. The public is advised to minimize contact with standing water in the vicinity of the installation as the full impact cannot be determined due to Hurricane Irma and the volume of storm recovery activities. The lift station overflow ceased at 12:30 PM on September 12, 2017 and is currently on a generator. PCU notified the Department via email on September 11, 2017 at 7:03 PM. State Watch Office was contacted at 4:45 PM on September 12, 2017 and incident number #2017-7371 was issued on September 13, 2017. | 09/13/2017 09:34 AM | TWA-Lake Marion | 1001 Lake Marion Creek Drive; Kissimmee FL; 34759 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 09/11/2017 10:55 AM | 09/11/2017 12:30 PM | Polk |  |  | 28.012508 | -81.529943 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=406
Northeast Regional Utility Service Area (NERUSA) | 20177345 | The incident occurred at the following locations: ¿ Lift Station # 120; 103 Montana Ave in Davenport. ¿ Lift Station # 198; 7835 Elgin Street in Davenport. ¿ Lift Station #134; 1728 1/2 Challenger Avenue in Davenport. ¿ Lift Station #126; International Bass Boulevard in Davenport. ¿ Lift Station #159; 150 Pete¿s Lane in Davenport. The incidents occurred when the lift stations lost power due to Hurricane Irma resulting in overflows. An undetermined amount of raw wastewater discharged on the ground. The spill from Lift Station #126 also went into Bass Lake. The public is advised to minimize contact with standing water in the vicinity of the installation as the full impact cannot be determined due to Hurricane Irma and the volume of storm recovery activities. Lift Station #120 is currently being pumped down to prevent a recurrence and stations #198, #126, and #159 will also be pumped down. Lift Station #134 is currently inaccessible due to high standing water. Polk County Roads & Drainage has been notified to assist with removal of the excess water. PCU notified the Department via email on September 11, 2017 at 7:03 PM. As a precaution, signs were posted on September 13, 2017 and sampling will occur in the next few days. State Watch Office was contacted at 4:45 PM on September 12, 2017 and the incident numbers were issued on September 13, 2017 as follows: ¿ Lift Station # 120; 103 Montana Ave in Davenport; (Incident # 2017-7345). ¿ Lift Station # 198; 7835 Elgin Street in Davenport; (Incident # 2017-7347). ¿ Lift Station #134; 1728 1/2 Challenger Avenue in Davenport; (Incident # 2017-7348). ¿ Lift Station #126; International Bass Boulevard in Davenport; (Incident # 2017-7350). ¿ Lift Station #159; 150 Pete¿s Lane in Davenport; (Incident # 2017-7355). | 09/13/2017 09:20 AM | Northeast Regional WWTF | 200 Westview Drive ; Davenport FL; 33837 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 09/11/2017 10:55 AM | 09/11/2017 07:05 PM | Polk |  |  | 28.291165 | -81.673704 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=405
Marshall Street WRF | 20177373 | At 10:30 pm, the facility lost power to the Main Control Room. This incident caused us to lose power to our airbays, clarifiers and the filter feed pumps. The back up generator came on however, the automatic transfer switch did not function properly because there was partial power on the utility side of the transfer switch. With no power to our Filter Feed pumps this caused the loss of approximately 338,000 gallons of secondary treated effluent which flowed into Stevenson Creek. The problem was corrected at 11:45 p.m. when the generator controls were able to be reset which allowed the emergency power to start up. The State Warning Point was Notified at 12:15 am. Report # 2017-7373. We are working with our engineers and contractors to make the necessary adjustments to minimize the possibility of a reoccurrence in the future. The area is being limed and the lime will be cleaned up after 24 hours when weather permits. | 09/13/2017 08:57 AM | Marshall Street WRF | 1605 Harbor Drive Clearwater Florida; Clearwater FL; 33755 |  | Ron Nelson | Chief Operator | ron.nelson@myclearwater.com | (727) 224-7691 |  | Operator Of the Facility | Dave Porter | (727) 224-7680 |  | david.porter@myclearwater.com | 09/12/2017 10:30 PM | 09/12/2017 11:45 PM | Pinellas |  |  | 27.981615 | -82.787784 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=404
Sanitary Sewer Spill | 20177375 | Lift station crew was relocating a bypass pump which was needed due to widespread power outages resulting from Hurricane Irma. The crew did not follow correct procedures in disconnecting the bypass pump which resulted in approx. 2000 gallons of raw sewage (domestic wastewater) discharging into the street and adjacent residential yards. Spill was contained to immediate vicinity and did not migrate to surface waters. Affected areas were disinfected with HTH, rinsed, and lime was applied. State watch office was duly notified. | 09/13/2017 08:36 AM | Lift Station #15 | 1517 Mango Tree Drive; Edgewater FL; 32132 | Intersection of Regent Street and Mango Tree Drive | Randy J. Coslow, P.E. | Deputy Director of Environmental Services / City Engineer | RCoslow@cityofedgewater.org | (386) 424-2400 | 4007 | Owner Of the Facility | Randy J. Coslow, P.E. | (386) 424-2400 |  | RCoslow@cityofedgewater.org | 09/12/2017 10:30 PM | 09/12/2017 11:15 PM | Volusia |  |  | 28.974129 | -80.910571 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=403
City of Pompano Beach Wastewater Spill LS 143 | 20177338 | Due to power outages from Hurricane Irma, Lift Station 143 at 3993 Cypress Reach Court released approximately 40,000 gallons of wastewater into a private storm drain which leads to a privately owned lake. The released started at 9:00am and ended at 3:00pm. Partial clean up was done. | 09/13/2017 08:35 AM | City of Pompano Beach | 1205 NE 5th Ave; Pomapno Beach FL; 33060 |  | Shana Coombs-Gordon | Interim Utility Compliance & Efficiency Manager | shana.coombs@copbfl.com | (954) 545-7004 |  | Employee | Steve Almyda | (954) 803-2932 |  | steve.almyda@copbfl.com | 09/12/2017 09:00 AM | 09/12/2017 03:00 PM | Broward |  |  | 26.209602 | -80.178447 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=402
Stillwater Force main break |  | 6ft. crack within a section of a class 200 PVC forcemain located behind 518 Appleton Place. Isolated the force main and made repair with 2 full circle repair clamps. Repair took longer than expected due to the curfew established for hurricane IRMA. | 09/13/2017 01:21 AM | Carillon Master 12" Force main | 518 Appleton Place; Oviedo FL; 32765 |  | Michael Riley | Utilities Asset Manager | mriley@seminolecountyfl.gov | (407) 665-2729 |  | Operator Of the Facility | Jeff Lane | (407) 782-1225 |  | jlane@seminolecountyfl.gov | 09/10/2017 05:00 PM | 09/11/2017 11:00 AM | Seminole |  |  | 28.631 | -81.197005 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=401
Private Sanitary Sewer Overflow - City of Orlando | 20177364 | On 09-12-2017, the private lift station located at the Gallery at Mills Park experienced pump failure for both pumps in the wet well. An overflow occurred and 15,000 gallons of sewer were released from the station to the surrounding area. City personnel assisted the facility in shutting valves throughout the property to stop the flow of sewer to the lift station. The pumps were repaired and flow was properly restored to the private lift station. | 09/12/2017 11:34 PM | Gallery at Mills Park | 1650 N Mill Avenue; Orlando FL; 32803 | Take Princeton East to Mills and turn Right. Address will be on right. | Daniel Friedline | Public Outreach Coordinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | Authorized Representative of the City of Orlando | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 09/12/2017 03:30 PM | 09/12/2017 05:00 PM | Orange |  |  | 28.567606 | -81.365663 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=400
Lake Reedy Spill | 119073 | Hurricane Irma caused a tree to fall and rupture an irrigation fuel tank line. An estimated 200 hundred gallons spilled into lake Reedy in Frostproof Fl. | 09/12/2017 07:35 PM | Alico Citrus | 181 hwy 630 ; frostproof FL; 33843 |  | joe barajas | Safety | jbarajas@alicoinc.com | (863) 990-8034 |  | Safety Manager | joe barajas | (863) 990-8034 |  | jbarajas@alicoinc.com | 09/12/2017 05:55 PM |  | Polk |  |  | 27.720755 | -81.490997 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=399
OCU WW Collection System; Hurricane Irma |  | Due to wide spread power outages caused by Hurricane Irma, the Orange County Utilities Department had overflows from manholes and pump stations at multiple locations throughout its collection system. OCU Wastewater staff are diligently addressing any ongoing conditions and the Department will follow up with additional detailed information and volume estimates as they become available. OCU will be preparing one report summarizing SSOs from OCU¿s wastewater collection system and submitting to the department on a daily basis during the immediate post-hurricane recovery period. The State Watch Office has been contacted and we are preparing the detailed report requested. | 09/12/2017 06:26 PM | Orange County Utilities Collection System | FL |  | Laura Woodbury | Sr. Engineer, Field Services | laura.woodbury@ocfl.net | (407) 836-6826 |  | Sr. Eng. Field Services | Troy Layton, Manager, Field Services | (407) 254-9794 |  | Troy.Layton@ocfl.net | 09/10/2017 08:00 PM |  | Orange |  |  | 28.447681 | -81.41779 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=398
EWRF 3; 9-11-2017 | 20177225 | On September 11th at approximately 7:45 PM, Plant Influent flow increased to over 40 MGD Peak hourly flows. This in turn caused high flows throughout the Plant and subsequently caused the Phase 3 Automatic Backwash Filters to overflow into the plant¿s sanitary sewer system, which became surcharged causing the nearby man holes to overflow. The secondary treated effluent flowed into a nearby storm water ditch. The storm water ditch was blocked off in response to a spill that occurred the day before. The spill amount was contained and pumped back into the north lift station for re-treatment. The estimated amount discharged was 10,000 gallons. The amount recovered was approximately 12,000 gallons. The discharge lasted one hour; 7:45 pm to 8:45 pm. | 09/12/2017 06:14 PM | OCU East Water Reclamation Facility | 1621 S. Alafaya Trail; Orlando FL; 32828 |  | Laura Woodbury | Sr. Engineer, Field Services | laura.woodbury@ocfl.net | (407) 836-6826 |  | Sr. Eng, Field Services | Mark Robinson, Assistant Manager, WRD | (407) 254-6791 |  | Mark.Robinson@ocfl.net | 09/11/2017 07:45 PM | 09/11/2017 08:45 PM | Orange |  | N | 28.523178 | -81.203006 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=397
Northeast Water Reclamation Facility, Reject Tank | 20177224 | Reclaimed water reject storage tank overflowed due to a faulty level indicator, causing approximately 432,000 gallons of partially treated effluent to spill on the ground around the tank. None of the spill migrated off plant property. The plant was in reject because of failure to maintain minimum chlorine residual, due to nitrification within the treatment system. | 09/12/2017 05:04 PM | Northeast Water Reclimaiton Facility (FLA128856) | 1160 62nd Ave. NE; St. Petersburg FL; 33701 |  | John E. Palenchar | Interm Director | john.palenchar@stpete.org | (727) 892-5600 |  | Owner Of the Facility | Doug Larue | (727) 893-7779 |  | doug.larue@stpete.org | 09/11/2017 04:00 PM | 09/11/2017 04:35 PM | Pinellas |  |  | 27.82759 | -82.615105 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=396
EWRF 2; 9-10-17 | 20177079 | As a result of Hurricane Irma, on September 10th at approximately 2:00 PM, Plant influent flows increased to over 55 MGD peak hourly flows. This in turn caused the high flows throughout the Plant and subsequently caused the Phase III Automatic Backwash Filters to overflow from the Influent channels. The partially treated effluent that was released from the Phase 3 Automatic Backwash filter influent channel ponded on adjacent ground surfaces and flowed into and ponded in a nearby stormwater ditch. EWRF Plant staff enacted emergency by-pass measures to stop the overflow and deployed crews and a tanker to assist with clean-up and spill recovery measures. Staff decided to block off culverts to ponds and contain the spill within west stormwater ditches. Staff set up a pump system to pull water from the ditches and discharged back into the north lift station for re-treatment. The estimated amount discharged was 120,000 gallons. Over 120,000 gallons was recovered and pumped back into the plant. | 09/12/2017 05:02 PM | OCU East Water Reclamation Facility | 1621 S. Alafaya Trail, Orlando, FL. 32828 FL |  | Laura Woodbury | Sr. Engineer, OCU Field Services | Laura.Woodbury@OCFL.net | (407) 836-6826 |  | Sr. Eng. Field Services | Mark Robinson, Assistant Manager WRD | (407) 254-6791 |  | Mark.Robinson@ocfl.net | 09/10/2017 03:00 PM | 09/11/2017 03:00 AM | Orange |  | N | 28.522566 | -81.202122 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=395
City of Lakeland - FL0039772 | 20177326 | Due to Hurricane Irma, the City of Lakeland Wastewater Collection Division has experienced system wide power outages and area flooding. These have caused the City to have overflows from manholes and pump stations throughout the service area. City crews are working around the clock pulling generators and pumps to handle the situation. Additional information will be provided after recovery efforts have been completed. The following known SSOs occurred during Hurricane Irma from pump stations located with the City of Lakeland service territory: L0410 at 2900 E Edgewood Dr. 75,000 gallons (SWP# 2017-7326), L0730 at 2026 Wayman St. 25,000 gallons (SWP# 2017-8121), L1410 at 20 Lake Hunter Dr. 25,000 gallons (SWP# 2017-8123), L3820 at 955 Longfellow Blvd 20,000 gallons (SWP# 2017-8130), L4420 at 1510 Ariana Street 10,000 gallons (SWP# 2017-8132), L1720 at 2037 Nottingham 10,000 gallons (SWP# 2017-8134), L0710 at 1501 Ariana Street 5,000 gallons (SWP# 2017-8136), L4430 at 1510 Ariana Street 5,000 gallons (SWP# 2017-8137), L1910 at 1351 W. Lake Bonny Dr. 7,500 gallons (SWP# 2017-8139), L6650 at 4444 N Rd 98 2,500 gallons (SWP# 2017-8141), L6660 at 4051 Sunset Lake Dr. 2,500 gallons (SWP# 2017-8145), L3865 at 1610 Reynolds Rd 2,500 gallons (SWP# 2017-8147), L4440 at 2141 Harden Blvd 2,500 gallons (SWP# 2017-8150), L6825 at 632 Sandstone Dr. 2,500 gallons (SWP# 2017-8120), L2640 at 4375 S Rd 98 1,500 gallons (SWP# 2017-8122), L4520 at 1001 Pine Chase Ave 1,500 gallons (SWP# 2017-8124), L4410 at 1625 Ariana Village 1,000 gallons (SWP# 2017-8126), L6670 at 1105 Plaza Dr. 1,000 gallons (SWP# 2017-8127). The following known SSOs occurred during Hurricane Irma at manholes located with the City of Lakeland service territory: 3350 Kilmer 1,000 gallons (SWP# 2017-8129), 1501 Lake Bonny Dr. 250 gallons (SWP# 2017-8131), 847 Buttercup 250 gallons (SWP# 2017-8133), 2313 N Florida Ave 250 gallons (SWP# 2017-8135), 10 Pirates Way 250 gallons (SWP# 2017-8138), 1417 Glendale 250 gallons (SWP# 2017-8140), 2945 Oxford 250 gallons (SWP# 2017-8142) | 09/12/2017 04:39 PM | City of Lakeland Glendale WRF - FL0039772 | 1825 Glendale Street; Lakeland FL; 33803 |  | Richard Ruede | Wastewater Collection Manager | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 09/10/2017 11:00 PM | 09/14/2017 09:00 AM | Polk | Polk | Y | 28.006743 | -81.927511 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=394
PCU DS-346 9.11.17 | 20177201 | Manholes overflowed associated to pump station 346 located at 508 19th St. N. Palm Harbor started at 9:51 AM 9/11/17. (DEP Incident #387) tied to DEP Incident # 393. Generators in place and/or rotated until power was restored - debris clean-up as needed. Date ceased:9/11/2017 @ 12:57. Signs have been posted. Waterway Affected: Allen's Creek. Samples met state surface water bacteriological criteria. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount :7,875 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions.. Pump Station 346 Power Outage - calls from 1827 Mary's Meadow Lane 1808 Mary's Meadow Lane 1868 Mary's Meadow Lane 1838 Mary's Meadow Lane 1800 Mary's Meadow Lane 1890 Mourning Dove Drive | 09/12/2017 04:33 PM | W.E. Dunn WRF FL0128775 | 4111 Dunn Drive, Palm Harbor, FL 34683; Palm Harbor FL; 34683 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:00 AM | 09/11/2017 01:00 PM | Pinellas |  | N | 28.074574 | -82.751496 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=393
Lift Station #22 Flooding | 20177301 | Black Creek flooded during hurricane Irma and flooded master lift station at 2647 Blanding Blvd, Middleburg, Florida. Lift Station is 10 - 12 feet under water, | 09/12/2017 04:20 PM | Ridaught WWTP | 2878-1 Tuscarora Trail; Middleburg FL; 32068 |  | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Plant Manager | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 09/11/2017 05:00 PM |  | Clay |  |  | 30.060937 | -81.871251 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=392
EWRF 1; 9-10-2017 | 20177078 | During hurricane Irma, pretreatment Influent flow increased to over 55 MGD causing the pretreatment structure to overflow into the old odor control system and on to the ground. Releasing initially 250,000 gallons before semi repair was completed within an hour. Semi repair slowed the spill down to 400 GPM. Since the onsite storm water system was involved and there was no way of stopping the overflow until influent flows decreased, Plant staff decided to block off culverts to the stormwater ponds and contain the spill within west stormwater ditches. Staff set up pump system to pull water from the ditches and discharge it back into north lift station for re-treatment. The estimated total discharge is 538,000 gallons. More than this amount was recovered. | 09/12/2017 04:18 PM | OCU East Water Reclamation Facility | 1621 S. Alafaya Trail, Orlando, FL. 32828; Orlando FL; 32828 |  | Laura Woodbury | Sr. Engineer, OCU Field Services | Laura.Woodbury@OCFL.net | (407) 836-6826 |  | Sr Eng, OCU Field Services | Mark Robinson, Assistant Manager WRD | (407) 257-6791 |  | Mark.Robinson@ocfl.net | 09/10/2017 02:30 PM | 09/11/2017 02:00 AM | Orange |  | N | 28.522734 | -81.203109 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=391
2662 Shenandoah Dr Force Main Break | 20177300 | Uprooted tree broke sewage force main during hurricane Irma. Sewage flowed into nearby drainage ditch. Notified affected property owner. | 09/12/2017 04:13 PM | Miller Street WWTP | 1600 Bartlett; Orange Park FL; 32073 |  | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Plant Manager | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 09/11/2017 01:30 PM | 09/11/2017 05:30 PM | Clay |  |  | 30.135065 | -81.755519 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=390
Big Bend Irma Discharge | 20177314 | Recycle Water Pond overflowed into County ditches. The water is being transferred through another pond to a dyked area for containment on-site. | 09/12/2017 04:13 PM | Big Bend Station | 13031 Wyandotte Road; Apollo Beach, FL 33572 FL |  | Amy Butler | Sr. Consulting Engineer | ambutler@tecoenergy.com | (813) 228-4433 |  | Owner Of the Facility | Amy Butler | (813) 228-4433 |  | ambutler@tecoenergy.com | 09/11/2017 09:00 AM |  | Hillsborough |  |  | 27.789916 | -82.399502 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=389
Lester Murray Sewer Backup | 20177312 | Gravity sewer backed up into 6 homes due to partial lift station failure. Sewage ran from properties to storm drainage system and into nearby storm water ponds. Significant rainfall was occurring during hurricane Irma. | 09/12/2017 04:04 PM | Ridaught WWTP | 2878-1 Tuscarora Trail; Middleburg FL; 32068 |  | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Facility Manager | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 09/11/2017 09:00 AM | 09/11/2017 10:15 AM | Clay |  |  | 30.114253 | -81.796223 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=388
PCU DS-346 9.11.17 | 20177201 | Manholes overflowed associated to pump station 346 located at 508 19th St. N. Palm Harbor started at 9:51 AM 9/11/17. (DEP Incident #387) tied to DEP Incident # 393. Generators in place and/or rotated until power was restored - debris clean-up as needed. Date ceased:9/11/2017 @ 12:57. Waterway Affected: Allen's Creek (incorrect, later determined to be Smith Creek). Samples met state surface water bacteriological criteria. Signs removed. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount :7,875 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions.. Pump Station 346 Power Outage - calls from 1827 Mary's Meadow Lane 1808 Mary's Meadow Lane 1868 Mary's Meadow Lane 1838 Mary's Meadow Lane 1800 Mary's Meadow Lane 1890 Mourning Dove Drive | 09/12/2017 03:50 PM | W.E Dunn WRF | 4111 Dunn Drive, Palm Harbor, FL 34683; Palm Harbor FL; 34683 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 09:50 AM | 09/11/2017 01:00 PM | Pinellas |  | N | 28.074792 | -82.753266 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=387
MPS 450 | 20177219 | Wastewater spill due to a faulty controller. The estimated discharge is 1000 gallons. No water bodies, storm drains or public access areas were impacted. The area was sanitized and cleaned up with HTH by utility crew. | 09/12/2017 03:32 PM | MPS 450 | 3701 N State Rd 7; Lauderdale Lakes FL; 33319 |  | Metason Phillip | Utilities Superintendent | mphillip@broward.org | (954) 831-0829 |  | First Responder | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 09/11/2017 04:00 PM | 09/11/2017 04:05 PM | Broward |  |  | 26.172024 | -80.203161 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=386
Waters #2 Station |  | Incident was at the Waters #2 station. 175 gal. was spilled into the street, due to power out from hurricane IRMA. Street was washed down and clean up is completed. | 09/12/2017 03:23 PM | Waters #2 station | 6154 Waters Way; Weeki Wachee FL; 34607 - 4047 | This location is in between 6154 and 6157 Waters WAY. | James Minnie | Asset Information Specialist | jminnie@co.hernando.fl.us | (352) 754-4490 |  | Asset Information Specialist | Larry Cooper | (352) 754-4490 |  | lcooper@co.hernando.fl.us | 09/12/2017 12:00 PM | 09/12/2017 12:30 PM | Hernando |  |  | 28.524993 | -82.598219 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=385
7413 Gettysburg Dr. | 20177289 | Incident was at 7413 Gettysburg Dr. 2500 gal. was spilled due to power out from Hurricane IRMA. Spill did enter into wetlands. Area was limed and clean up is completed. | 09/12/2017 03:10 PM | Gettysburg Dr. | 7413 Gettysburg Dr.; Weeki Wachee FL; 34607 - 1724 |  | James Minnie | Asset Information Specialist | jminnie@co.hernando.fl.us | (352) 754-4490 |  | Asset Information Specialist | Larry Cooper | (352) 754-4490 |  | lcooper@co.hernando.fl.us | 09/12/2017 12:00 PM | 09/12/2017 12:30 PM | Hernando |  |  | 28.536758 | -82.613773 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=384
Baracoa | 20177290 | Lift Station overflow due to power outage with Hurricane Irma | 09/12/2017 02:53 PM | Anastasia Island WWTF | 860 W 16th St; St. Augustine FL; 32080 |  | Tony Cubbedge | Env Div Mgr | twcubbedge@sjcfl.us | (904) 209-2620 |  | Env Div Mgr | Tony Cubbedge | (904) 209-2620 |  | twcubbedge@sjcfl.us | 09/11/2017 03:00 PM | 09/11/2017 05:00 PM | St. Johns |  |  | 29.813227 | -81.313575 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=383
Lenox & Scarlett Station |  | Incident was at the Lenox and Scarlett Lift-station. 500 gal. spill on to the street due to power out from Hurricane IRMA. Street was wash down and clean up is completed. | 09/12/2017 02:47 PM | Lenox and Scarlett Lift-station | 10003 Scarlett Ct.; Weeki Wachee FL; 34613 - 4042 | At the intersection of Lenox Blvd. and Scarlett Ct. | James Minnie | Asset Information Specialist | jminnie@co.hernando.fl.us | (352) 754-4490 |  | Asset Information Specialist | Larry Cooper | (352) 754-4490 |  | lcooper@co.hernando.fl.us | 09/10/2017 10:30 AM | 09/12/2017 12:00 PM | Hernando |  |  | 28.568385 | -82.575552 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=382
406954 |  | WASD Incident #: 406954 Version: 2 Version Type: Supplementary Incident Version Created On: 09/12/17 02:07 PM Job Order #: 1003495932 Location of Discharge: 10200 SW 174 TER UNINCORPORATED MIAMI-DADE 33157 Additional Location Description: SPILL ALSO LOCATED ON THE EAST SWALE AREA Reported by WASD Employee? Yes Employee ID: 00024168 Employee Title: WDS Reported by: ISRAEL CAMACHO Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: North and South On: 102 AVE Discharge Caused by Asset Type: Manual Air Release Valve Contractor Involved? No Discharge Due to/Caused by: Manual Air Release Valve Broken Pipe Material: PVC (Polyvinyl Chloride) Pipe Size in inches: 12 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Sunny Estimated Quantity of Sewage Released in Gallons: 30,256 Estimated Time Release Started: 09/12/17 09:28 AM Estimated Time Action Taken at Site: 09/12/17 10:30 AM ACTION TAKEN Active Spill Observed? No Discharge Flow Stopped? Yes Discharge Stopped On: 09/12/17 01:50 PM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 09/12/17 01:55 PM Spill Recovered? Yes Recovered Amount in Gallons: 1,200 AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone KEN 2017-7266 09/12/17 02:10 PM RER RER Compliance Desk Phone LINDA 09/12/17 02:10 PM WASD WASD Bertha Goldenberg Phone B.GOLDENBERG 09/12/17 02:10 PM DEP DEP Notification Group E-mail 09/12/17 02:10 PM DOH DOH Notification Group E-mail 09/12/17 02:10 PM EPA EPA Notification Group E-mail 09/12/17 02:10 PM HMS Hazardous Materials Subcommittee Group E-mail 09/12/17 02:10 PM RER RER Notification Group E-mail 09/12/17 02:10 PM SFWM SFWM Notification Group E-mail 09/12/17 02:10 PM WASD WASD Interdepartmental Personnel E-mail 09/12/17 02:10 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Lynisha T. Beechum (BEECHL) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.6075231279862 Longitude: -80.3570097525228 09/12/17 02:10 PM * Fields on red are the ones that changed from previous version Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/12/2017 02:33 PM | Miami-Dade W&S Collection System | 10200 SW 174 TER UNINCORPORATED MIAMI-DADE 33157; Miami FL; 33157 |  | Israel Camacho | WDS | israel.camacho@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/12/2017 09:30 AM | 09/12/2017 01:50 PM | Miami-Dade |  |  | 25.608562 | -80.356882 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=381
407013 | 20177283 | WASD Incident #: 407013 Version: 1 Version Type: Preliminary Qualified UDP? Yes Incident Version Created On: 09/12/17 01:14 PM Job Order #: 1003496014 Location of Discharge: 3989 RICKENBACKER CSWY UNINCORPORATED MIAMI-DADE 33149 Additional Location Description: VIRGINIA KEY WASTEWATER TREATMENT PLANT 9-10-17 Reported by WASD Employee? Yes Employee ID: 00035207 Employee Title: CHIEF PLANT OPERATOR Reported by: FRANCOIS FAINT-PHARD Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: East and West On: GROUND Discharge Caused by Asset Type: Central District WWTP Contractor Involved? No Discharge Due to/Caused by: Central District WWTP Other Cause Additional Discharge Cause: POWER OUTAGE DUE TO HURRICANE IRMA Type of Water Discharge: SECONDARY EFFLUENT Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? Yes Distance in Feet into Surface Water: 100 Body of Water Name: BISCAYNE BAY Type of Water: Ocean Weather Conditions: Rainy Estimated Quantity of Sewage Released in Gallons: 6,000,000 Estimated Time Release Started: 09/10/17 06:30 PM Estimated Time Action Taken at Site: 09/11/17 02:30 AM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 09/11/17 02:30 AM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Wash Down Public Notified? No Spill Recovered? No AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone 2017-7283 HENRY 09/12/17 01:41 PM RER RER Compliance Desk Phone ANITA 09/12/17 01:41 PM WASD WASD Bertha Goldenberg Phone GOLDENBERG/LM 09/12/17 01:41 PM DEM DEM Notification Group E-mail 09/12/17 01:41 PM DEP DEP Notification Group E-mail 09/12/17 01:41 PM DOH DOH Notification Group E-mail 09/12/17 01:41 PM EPA EPA Notification Group E-mail 09/12/17 01:41 PM HMS Hazardous Materials Subcommittee Group E-mail 09/12/17 01:41 PM MD-BCC DIST11 E-mail 09/12/17 01:41 PM RER RER Notification Group E-mail 09/12/17 01:41 PM SFWM SFWM Notification Group E-mail 09/12/17 01:41 PM WASD WASD Interdepartmental Personnel E-mail 09/12/17 01:41 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Shanterra M. Spencer (SSPENC) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.7367251690968 Longitude: -80.1656523801101 09/12/17 01:41 PM Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/12/2017 02:00 PM | Miami-Dade W&S Central District Wastewater Treatment Plant | 3989 Rickenbacker Cswy; Virginia Key FL; 33149 |  | Francois Saint-Phard | Acting Chief Plant Operator | francois-saint-phard@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/10/2017 06:30 AM | 09/11/2017 02:30 AM | Miami-Dade |  |  | 25.746832 | -80.149042 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=380
PCU DS-356 9-11-17 | 20177252 | Manholes overflowed associated to pump station 356 located at 1231 Queen Ann Blvd., started at 11:43 and ceased at 9/11/17 @ 14:04. Generators in place and/or rotated until power was restored - debris clean-up as needed. Storm System affected: Went into storm drain to man-made ditch to wetland/forested area. Waterway Affected :none. Samples met state surface water bacteriological criteria. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount: 76,395 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions. (DEP Incident #367) tied to DEP Incident # 379. Pump Station 356 Power Outage - calls from 2949 Briar Cliff Drive 2963 Huntington Court 2976 Huntington Court 2976 Huntington Court 1121 Queen Anne Drive 2948 Sutherland Court | 09/12/2017 01:04 PM | William E. Dunn WRF Service Area FL0128775 | 4111 Dunn Drive; Palm Harbor FL; 34683 |  | Matthew Wotowiec | Water Quality Monitoring Manager | mwotowiec@co.pinellas.fl.us | (727) 599-4273 |  | Pinellas County Utilities Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:45 AM | 09/11/2017 02:05 PM | Pinellas |  | N | 28.076846 | -82.730195 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=379
Howard F. Curran AWTP - Irma | 20177143 | Due to wide spread power outages caused by Hurricane Irma, the City of Tampa Wastewater Department had overflows from manholes and pump stations, as well as a short duration overflow at the AWTP. Wastewater staff are diligently addressing any ongoing conditions and the Department will follow up with additional detailed information as it becomes available. | 09/12/2017 12:58 PM | Howard F. Curran AWTP | 2700 MARITIME BLVD; TAMPA FL; 33605 |  | Jeff Hilton | Wastewater Planning Head | jeffrey.hilton@tampagov.net | (813) 274-7844 |  | Wastewater Planning Head | Eric Weiss | (813) 274-8039 |  | eric.weiss@tampagov.net | 09/10/2017 10:35 PM |  | Hillsborough |  |  | 27.92206 | -82.436906 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=378
Sanitary Sewer Spill | 20177196 | The Utility District staff responded to a pump failure due to overload in VFD. This overload caused the #4 pump to failure, causing a sanitary sewer overspill. Emergency Response Team started corrective actions by cleaning and pumping out catch basin and applying lime to hard surface road. Sampling has been requested due to discharged into body of water. Spillage enter into a catch basin north of the spill. Back to normal at 4:25pm on September 11, 2017. | 09/12/2017 12:54 PM | City of Riviera Beach | 600 West Blue Heron Blvd.; Riviera Beach FL; 33404 |  | Allen J. Davis | Superintendent | adavis@rivierabch.com | (561) 845-4185 | 4186 | Operator Of the Facility | Allen J. Davis | (561) 845-4185 |  | adavis@rivierabch.com | 09/11/2017 04:00 PM | 09/11/2017 04:25 PM | Palm Beach |  | N | 26.770999 | -80.083535 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=377
PCU DS-168 9/11/17 | 20177250 | Manholes overflowed associated to pump station 168 located at 6990 125th Street N. Started at 9/11/17 @ 10:00 and ceased at 9/12/17 at 06:14. Generators in place and/or rotated until power was restored - debris clean-up as needed. Samples met state surface water bacteriological criteria. Signs have been removed. Waterway Affected: Intracoastal waterway & retention pond. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount: 259,725 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Samples have been collected. Please contact our office if there are any questions. (DEP Incident #440) tied to DEP Incident # 376 Pump Station 168 Power Outage - calls from 13030 Poinsettia Avenue 6719 121st Street North 6910 121st Street North 13310 72nd Terrace North | 09/12/2017 12:46 PM | South Cross Bayou AWWTF Service Area - FL0040436 | 7401 54th Avenue North; St Petersburg FL; 33709 - 1374 |  | Matthew Wotowiec | Water Quality Monitoring Manager | mwotowiec@pinellascounty.org | (727) 599-4273 |  | Pinellas County Utilities Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 10:00 AM | 09/12/2017 06:15 AM | Pinellas |  | N | 27.836951 | -82.819072 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=376
City of Quincy Circle Drive Lift Station Spill | 20177240 | On 9-11-17 at approximately 0400 the Circle Drive lift station lost power due to Hurricane Irma. The Station started spilling at approximately 0500 on the same night. The station spilled until around 1400 on 9-11-17 when power was restored to the station. Lime has been applied to the spill areas but their was no recoverable liquid. The spill ran into Tanyard Creek behind the station. Samples will be collected. | 09/12/2017 12:34 PM | City of Quincy Circle Drive Lift Station | Off south Circle Drive; Quincy FL; 32351 |  | Denvil Presnal | Project Manager | dpresnal@ch2m.com | (850) 627-2089 |  | Operator Of the Facility | Denvil Presnal | (850) 627-2089 |  | dpresnal@ch2m.com | 09/11/2017 05:00 AM | 09/11/2017 02:00 PM | Gadsden |  |  | 30.576928 | -84.559636 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=375
Pat Thomas Law Enforcement Lift Station | 20177206 | Lift station over flow due to power outage. | 09/12/2017 12:27 PM | Gadsden East WWTP | FL; 32303 |  | John | Manager of Water Services | John.Hallas@talquinelectric.com | (850) 514-4713 |  | Owner Of the Facility | John Hallas | (850) 514-4713 |  | John.Hallas@talquinelectric.com | 09/11/2017 02:00 AM | 09/11/2017 12:25 PM | Gadsden |  |  | 30.550308 | -84.491123 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=374
Town of Havana 12 Ave Lift Station Spill | 20177239 | The Town of Havana had a spill at the 12th Ave Lift Station starting at about 0300 in the morning on 9-11-17 due to loss of power to the station. The station spilled until approximately 1800 on 9-11-17 when power was restored to the station from the utility. | 09/12/2017 12:24 PM | 12th Ave Lift Station | ; Havana FL; 32324 |  | Denvil Presnal | Project Manager | dpresnal@ch2m.com | (850) 627-2089 |  | Operator Of the Facility | Denvil Presnal | (850) 624-7208 |  | dpresnal@ch2m.com | 09/11/2017 03:00 AM | 09/11/2017 06:00 AM | Gadsden |  |  | 30.618639 | -84.412013 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=373
Hurricane Irma Incidents - 1 |  | Hurricane Irma had catastrophic statewide impacts, including historic rainfall and unprecedented river surges. JEA has begun damage assessment of its water, wastewater and reuse systems. Once these assessments have been completed and identified, JEA will provide information as required by state regulatory agencies and on jea.com. Sanitary Sewer Overflows Sanitary sewer overflows occurred at various locations throughout JEA¿s service area due to Hurricane Irma. Crews are working to determine spill locations and volumes. Below are three known incidents. Further updates will be provided as they become available. 1. Incident a. Incident Address: 9441 Beauclerc Cove Rd., Jacksonville FL 32257 - At approximately 12:01 am 9/11/2017 JEA identified a power outage at lift station causing an approximately 100-gallon release from manhole to Strawberry Creek. b. Incident Address: 1058 Wilderland Drive, Jacksonville FL 32225 - At approximately 12:01 am 9/11/2017 JEA identified a power outage at lift station causing an approximately 30-gallon release from manhole into marsh area of Mt. Pleasant Creek. c. Incident Address: 1647 Brookview Drive S, Jacksonville FL 32246 - At approximately 12:01 am 9/11/2017 JEA identified a power outage at lift station causing an approximately 2,000-gallon release from manhole to Ginhouse Creek. 2. There was no enduring risk to public health, safety or welfare. The Florida Department of Environmental Protection has been notified. Partially Treated Wastewater As a result of Hurricane Irma, a number of JEA wastewater plants experienced treatment impacts resulting in partially treated wastewater, including temporary loss of disinfection at the 4 plants listed below. The partially treated effluent was discharged offsite to state surface waters. JEA aggressively deployed assets and people to restore normal operations. All disinfection systems are back in operation. ¿ District II WRF (1840 Cedar Bay Road, Jacksonville, FL, 32218) lost disinfection for approximately 7 1/2 hours. (located at 30¿ 25¿ 32¿ N, 81¿ 37¿ 7¿ W) ¿ Arlington East WRF (1555 Milcoe Road, Jacksonville FL 32225) lost disinfection for approximately 2 1/2 hours (located at 30¿ 20¿ 40.794¿ N, 81¿ 32¿ 35.37¿ W) ¿ Mandarin WRF (10828 Hampton Road Jacksonville Fl 32257) lost disinfection for less than 1 hour (located at 30¿ 10¿ 44.49¿ N, 81¿ 37¿ 20.68¿ W) ¿ Blacks Ford WRF (1245 Reclamation Drive, Jacksonville Fl 32259 - St. Johns County) lost disinfection for less than 1 hour (located at 30¿ 4¿ 39.38¿ N, 81¿ 35¿ 5.56¿ W) See https://www.jea.com/environment/environmental_incident_reporting/ for more details | 09/12/2017 12:13 PM | JEA | 21 West Church St.; Jacksonville FL; 32206 |  | Alan Tablada | Manager, Environmental Incident Response | tablas@jea.com | (904) 703-0425 |  | Environmental | Alan Tablada | (904) 703-0425 |  | tablas@jea.com | 09/11/2017 07:15 AM |  | Duval, St. Johns |  | N | 30.330569 | -81.657337 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=372
L/S# 15 Overflow | 20177260 | LS # 15 power loss due to Hurricane Irma resulting in overflow from manhole outside station. Wastewater did make it to Cross Bayou Canal. Estimated 4000 gallons escaped. | 09/12/2017 12:01 PM | LS#15 | 6901 102nd Ave N; Pinellas Park FL; 33782 |  | Ryan Gonzalez | Utilities Foreman | Rgonzalez@pinellas-park.com | (727) 369-5707 |  | Operator Of the Facility | Ryan Gonzalez | (727) 369-5707 |  | Rgonzalez@pinellas-park.com | 09/11/2017 01:00 PM | 09/11/2017 02:00 PM | Pinellas |  |  | 27.864901 | -82.7358 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=371
Hermosa Lift-station | 20177255 | Incident started 9/11/2017 at 11:00 am 2017 at the Hermosa Lift-station and end at 6:00 am 9/12/2017. Total spill was 25000 gal. Clean up is completed. | 09/12/2017 11:52 AM | Hermosa Lift-station | 3305 Shoal Line BLVD.; Hernando Beach FL; 34607 | On the southwest corner of Hermosa Blvd. and Shoal Line Blvd. | James Minnie | Asset Information Specialist | jminnie@co.hernando.fl.us | (352) 754-4490 | 35512 | Asset Information Specialist | Larry Cooper | (352) 754-4490 |  | lcooper@co.hernando.fl.us | 09/11/2017 11:00 AM | 09/12/2017 06:00 AM | Hernando |  |  | 28.48121 | -82.650412 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=370
PCU DS-360 9/11/17 | 2017215 | Manholes overflowed associated to pump station 360 located at 3820 Lake Point Rd., Palm Harbor. Started at 9/11/17 @ 11:43 and ceased at 9/11/17 at 11:58. Generators in place and/or rotated until power was restored - debris clean-up as needed. Waterway Affected: none. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount: 33,817 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions. Pump Station 360 Power Outage - calls from 3878 Tarian Court 3890 Tarian Court | 09/12/2017 11:30 AM | W.E. Dunn WRF | 4111 Dunn Drive, Palm Harbor, FL 34683; Palm Harbor FL; 34683 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:45 AM | 09/11/2017 12:00 PM | Pinellas |  | N | 28.08015 | -82.712309 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=369
TWA Cypress West WRF effluent spill |  | On September 10, 2017, at approximately 7:30 PM, an effluent reuse spill began at the Cypress West WRF. The facility was hydraulically overloaded due to Hurricane Irma. By approximately 7:30 PM the 1.5 MG ground storage tank was full and flow had to be diverted to the reject ponds. Cypress West is currently permitted for 3.0 MGD and at 7:30 PM over 13.0 MGD was coming into the facility. Once the GST was full, flow had to be diverted to the reject ponds via the effluent transfer pumps. The effluent transfer pumps were unable to keep up with the hydraulic overload; overflowing the CCC's. The spill was mostly contained onsite in the storm water ponds and had met all discharge compliance parameters. The volume of effluent spill was estimated to be 1.5 million gallons. The spill was stopped at approximately 9:00 AM on September 11, 2017. The State Watch Office was called and produced incident report #2017-7173. | 09/12/2017 11:26 AM | TWA Cypress West WRF | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5000 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5000 |  | environmental@tohowater.com | 09/10/2017 07:30 PM | 09/11/2017 09:00 AM | Osceola |  | N | 28.150359 | -81.501721 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=368
PCU DS-356 9/11/17 | 20177214 | Manholes overflowed associated to pump station 356 located at 1231 Queen Ann Blvd., started at 11:43 and ceased at 9/11/17 @ 14:04. Generators in place and/or rotated until power was restored - debris clean-up as needed. Storm System affected: Went in storm drain to man-made ditch to wetland/forested area. Samples met state surface water bacteriological criteria. Waterway Affected:none. SSO discharge volumes have been revised as a result of re-evaluation by SCB staff, based on data obtained from SCADA. Spill amount: 76,395 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions. (DEP Incident #367) tied to DEP Incident # 379. Pump Station 356 Power Outage - calls from 2949 Briar Cliff Drive 2963 Huntington Court 2976 Huntington Court 2976 Huntington Court 1121 Queen Anne Drive 2948 Sutherland Court | 09/12/2017 11:09 AM | W.E. Dunn WRF | 4111 Dunn Drive, Palm Harbor, FL 34683; Palm Harbor FL; 34683 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 11:45 AM | 09/11/2017 02:05 PM | Pinellas |  | N | 28.076116 | -82.730164 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=367
TWA Lake Marion WRF Aeration Basin Overflow #2 |  | On September 12, 2017, starting approximately in the early morning hours and ending at approximately 6:00 AM, a mixed liquor wastewater spill occurred at the Lake Marion WRF. The cause of the spill excessive rainfall from Hurricane Irma, which caused the aeration basins to splash over the walls, resulting in an estimated 5,000 gallon spill. | 09/12/2017 11:00 AM | TWA Lake Marion WRF (FL0036862) | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5000 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5000 |  | environmental@tohowater.com | 09/12/2017 12:00 AM | 09/12/2017 06:00 AM | Polk |  |  | 28.063452 | -81.493657 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=366
TWA Lake Marion WRF Aeration Basin Overflow |  | On September 11, 2017, starting at approximately 8:00 AM and ending at approximately 11:30 AM, a mixed liquor wastewater spill occurred at the Lake Marion WRF. The cause of the spill excessive rainfall from Hurricane Irma, which caused the aeration basins to splash over the walls, resulting in an estimated 3,000 gallon spill. | 09/12/2017 10:56 AM | TWA Lake Marion WRF (FL0036862) | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5000 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5000 |  | environmental@tohowater.com | 09/11/2017 08:00 AM | 09/11/2017 11:30 AM | Polk |  |  | 28.063422 | -81.493682 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=365
CC/EQ Overflow | 20177246 | Date of Occurrences: 09/10/17 from 10pm to 4:30am 09/11/17 and 09/11/17 10am to 3am 09/12/17 Chlorine Contact and Equalization Basin overflow due to storm Approximately 2 million gallons of treated effluent overflow onto ground Surface Water impacted: Thompson Creek No cleanup efforts | 09/12/2017 10:43 AM | Ormond Beach WWTP | 550 North Orchard Street; Ormond Beach FL; 32174 | From I95 to West State Rd 40 to North on Orchard Street | Sammy Butler Sr | Chief Plant Operator | butler@ormondbeach.org | (386) 676-3592 |  | Operator Of the Facility | Sammy Butler Sr | (386) 676-3592 |  | butler@ormondbeach.org | 09/10/2017 10:15 AM | 09/12/2017 03:00 AM | Volusia |  |  | 29.288796 | -81.073885 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=364
Bartow Process Water Release | 20177167 | In the early afternoon of Monday, September 11, 2017, following an extreme rain event caused by Hurricane Irma, a process water ditch containing 2% phosphoric acid at Mosaic Fertilizer¿s (Mosaic) Bartow Chemical Plant in Bartow, Florida was inundated with storm water, causing the ditch to overtop its banks. The indeterminate volume of process and rain water then flowed into a storm water impoundment and second ditch. Mosaic closed valves downstream of the impoundment and ditch, keeping the release onsite. Thereafter, Mosaic began to recover the water. | 09/12/2017 10:30 AM | Mosaic Bartow Chemical Plant | 3200 Hwy 60 West; Bartow FL; 33830 |  | Scott Lehr | Manager, EHS Regulatory & Compliance | scott.lehr@mosaicco.com | (813) 500-6779 |  | Environmental Manager | Keith Nadaskay | (863) 800-9259 |  | keith.nadaskay@mosaicco.com | 09/11/2017 01:25 PM | 09/11/2017 01:30 PM | Polk |  |  | 27.903675 | -81.914777 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=363
South Bermuda Reject Overflow |  | On Sunday, September 10, 2017 at 8:37 PM, the South Bermuda WRF went out of compliance with turbidity levels above the permitted limit. This was the result of high flows being processed through the facility, the facility was processing 19 MGD since 10:30 AM, and maintained that flow all through the day. These high flows are believed to be the result of extremely high rainfall brought about by Hurricane Irma. The facility was also forced to shut off sludge wasting as the sludge holding tanks were at a high level and the presses could not be run due to the pending hurricane. In addition, the Reject pond reached a high level, so a suitable solution to the high level of hydraulic load that was placed on the facility was unable to be accomplished. A combination of these events created a high turbidity reading that placed the facility out of compliance. This was during a time when the wind gusts were becoming hazardous to work in. During lulls between tropical storm force winds operators attempted to find a cause and solution for the high turbidity being experienced in the process. Operators found that clarifier¿s 3 & 4 were causing the turbidity and made adjustments to the flow to these units that allowed the turbidity to decrease, and the facility regained compliance status; although the facility rejected approximately 5.5 MGD during the event. The reject was contained on site and mainly contained within the storm water basins. The overflow was reported to the State Warning Point Incident # 2017-7147. | 09/12/2017 10:29 AM | TWA South Bermuda WRF (#FLA010957) | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5000 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5000 |  | environmental@tohowater.com | 09/10/2017 08:35 PM | 09/11/2017 08:00 PM | Osceola |  |  | 28.275416 | -81.425767 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=362
PCU DS-012 | 20177203 | Manholes overflowed associated to pump station 012 located at 6990 9398 90th Avenue N., Seminole. Started at 9/11/17 @ 10:05 and ceased at 9/11/17 at 12:59. Generators in place and/or rotated until power was restored - debris clean-up as needed. Signs have been posted. Waterway Affected: Lake Seminole Bypass Canal. Spill amount: 7,320 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Samples have been collected. Samples met state surface water criteria. Please contact our office if there are any questions. Pump Station 012 Power Outage - call from 8888 95th Street North | 09/12/2017 10:16 AM | South Cross Bayou AWRF | 7401 54th Avenue North, St Petersburg, FL 33709-1374; St Petersburg, FL; 33709 |  | Sheri Lovely | Technical Project Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Megan Ross | (727) 582-7020 |  | mross@pinellascounty.org | 09/11/2017 10:05 AM | 09/11/2017 01:00 PM | Pinellas |  | N | 27.853257 | -82.770172 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=361
PCU DS-024 9.11.17 | 20177216 | Pump station & MH's overflowing around Lake Dr. PS- belongs to PCU. Going into retention pond still needs to be verified if goes to any other surface water body.12501 Ulmerton Road, Largo ongoing until can reverify. Manholes overflowed associated to pump station 024 located at 12950 126th Avenue N., Largo. Started at 9/11/17 @ 10:05 and ceased at 9/11/17 at 15:40. Generators in place and/or rotated until power was restored - debris clean-up as needed. Waterway Affected: retention pond. Samples have been collected. Samples met state surface water criteria. SSO discharge volumes have been evaluated by SCB staff, based on data obtained from SCADA. Spill amount: 63,341 gallons. Cause of release: Hurricane Irma resulting in power failure at pump station. Please contact our office if there are any questions. Pump Station 024 Power Outage - calls from: 12501 Ulmerton Rd. | 09/12/2017 10:00 AM | South Cross Bayou AWRF | 7401 54th Avenue North, St Petersburg, FL 33709-1374; St Petersburg, FL; 33709 |  | Sheri Lovely | Technical Project Cooordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Sheri Lovely | (727) 582-2379 |  | slovely@pinellascounty.org | 09/11/2017 09:50 AM | 09/11/2017 03:40 PM | Pinellas |  | N | 27.887677 | -82.815511 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=360
Robert Mason | 1189875 | I am giving notice that per the influent flow meter during Irma the City of Oviedo WWRF located at 1067 McKinnon Ave had a 1.1 MG spill both raw and treated. Facility ld. No. FLA011074. Clean up will continue through out the day as weather conditions permit. We received currently 10.4 inches of rain at this time since yesterday morning. | 09/12/2017 09:39 AM | City of Oviedo WWRF | 1067 Mckinnon Ave.; Oviedo FL; 32765 | Alafia Woods Blvd.. to 1067 McKinnon Ave. | Robert Mason | Lead Operator | rmason@cityofoviedo.net | (407) 971-5676 | 5676 | Operator Of the Facility | Josef Grusausks | (407) 971-5679 |  | jgrusausks@cityofoviedo.net | 09/10/2017 03:30 AM | 09/11/2017 07:00 AM | Seminole |  |  | 28.698463 | -81.344824 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=359
406847 | 20177220 | WASD Incident #: 406847 Version: 2 Version Type: Supplementary Incident Version Created On: 09/11/17 09:08 PM Job Order #: 1003495745 Location of Discharge: 4801 SW 117 AVE UNINCORPORATED MIAMI-DADE 33165 Reported by WASD Employee? Yes Employee ID: 00010680 Employee Title: ASST SUPERINTENDENT Reported by: SIGFREDO SANCHEZ Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: East and West On: 48TH STREET Discharge Caused by Asset Type: WASD Pump Station WASD Pump Station: 683 Contractor Involved? No Discharge Due to/Caused by: WASD Pump Station Due to FPL Service Problem Additional Discharge Cause: GENERATOR FAILURE Pipe Material: DIP (Ductile Iron Pipe) Pipe Size in inches: 18 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? No Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Clear Estimated Quantity of Sewage Released in Gallons: 1,200 Estimated Time Release Started: 09/11/17 12:30 PM Estimated Time Action Taken at Site: 09/11/17 12:45 PM ACTION TAKEN Active Spill Observed? No Discharge Flow Stopped? Yes Discharge Stopped On: 09/11/17 12:45 PM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Public Notified? No Spill Recovered? Yes Recovered Amount in Gallons: 100 AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone TAYLOR 2017-7220 09/11/17 09:21 PM RER RER Compliance Desk Phone KATIE 09/11/17 09:21 PM WASD WASD Bertha Goldenberg Phone LVM FOR B. GOLDENBERG 09/11/17 09:21 PM DEP DEP Notification Group E-mail 09/11/17 09:21 PM DOH DOH Notification Group E-mail 09/11/17 09:21 PM EPA EPA Notification Group E-mail 09/11/17 09:21 PM HMS Hazardous Materials Subcommittee Group E-mail 09/11/17 09:21 PM RER RER Notification Group E-mail 09/11/17 09:21 PM SFWM SFWM Notification Group E-mail 09/11/17 09:21 PM WASD WASD Interdepartmental Personnel E-mail 09/11/17 09:21 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Edlyn Alcinor (ALCINE) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ Latitude: 25.7223273612441 Longitude: -80.3827732622028 09/11/17 09:21 PM * Fields on red are the ones that changed from previous version Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 09/12/2017 09:32 AM | Miami-Dade W&S Westwood Lakes Facility PS 683 | 4801 SW 117 Ave ; Miami FL; 33165 |  | Sigfredo Sanchez | Assistant Superintendant | sigfredo.sanchez@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/11/2017 12:30 PM | 09/11/2017 12:45 PM | Miami-Dade |  |  | 25.72139 | -80.382184 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=358
City of St. Petersburg LIft Station #3 | 20177222 | Power failure from Irma caused lift station pumps to cease operation and the sewer line to surcharge, causing a discharge of approximately 3,750 gallons of very diluted with raw sewage into Big Bayou. | 09/12/2017 08:45 AM | City of St. Petersburg LIft Station #3 | 2801 Bayside Drive S; St. Petersburg FL; 33705 |  | Frank Niles | WRF Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person reporting incident. | Randy Miller | (727) 892-5617 |  | randall.miller@stpete.org | 09/10/2017 10:00 PM | 09/11/2017 10:30 AM | Pinellas |  |  | 27.742375 | -82.635494 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=357
City of St. Petersburg Lift Station #53 | 20177221 | Power failure from Irma caused lift station pumps to cease operation and the sewer line to surcharge, causing a discharge of approximately 3,390 of very diluted with raw sewage into Clam Bayou. | 09/12/2017 08:32 AM | City of St. Petersburg Lift Station #53 | 4074 24th Ave S; St. Petersburg FL; 33711 |  | Frank Niles | WRF Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person reporting incident. | Randy Miller | (727) 892-5617 |  | randall.miller@stpete.org | 09/10/2017 09:45 PM | 09/11/2017 09:05 AM | Pinellas |  |  | 27.746865 | -82.688622 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=356
Sanitary Sewer Overflow - City of Orlando | 20177230 | Power outage at lift station caused the main pumps to shutdown. Generator was activated to restore flow but main pumps failed to reset on initial start up. Manual Troubleshooting of electrical system was necessary to reset pumps and restore power. While working to reset the main pumps, approximately 485,000 gallons of sanitary sewer overflowed from the lift station and into the stormwater catch basin for the area. All pumps were restored and clean up actions are currently under way to properly sanitize and clean all areas impacted by the sanitary sewer overflow. | 09/12/2017 05:49 AM | Lift Station 249 - City of Orlando | 7901 E Colonial Drive; Orlando FL; 32807 | I-4 to East Colonial Drive. Address is on left side of the road. | Daniel Friedline | Public Outreach Coordinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | Authorized Representative of the City of Orlando | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 09/11/2017 11:15 PM | 09/12/2017 01:35 AM | Orange |  |  | 28.568746 | -81.280916 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=355
St. Petersburg Lift Station #25 | 20177223 | Power failure caused to lift station #25 motor to trip , due to hurricane Irma causing sewer line to surcharge approximately 11,670 gallons of very diluted raw sewage with stormwater. | 09/11/2017 11:08 PM | Lift Station #25 | 601 Grevilla Ave S; St. Petersburg FL; 33707 |  | Frank Niles | WRF Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person filing report. | Randy Miller | (727) 892-5617 |  | randall.miller@stpete.org | 09/11/2017 01:25 AM | 09/11/2017 07:55 AM | Pinellas |  |  | 27.765401 | -82.740895 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=354
406822 |  | LAT 25.686748 LONG -80.350361 Summary Information for MDWASD Spill Report Incident # 406822 Version 2. Location of Discharge: SW 235 ST & SW 97 AVE Select Municipality and Zip Code... 0. Estimated Quantity of Sewage Released: 9,966 gallons to Surface Water. Water Discharge Type: Raw Sewage. Spill was stopped on: 09/11/17 02:00 PM. Please do not respond to this e-mail. For more detailed information, see attached report. Miami-Dade Water and Sewer Department - Emergency Communications Section (305) 274-9272. | 09/11/2017 10:39 PM | Miami-Dade W&S Collection System | SW 235 & SW 97 Ave; Miami FL; 33190 |  | Israel Camacho | WDS | israel.camacho@miamidade.gov | (305) 274-9292 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 09/11/2017 11:30 AM | 09/11/2017 02:30 PM | Miami-Dade |  |  | 25.545562 | -80.347807 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=353
Sewer Spill at Old Miramar Parkway and SW 132nd Ave. | 20177181 | As a result of Hurricane Irma, the City of Miramar experienced a sanitary sewer force main break on the north side of Old Miramar Pkwy between 136th Ave and Flamingo Rd. Sewage spilled across the parkway south into the canal along SW 132nd Ave beginning at approximately 0600 9-11-17. Field crew has been working all day to isolate the break to contain the spill; an additional contractor has been called in and repair work will continue throughout the night until completed. Residents have been notified in writing about the incident. Status of utility line repair 9-12-17: Repairs have been completed early this evening. Restoration activities to follow. Started pumping the canal which will continue for at least 24 hours. Test results of all private wells indicated no bacteria; City to commence required regulatory testing in the morning. Status of utility line repair 9-14-17: Restoration activities continue; 700 lbs of HTH (common pool chlorine) were dispersed to impacted ground and roads. City pumped and hauled a total of 312,000 gallons of water within a 24-hour time frame (5 pm 9-12-2017 through 5 pm 9-13-2017) out of the canal from the initial discharge of approximately 300,000 gallons. All private wells at residences adjacent to the canal were retested 9-13-2017; results thus far are negative for fecal coliform. City continues required regulatory testing. Booms are being placed to trap floating potentially- contaminated debris. Skimming will be conducted tomorrow. City updating the residents daily with hand-delivered door hangers. The cause of the force main break has been identified as hurricane winds and rain saturated the berm and ground beneath where the PVC pipeline is buried; a huge oak tree with a root ball of approx. 4-5 ft that was on the berm was partly uprooted, triggering enough vibration and friction to cause a longitudinal crack to erupt. Status as of 9-18-17: The City also contracted an Environmental Restoration Company (Clean Harbors) to assist with the canal clean-up efforts. To date, Clean Harbors has placed floating booms in the canals and have skimmed both canals of floating debris. Clean Harbors also placed an aeration system in the canal located on 132nd Avenue to increase the dissolved oxygen in the canal system. Status as of 9-19-17: Required compliance testing at the Point of Entry (SW 132nd Canal, north end), upstream (West Water Treatment Plant Backgate canal - 200 ft Upstream) and downstream (West Water Treatment Plant Main Road - 200 ft Downstream) has now been completed due to all three sampling locations dropping below 800 Fecal Coliform count (CFU/100 mL), established by regulation as it reflects ambient conditions. | 09/11/2017 08:04 PM | City of Miramar WWRF | 13900 Pembroke Road, Miramar FL 33027; Miramar FL; 33027 | sewer spill: Old Miramar Pkwy and 132nd Avenue | Jose G. Cardoso | Regulatory Compliance Officer | jgcardoso@miramarfl.gov | (954) 883-6851 |  | Regulatory Compliance Officer | Robin Bain, P.E. | (954) 883-6825 |  | rebain@miramarfl.gov | 09/11/2017 06:00 AM | 09/12/2017 06:00 PM | Broward | Broward | Y | 25.978826 | -80.324303 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=352
WRF #2 4200 SE 24th St Ocala, FL | 20177172 | Chris Wildner reported incident to David Smicherko @ David.Smicherko@dep.state.fl.us on 9/11/17 | 09/11/2017 06:15 PM | WRF #2 | 4200 SE 24th St ; Ocala FL; 34471 |  | Chris Wildner | Lead Plant Operator | CWildner@ocalafl.org | (352) 401-6929 |  | Operator Of the Facility | Chris Wildner | (352) 401-6929 |  | CWildner@ocalafl.org | 09/10/2017 11:45 PM | 09/11/2017 04:35 PM | Marion |  |  | 29.163364 | -82.072543 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=351
City of Pompano Beach Wastewater Spill | 20177212 | Hurricane Irma resulted in wastewater spill from Lift Station. LS 35 at 1030 NE 27th Terrace approximately 48,000 from 10:30am to 1:00pm which discharged to a storm drain then into a water body along the intercostal. LS 35 released an additional 1000 gallons on land from 11:00pm to 11:15pm. | 09/11/2017 06:09 PM | City of Pompano Beach | 1205 NE 5th Ave; Pompano Beach FL; 33060 |  | Shana Coombs-Gordon | Interim Utility Compliance & Efficiency Manager | shana.coombs@copbfl.com | (954) 549-9684 |  | Employee | Steve Almyda | (954) 803-2932 |  | steve.almyda@copbfl.com | 09/11/2017 10:30 AM | 09/11/2017 01:00 PM | Broward | Broward | Y | 26.243476 | -80.095476 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=350
Georgia-Pacific Palatka Hurricane Irma Storm Water Impacts | 20177176 | Storm water and storm water mixed with small amounts of process water overflowed from our collection system into wetlands that eventually go to Rice Creek. Amount unknown at this time, but believed to be greater than 1,000 gallons. Processes were down. Environmental impact believed to be negligible due to minimal exposure to wastewater. | 09/11/2017 06:00 PM | Georgia-Pacific Consumer Operations LLC | 215 County Road 216; Palatka FL; 32177 | From US 17 west/north from Palatka, turn left on County Road 16. The Georgia-Pacific Mill will be on the right side of the road. Lat: 29.676111 N Long: 81.679167 W | Terry Hadaway | Public Affairs Manager | Raymond.Hadaway@GAPAC.com | (386) 972-4231 |  | Public Affairs Manager for Georgia-Pacific Palatka | Jim Eckenrode | (770) 843-3302 |  | jpeckenr@gapac.com | 09/10/2017 04:30 PM |  | Putnam |  |  | 29.67579 | -81.679716 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=349
City of Pompano Beach Wastewater Spill | 20177213 | Hurricane Irma resulted in wastewater spill from Lift Station. LS 90 at 351 SW 2nd Court approximately 36,000 from 9am to 11am which discharged into a water body along the intercostal. LS 90 released an additional 2000 gallons from 10pm t 10:15pm on land. | 09/11/2017 06:00 PM | City of Pompano Beach | 1205 NE 5th Ave; Pompano Beach FL; 33060 |  | Shana Coombs-Gordon | Interim Utility Compliance & Efficiency Manager | shana.coombs@copbfl.com | (954) 549-9684 |  | Employee | Steve Almyda | (954) 803-2932 |  | steve.almyda@copbfl.com | 09/11/2017 09:00 AM | 09/11/2017 11:00 AM | Broward | Broward | Y | 26.228682 | -80.130561 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=348
Sanitary Sewer Overflow - City of Orlando | 20177197 | Power outage at City lift station 94 incapacitated the lift station pumps and eventually caused a sanitary sewer overflow. The overflow occurred from the upstream manhole directly prior to the lift station and approximately 5000 gallons was released. City crews responded to the lift station with a generator, hooked it up properly, and were able to restore power to the station. The pumps were activated for the station and flow was restored. City crews sanitized and cleaned all areas impacted by the sanitary sewer overflow. | 09/11/2017 05:40 PM | City of Orlando Public Lift Station 94 | 5169 Lido Street ; Orlando FL; 32807 | Take Gaston Foster Rd North. Turn Right on Andrea Blvd and then left on Jessica Ave. Turn right on Lido Street. | Daniel Friedline | Public Outreach Coordinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | Authorized Representative of the City of Orlando | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 09/11/2017 12:30 PM | 09/11/2017 03:30 PM | Orange |  |  | 28.531049 | -81.321219 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=347
Event 126 | 20177195 | Generator at lift station 123 was in auto working off float balls when fuse failed causing wastewater to overflow station and flow into Lake Howard. Generator was placed into manual and station pumped down. Fuse was then replaced. | 09/11/2017 04:58 PM | Lift Station 123 | Ave F SW and Lake Howard Drive; Winter Haven FL |  | Terry Carver | Wastewater Superintendent | tcarver@mywinterhaven.com | (863) 291-5766 |  | Operator Of the Facility | Terry Carver | (863) 291-5766 |  | tcarver@mywinterhaven.com | 09/11/2017 08:30 AM | 09/11/2017 09:00 AM | Polk |  |  | 28.015939 | -81.749006 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=346
GRU Wastewater Collection System - Hurricane Irma |  | 9/27/2017 UPDATE: Following Hurricane Irma, GRU Water/Wastewater Engineering has been conducting environmental assessments throughout our service area. Part of this effort included walking creek banks to inspect our wastewater infrastructure located in remote areas. During an assessment this morning an active wastewater release was discovered. Due to high stormwater conditions during Hurricane Irma, the sediments surrounding a manhole and gravity main were undermined and the gravity main broke. Our crews have repaired the break and we have posted advisory signs in the area. It is estimated that approximately 30,000 gallons of wastewater was released from this location into Hogtown Creek since the storm event. GRU has coordinated with regulatory authorities and is conducting water quality sampling of the creek. The release is located in a wooded area near the 1600 block of NW 35th Pl. ---------------------------------------------------------------------------------------------------- 9/20/2017 REPORT: Hurricane Irma impacted the GRU service area from approximately 3 pm on September 10 through 1 pm September 11, 2017. The storm was an extreme weather event that exceeded the 100 year storm for the Gainesville area and brought over 12 inches of rain. For approximately 24 hours, GRU¿s service area was inundated with stormwater and sustained high winds. It is estimated that over 24 billion gallons of rain flooded our service area. High rainfall from Irma, combined with high water tables from record rainfall this summer, resulted in GRU¿s wastewater collection system being inundated with stormwater. High winds resulted in power outages at 92 of our 170 lift stations. A total of 41 generators were utilized in the system during the storm and throughout the recovery response. During the hurricane and in the following days, it is estimated that approximately 3.5 million gallons of combined stormwater and wastewater were released from the collection system. It is estimated that approximately 80% (or 2.8 million gallons) of the release was stormwater and 20% (or 0.7 million gallons) was wastewater. When the sustained winds returned to safe levels, GRU crews immediately mobilized and began assessing the collection system and responding to known release events. GRU worked around the clock to assess and respond to releases in our area. Assessment teams noted 48 release sites which were assessed daily until full recovery was achieved. Sites have been cleaned and disinfected and advisory signs have been posted. GRU and private pumpers hauled over 13.8 million gallons of stormwater and wastewater from the collection system to mitigate release impact and help bring the system back to normal operation. GRU is working closely with the Alachua County Environmental Protection Department to sample our creek system and determine the overall impact. While assessment of the creeks during and immediately following the storm was unsafe due to high flows, it is assumed that releases in the vicinity of creeks likely made an impact. As a precaution, GRU has placed advisory signs at public access areas of the creeks near known releases. Water quality sampling has begun and is showing improvements. Advisory signs will remain posted until the water quality returns to background levels. **The original report contained a list of specific locations and release volumes. Due report size limitations that information is not included in this update. Please email mcelroyja@gru.com for additional information. | 09/11/2017 04:55 PM | GRU Wastewater Collection System | FL; 32614 |  | Jennifer McElroy | Supervising Utility Engineer | mcelroyja@gru.com | (352) 393-1291 |  | Supervising Engineer | Tiffany Small | (352) 393-1492 |  | smalltn@gru.com | 09/10/2017 05:00 PM | 09/20/2017 04:00 PM | Alachua |  | N | 29.666807 | -82.290147 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=345
Sanitary Sewer Overflows |  | Sanitary sewer overflows occurred at various locations throughout the City's service area due to Hurricane Irma. Crews are working to determine exact spill locations and volumes. Updates will be provided when they become available. Sanitary Sewer Overflow Incidents: a) Incident Address: 14 Isla Drive 9/11/17 to 9/12/17, approximately 6,700 gallons spilled due to power failure at pump station (SWP# 2017-8014); b) Incident Address: 1075 N. Ponce de Leon Blvd on 9/11/17, approximately 5,250 gallons spilled due to power failure at pump station and flooded control panel/station, causing a release to the San Sebastian River. An additional 4,455 gallons spilled at this station due to bypass pump failures on 9/12/17 and 9/13/17 (SWP# 2017-8015); c) Incident Address: 1 Helen Street on 9/11/17, approximately 48,700 gallons spilled due to pump station power failure and flooded control panel, causing a release to the San Sebastian River (SWP# 2017-8017). d) Incident Address: 144 Riberia Street on 9/11/17, approximately 27,500 gallons spilled due to power failure at pump station and flooded control panel, causing release to the San Sebastian River (SWP# 2017-8024); e) Incident Address: 254 Riberia Street on 9/11/17, approximately 36,500 gallons spilled due to power failure at pump station and flooded control panel, causing a release to the San Sebastian River (SWP# 2017-0827); f) Incident Address: 39 Ocean Ave on 9/11/17, approximately 3,000 gallons spilled due to power failure at pump station and flooded control panel, causing release to Hospital Creek (SWP# 2017-8035); g) Incident Address: 40 Joiner Street on 9/11/17 and 9/12/17, approximately 27,750 gallons spilled due to power failure at pump station and flooded control panel, causing release to Hospital Creek (SWP# 2017-8036); h) Incident Address: Pine Street 200 ft East of San Marco Ave on 9/14/17, approximately 450 gallons spilled due to manhole overflow because bypass pump at pump station lost prime, causing release to Hospital Creek (SWP# 2017-8018); i) Incident Address: 177 Avenida Menendez on 9/11/17, approximately 13,750 gallons spilled due to pump station power failure and flooded control panel, causing spill to Lake Maria Sanchez and the Matanzas River (SWP# 2017-8025); j) Incident Address: 1710 US 1 South on 9/11/17, approximately 23,400 gallons spilled due to pump station power failure, causing release to the San Sebastian River; k) Incident Address: 5A Arredondo Ave on 9/11/17, approximately 33,500 gallons spilled due to power failure at pump station and flooded control panel, causing a release to the Matanzas River. This station spilled twice more on 9/12/17 due to downstream bypass pump over-running capacity of station, causing an additional 4,000 gallons to spill (SWP# 2017-8032); l) Incident Address: 88 Coquina Street on 9/11/17, approx. 40,950 gallons spilled due to power failure at pump station and control panel flooding, causing a release to Quarry Creek/Matanzas River (SWP# 2017-8035); m) Incident Address: 32 Solano Ave on 9/13/17, manhole overflowed due to downstream system surcharge, causing a release of approximately 1,000 gallons to Quarry Creek/Matanzas River (SWP# 2017-8038); n) Incident Address: 13 Ferry Place on 9/11/17, approximately 110,000 gallons spilled due to power failure at pump station, causing release to the San Sebastian River (SWP# 2017-8042); o) Incident Address: 305 Hefferon Drive on 9/12/17, manhole overflowed twice due to power outage at pump station, causing spill of 161 gallons to retention pond (SWP# 2017-8043); p) Incident Address: 907 S. Ponce de Leon Blvd on 9/12/17, residential clean-out spilled due to power outage at pump station, causing spill of approximately 50 gallons (SWP# 2017-8056); q) Incident Address: 900 N. Ponce de Leon Blvd on 9/14/17 manhole overflowed due to water main break inundating manhole, causing approximately 1,000 gallons to spill (SWP# 2017-8059). | 09/11/2017 04:40 PM | City of St. Augustine | FL |  | Glabra Skipp | Environmental Compliance Analyst | gskipp@citystaug.com | (904) 825-1055 |  | Environmental Compliance Analyst | Glabra Skipp | (904) 825-1055 |  | gskipp@citystaug.com | 09/11/2017 08:00 AM | 09/14/2017 04:15 PM | St. Johns |  | N | 29.875974 | -81.310583 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=344
Crews Park Lift Station - Hurricane Irma |  | Called state watch office with no answer. Due to Hurricane Irma, Peace River is steadily rising. Lift station at Crews Park is underwater. Lift stations serves approximately 30 homes. Crews will try to get a pump to it. | 09/11/2017 04:16 PM | Crews Park Lift Station | 130 Park Drive; Wauchula FL; 33873 | From Bartow, head south on US 17, once in Wauchula, turn left to head east on Main Street. Turn left on Riverside drive just before reaching Peace River. Turn right on Park Drive. Lift station is at the end of the road. | Olivia Minshew | Assistant City Manager | ominshew@cityofwauchula.com | (863) 773-9193 |  | Owner Of the Facility | Andy Maddox | (863) 781-1976 |  | andy@cityofwauchula.com | 09/11/2017 02:40 PM |  | Hardee |  |  | 27.551267 | -81.795235 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=343
City of Clermont |  | Three lift stations overflowed during lockdown while hurricane Irma passed over. Total time approx 4 hours with a total flow of 170,000 gallons. Reported to State Warning Point 9/11/17 at 3:00pm. | 09/11/2017 03:13 PM | Clermont/East WWTF | 3335 Hancock Road; Clermont FL; 34711 |  | Mark Griffin | Environmental services coordinator | Mgriffin@clermontfl.org | (352) 241-0178 | 6623 | Representative | Mark Griffin | (352) 241-0178 |  | Mgriffin@clermontfl.org | 09/11/2017 12:00 AM | 09/11/2017 03:00 PM | Lake |  |  | 28.55631 | -81.763163 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=342
Seminole Generating Station Pond Overflow - Hurricane Irma | 20177180 | At this time, we foresee no threat to human health or the environment from this discharge. Should this change, we will advise appropriately. On September 11, 2017 at 0650 Seminole Generating Station in Putnam County experienced an overflow of an on-site industrial wastewater pond. The purpose of this pond is to collect stormwater runoff from a coal pile within the facility. This overflow was a result of excessive rains caused by Hurricane Irma. The overflow occurred within Seminole's property boundary. Water samples of the discharge have been collected and are currently being analyzed by on-site technicians. Due to the significant influx of stormwater it is anticipated the quality of the discharge will be similar to rainfall. Due to limited resources available during the hurricane, Seminole is unaware if the discharge is ongoing and have not determined the amount of water discharged. Once hurricane conditions have receded and Seminole can return to full staff, Seminole will inspect the discharge area and conduct a full investigation and provide a written follow up. UPDATED INFORMATION 9/15/17: Upon ensuring stabilized and safe operational conditions, Seminole employees inspected the Coal Storage area run-off pond on Tuesday September 12th at 1000 hours. High wind and heavy rain driven over-topping of the pond had ceased and the surrounding berm area appeared to be structurally sound. Data indicates that the facility received over 10 inches of rainfall within the 24-hour period beginning Sunday September 10th at 0800 hours. This amount of rainfall is in excess of the defined 25-year, 24 hour storm amount (7.9 inches) and near the 25-year, 48 hour storm amount (10.54 inches). Follow-up engineering estimates and monitoring results indicate the discharge may have exceeded 1.6 Million gallons at a pH of 2.98 and conductivity of 1,644 ¿s/cm. Overflow of the associated pond is to an adjacent on-site storm-water ditch that is routed with various other drainage areas to a wetland area within Seminole property. Accordingly, Seminole believes that significant rainwater dilution of the discharge occurred prior to wetland inflow. Environmental impacts were not observed nor are they expected, however Seminole will continue to monitor the area for signs of vegetative distress. UPDATED INFORMATION 9/20/17: Post-restoration assessment of the area and associated review of drainage basin maps suggest an indeterminate portion of the previously reported coal pond overflow likely drained north to an off-site ditch paralleling the nearby railroad line. Accordingly, Seminole is amending the previous notice with respect to heavily diluted wastewaters reaching off-site areas. We do not believe identification of the additional discharge area alters previously reported information regarding no expected environmental impacts. | 09/11/2017 03:11 PM | Seminole Generating Station | 890 Highway 17 North; Palatka FL; 32177 | Entrance 5.6 miles north of Highway 17/Highway 19 intersection in Palatka. | Justin Gostnell | Senior Environmental Coordinator | jgostnell@seminole-electric.com | (813) 244-4877 |  | Corporate Environmental Staff | Ryan Hart | (813) 739-1402 |  | communications@seminole-electric.com | 09/11/2017 06:50 AM | 09/12/2017 10:00 AM | Putnam | Putnam | Y | 29.733713 | -81.636527 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=341
Event 125 | 20177154 | Air relief valve blew apart at WWTP # 3 causing approximately 13,000 gallons of sewage to spill. The line was capped until another air relief can be purchased. Cause began around 9/10/17 at 8:30am and was repaired 9/11/17 7:30am. Spill area was limed | 09/11/2017 12:37 PM | WWTP # 3 FL0036048 | 4400 Pollard Road Winter Haven FL 33884; Winter Haven FL; 33884 |  | Terry Carver | Wastewater Superintendent | Tcarver@mywinterhaven.com | (863) 291-5766 |  | Operator Of the Facility | Terry Carver | (863) 291-5766 |  | tcarver@mywinterhaven.com | 09/10/2017 08:30 AM | 09/11/2017 07:30 AM | Polk |  |  | 27.95324 | -81.710152 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=340
Marshall Street WRF 9/11/2017 | 20177119 | At 12: 50 am, the facility lost power to the main control room. This incident caused us to lose power to our airbays, clarifiers, and the filter feed pumps. The back up generator came on however, the automatic transfer switch did not function properly because there was partial power on the utility side of the transfer switch. With no power to our Filter Feed pumps this caused the loss of approximately 1.6 million gallons of secondary treated effluent which flowed into Stevenson Creek. The problem was corrected at 3:45 am when the generator controls were able to reset which allowed the emergency power to start up. The State Warning Point was notified at 2:00 am. Report # 20177119. | 09/11/2017 11:40 AM | Marshall Street WRF | 1605 Harbor Drive; Clearwater FL; 33755 |  | Ron Nelson | Chief Operator | ron.nelson@myclearwater.com | (727) 224-7691 |  | Operator Of the Facility | Jason Jennings | (727) 224-7477 |  | jason.jennings@myclearwater.com | 09/11/2017 12:50 AM | 09/11/2017 03:45 AM | Pinellas |  |  | 27.981274 | -82.787527 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=339
City of Sanford NWRF overflow | 20177084 | Due to high flows to the City's NWRF caused by Hurricane IRMA, even with all six (6) influent master lift station pumps operating, the manhole on the main influent line overflowed. Update: The volume over the 6 hour period of the sanitary sewer overflow occurring upstream of the NWRF master lift station was approximately 2 million gallons. | 09/10/2017 08:07 PM | City of Sanford North Water Reclamation Facility | 300 N. Poplar Ave; 1201 W. Seminole Blvd.; Sanford FL; 32771 |  | Richard Casella | Interim Plants Operation and Maintenance Manager | richard.casella@sanfordfl.gov | (407) 417-7733 |  | Plant Manager | Richard Casella | (407) 417-7733 |  | richard.casella@sanfordfl.gov | 09/10/2017 07:05 PM | 09/11/2017 01:00 AM | Seminole | Seminole | Y | 28.814039 | -81.2777 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=338
WinterPark DR./Marigold Rd., Casselberry, FL. | 20177041 | On September 10, 2017 at 1505 ET, Alan Richards with Duke Energy contacted ERTS regarding a Distribution transformer release on a residential roadway; S Winter Park Dr & Marigold Rd, Casselberry, FL 32707 . It was reported that on a pole-mounted transformer encountered a mechanical failure in which the grounding shorted, burning a hole in the bottom of the transformer. Approximately 1-5 gallons released to the soil and asphalt below then was washed into a drain by the Hurricane Irma storm inbound. Per Alan Richards, the release is unrecoverable. A storm drain was impacted by the release. Alan Richards advised that he will create a FMDR for this incident. No media, fire or road closures were reported. No further assistance was requested from ERTS. 1515 Alan Richards advised that a drain was impacted. Due to the drain and waterway impaction, the NRC has been notified. 1517 P.O. Justin Murray with the NRC took receipt of the call and issued report number 1189849. No further regulatory reporting shall be conducted, per Devin Barzilay. Upon further evaluation, this was not required to be reported to the NRC, State Watch Office, and/or the DEP. (Updated 1:41 PM on 9/20/2017 by Devin Barzilay, Duke Energy.) | 09/10/2017 07:18 PM | Water Treatment Plant | Intersection of Winter Park Dr./Marigold Rd.; Casselberry FL |  | Devin Barzilay | Environmental Spill Coordinator | Devin.Barzilay@Duke-Energy.com | (352) 573-6473 |  | Environmental SpillCoordinator | Duke Energy Corporate Communications | (800) 559-3853 |  | Duty-CorpComm@Duke-Energy.com | 09/10/2017 03:10 PM | 09/10/2017 04:10 PM | Seminole |  | N | 28.770328 | -81.206617 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=337
GTL Power Outage Switch Over | 20176988 | FLA041378 - George T. Lohmeyer Regional Wastewater Treatment Facility lost FPL power at 9:38 PM on Saturday, September 9th during Hurricane Irma due to loss of the primary plant feed. Power was restored within 1 minute but the power loss resulted in an overflow of the west wetwell to the emergency outfall from 9:42 PM to 9: 48 PM. An estimated volume of 86,000 gallons overflowed to the Intracoastal Waterway. | 09/10/2017 09:43 AM | FLA041378 - George T. Lohmeyer Regional Wastewater Treatment | 1765 SE 18 Street; Fort Lauderdale FL; 33309 |  | Lawrence Teich | Environmental Resource Supervisor | lteich@fortlauderdale.gov | (954) 828-7844 |  | Environmental and Regulatory Affairs | Lawrence Teich | (954) 828-7844 |  | lteich@fortlauderdale.gov | 09/09/2017 09:40 PM | 09/09/2017 09:45 PM | Broward |  |  | 26.099126 | -80.124984 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=336
12735 Gran Bay Parkway | 20176939 | ARV failed and released at least 1000 gallons of wastewater onto the road and into a stormwater drain. Replaced ARV and washed down area. Recovered sewer and wash water from roadway. | 09/09/2017 02:40 PM | JEA Municipal Sewer System | 12735 Gran Bay Parkway; Jacksonville FL; 32258 |  | Jason Hermening | Environmental Scientist Senior | hermjs@jea.com | (904) 376-5164 |  | JEA Environmental Response | Jason Hermening | (904) 376-5164 |  | hermjs@jea.com | 09/09/2017 10:55 AM | 09/09/2017 01:30 PM | Duval |  |  | 30.140664 | -81.527647 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=335
1555 Millcoe Roa | 20176898 | PLC failure caused wastewater to overflow prior to bar screens at wastewater facility. An estimated 363,500 gallons released on-site. Washed down and recovered released wastewater. | 09/08/2017 05:13 PM | Arlington East WRF | 1555 Millcoe Road; Jacksonville FL; 32225 |  | Jason Hermening | Environmental Scientist Senior | hermjs@jea.com | (904) 376-5164 |  | JEA Environmental Response | Jason Hermening | (904) 376-5164 |  | hermjs@jea.com | 09/08/2017 03:00 PM | 09/08/2017 03:30 PM | Duval |  |  | 30.347884 | -81.543419 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=334
Diesel cleanup | 2017689 | Type of product ¿ Diesel fuel Number of gallons approximately 6-8 gallons Cause of the release ¿ Faulty relay switch to the recirculation pump of the day tank, allowed the day tank to over flow. The faulty relay, anti-syphoning valve was replaced. Responsible Party¿s name, Siemens Energy Inc. address, Quad2- 11950 CORPORATE BOULEVARD, ORLANDO, FL 32826 -phone number if available, PS EHS Officer, Gary Garippo, 1-407-353-6490 Number/type of injuries or fatalities if applicable ¿ NA Name of affected waterway if available ¿ NA What clean-up efforts have been performed if any ¿ The initial Spill response stopped and contained the release. Pigs and absorbent pads were used to address the overflow. Excavation and offsite disposal of approximately 1.75 CY of impacted soil was performed. OVA samples of the excavation were taken along with an analytical sample of side wall that was sent to the lab for analysis. The excavation was backfilled with clean fill. Any fires, explosions, evacuations or road/waterway closures ¿NA Agencies responding ¿ NA Critical Infrastructure/Key Recourse NA | 09/08/2017 12:05 PM | Siemens Energy Inc. | 11950 CORPORATE BOULEVARD; orlando FL; 32826 |  | Brad Hoffmann | PS EHS Facilities | Bradford.hoffmann@siemens.com | (407) 736-2064 |  | EHS | Brad Hoffmann | (407) 736-2064 |  | Bradford.hoffmann@siemens.com | 08/30/2017 01:40 PM | 09/08/2017 09:00 AM | Seminole |  |  | 28.60711 | -81.212492 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=333
Diesel cleanup | 2017689 | Type of product ¿ Diesel fuel Number of gallons approximately 6-8 gallons Cause of the release ¿ Faulty relay switch to the recirculation pump of the day tank, allowed the day tank to over flow. The faulty relay, anti-syphoning valve was replaced. Responsible Party¿s name, Siemens Energy Inc. address, Quad2- 11950 CORPORATE BOULEVARD, ORLANDO, FL 32826 -phone number if available, PS EHS Officer, Gary Garippo, 1-407-353-6490 Number/type of injuries or fatalities if applicable ¿ NA Name of affected waterway if available ¿ NA What clean-up efforts have been performed if any ¿ The initial Spill response stopped and contained the release. Pigs and absorbent pads were used to address the overflow. Excavation and offsite disposal of approximately 1.75 CY of impacted soil was performed. OVA samples of the excavation were taken along with an analytical sample of side wall that was sent to the lab for analysis. The excavation was backfilled with clean fill. Any fires, explosions, evacuations or road/waterway closures ¿NA Agencies responding ¿ NA Critical Infrastructure/Key Recourse NA | 09/08/2017 12:05 PM | Siemens Energy Inc. | 11950 CORPORATE BOULEVARD; orlando FL; 32826 |  | Brad Hoffmann | PS EHS Facilities | Bradford.hoffmann@siemens.com | (407) 736-2064 |  | EHS | Brad Hoffmann | (407) 736-2064 |  | Bradford.hoffmann@siemens.com | 08/30/2017 01:40 PM | 09/08/2017 09:00 AM | Seminole |  |  | 28.60711 | -81.212492 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=332
Diesel cleanup | 2017689 | Type of product ¿ Diesel fuel Number of gallons approximately 6-8 gallons Cause of the release ¿ Faulty relay switch to the recirculation pump of the day tank, allowed the day tank to over flow. The faulty relay, anti-syphoning valve was replaced. Responsible Party¿s name, Siemens Energy Inc. address, Quad2- 11950 CORPORATE BOULEVARD, ORLANDO, FL 32826 -phone number if available, PS EHS Officer, Gary Garippo, 1-407-353-6490 Number/type of injuries or fatalities if applicable ¿ NA Name of affected waterway if available ¿ NA What clean-up efforts have been performed if any ¿ The initial Spill response stopped and contained the release. Pigs and absorbent pads were used to address the overflow. Excavation and offsite disposal of approximately 1.75 CY of impacted soil was performed. OVA samples of the excavation were taken along with an analytical sample of side wall that was sent to the lab for analysis. The excavation was backfilled with clean fill. Any fires, explosions, evacuations or road/waterway closures ¿NA Agencies responding ¿ NA Critical Infrastructure/Key Recourse NA | 09/08/2017 12:05 PM | Siemens Energy Inc. | 11950 CORPORATE BOULEVARD; orlando FL; 32826 |  | Brad Hoffmann | PS EHS Facilities | Bradford.hoffmann@siemens.com | (407) 736-2064 |  | EHS | Brad Hoffmann | (407) 736-2064 |  | Bradford.hoffmann@siemens.com | 08/30/2017 01:40 PM | 09/08/2017 09:00 AM | Seminole |  |  | 28.60711 | -81.212492 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=331
Controlled Release of Treated Industrial Wastewater | 20176890 | On Thursday, September 7, 2017 at approximately 11:15 a.m. Duke Energy initiated a controlled release of treated industrial wastewater from its permitted percolation ponds at the Crystal River Energy Complex. This action was taken to minimize risk of compromising pond integrity caused by water levels exceeding the minimum three (3) feet of freeboard that could occur as a result of precipitation and winds from Hurricane Irma over the next several days. The water is being discharged into the station¿s intake canal via portable pumps. The flow of water is being measured, and daily water quality samples are being collected and analyzed for permitted parameters. As of September 8, 2017 at 8:30 am, approximately 6.2 million gallons have been discharged. The controlled release will cease when pond levels return to normal operating levels (expected around Saturday afternoon depending on weather conditions), or when the path of the hurricane is confirmed to no longer pose a threat, whichever occurs first. The Florida Department of Environmental Protection was notified of this plan on September 6, 2017, as part of Duke's hurricane preparation activities, and the company will keep the agency informed on progress. 9/10/17 Update: With Hurricane Irma's path forecasted close to the facility, Duke Energy has continued to pump the treated industrial wastewater from the percolation ponds into the intake canal to assure additional capacity for expected rainfall amounts and maintain integrity of the percolation pond berms. As of 10:30 am on 9/10/17, an estimated 21 million gallons have been discharged. Samples have been collected daily as weather conditions permit. Discharge will be discontinued once storm conditions in the area have passed and it is safe to turn off the pumps. 9/10/17 5:25 pm update: The pumps were turned off on 9/10/17 at 3:50 pm and removed. An estimated total of 22.7 million gallons of treated wastewater were discharged to the intake canal. | 09/08/2017 09:45 AM | Duke Energy Crystal River Energy Complex | 15760 Power Line Street; Crystal River FL; 34428 |  | Ilia Balcom | Senior Environmental Specialist | Ilia.Balcom@duke-energy.com | (813) 362-5123 |  | Environmental Permitting Support | Ana Gibbs | (813) 926-7263 |  | Ana.Gibbs@duke-energy.com | 09/07/2017 11:15 AM | 09/10/2017 03:50 PM | Citrus | Citrus | Y | 28.956252 | -82.708614 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=330
Lift Station #231; 8400 W. Campbell Rd in Lakeland | 20176873 | Approximately 1,500 gallons of domestic wastewater discharged on the ground and flowed into a near-by wet retention pond. Further investigation indicates that a temporary control panel installed by a contractor caused a failure of the pumps. Clean-up action was immediately initiated and completed at 8:45 AM on September 7, 2017. The affected area was vacuumed and treated with lime disinfectant. Approximately 250 gallons was recovered and disposed in accordance with regulatory requirements. The pumps have been replaced and a phase monitor has also been installed to prevent a recurrence. Signs have been posted around the pond as a precaution and sampling will be done in the next few days. State Watch Office was contacted at 4:09 PM on September 7, 2017 as a precaution and the incident number is #2017-6873. | 09/07/2017 04:28 PM | Northwest Regional WWTF; FLA 178667 | 8950 N. Campbell Rd ; Lakeland FL; 33810 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 09/07/2017 07:30 AM | 09/07/2017 08:45 AM | Polk |  |  | 28.151752 | -82.002837 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=329
City of Orlando |  | At approximately 840 AM, City of Orlando Water Reclamation Division received notification that a sanitary sewer service lateral at 4283 Pappy Kennedy Blvd experienced a structural failure within the Right of Way. Approximately 100 gallons of sanitary sewer overflowed out of the broken clean-out and began to run into the street as well as a storm drain leading to a canal that drains into Lake Fran. The City of Orlando Water Reclamation Division dispatched a Hi-Vac and the Stopped Sewer crew onsite to repair the service lateral. All impacted surfaces were sanitized and 20 gallons of sanitary sewer were vactored from the impacted storm drains and returned to the collection system. | 09/07/2017 01:52 PM | City of Orlando limits | 4283 Pappy Kennedy Blvd; Orlando FL; 32811 | Pappy Kennedy Blvd/Aaron Ave. | Daron Johnson | SEM Manager | daron.johnson@cityoforlando.net | (407) 246-2273 |  | SEM Manager | Daron Johnson | (407) 246-2273 |  | daron.johnson@cityoforlando.net | 09/07/2017 08:40 AM | 09/07/2017 09:00 AM | Orange |  |  | 28.524322 | -81.431806 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=328
Reserve of Minneola | 176861 | A contractor's construction line plug blocked a gravity sewer line. The spill was reported at 8:00 PM Sept 6, 2017 at the intersection of Oxbow Rd. and Redbay Ave. The line was cleared by 8:30 PM with a total gallons of spillage of less than 200 gallons. Road and gutter washed down to on-site retention area and hydrated lime applied. Spill did not contaminate any state waters, recreational areas or wetlands. Wastewater collection system is permitted under FLA356344. | 09/07/2017 07:39 AM | City of Minneola WWRF | 18340 Scrub Jay Lane; P.O. Box 678; Minneola FL; 34755 |  | Robert Holland | Chief Plant Operator | rholland@minneola.us | (352) 242-1301 |  | Operator Of the Facility | Robert Holland | (352) 536-4162 |  | rholland@minneola.us | 09/06/2017 08:00 PM | 09/06/2017 08:30 PM | Lake |  |  | 28.592038 | -81.718875 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=327
Wastewater spill at 135 King Street, Cocoa | 20176781 | On September 2, 2017 at 9:55 pm, the Cocoa Utilities Department received a call about sewer bubbling up out of the ground at 135 W. King St. The stand-by person responded and found sewage bubbling up at an air relief valve manhole and called in a crew to fix the problem. The crew found a two-inch nipple on air relief valve failed causing sewage to leak out of the manhole into a retention area. The line was shut off east and west of the leak which stopped the sewage from leaking so repairs could be made. Cocoa Utilities Dept. estimates that 4,500 gallons of raw sewage spilled. It was contained in the retention area. The wastewater was contained in the storm retention area by damming off the spilled sewage. The Wastewater Collection crew cleaned up the area with the Vac-Con truck and Pine Oil Disinfectant was put at the affected area. The crew removed about 4,000 gallons with the Vac truck from the area. The Florida Warning Point was notified on 9/3/2017 at 9:50 am to report the spill. It was reported to Department Of Environmental Protection's David Smicherko on 9/5/2017 at 9:00 am. | 09/06/2017 05:31 PM | 135 W. King St., Cocoa | 135 W. King St.; Cocoa FL; 32922 |  | Donald W. Downs | Conservation/Public Relations Officer | ddowns@cocoafl.org | (321) 433-8705 |  | Conservation/Public Relations Officer | Donald W. Downs | (321) 433-8705 |  | ddowns@cocoafl.org | 09/02/2017 09:55 PM | 09/02/2017 10:30 PM | Brevard |  |  | 28.355851 | -80.725699 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=326
Summerline road | 6849 | Received a call at 9/6/17 at 7am about a SSO At 19111 Summerline road. We responded and found it was a 20 inch sewer pipe failed. We took steps to shut down the system and repairs completed by 2PM. | 09/06/2017 04:50 PM | FLA144215 Lee County Utilities Ft. Myers Beach WWTP | FL |  | Rich Sims | Manager | rsims@leegov.com | (239) 533-8721 |  | Employee | Rich Sims | (239) 533-8721 |  | rsims@leegov.com | 09/06/2017 07:00 AM | 09/06/2017 02:00 PM | Lee |  | N | 26.493215 | -81.959115 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=325
Hydraulic oil spill / Water Conservation Area 2 | 20176842 | Temporary pumps for flood control installed on L-39 Levee. Pin hole in hydraulic hose caused sheen to water body. Discovered discharge at ~3:00 am. Pump was secured. Absorbent booms were deployed. Hose was replaced. Location of pumps: Lat: 26.21.22 / Long: 80.18.00 (western terminus of Lox Road). | 09/06/2017 11:53 AM | South Florida Water Management District | 3301 Gun Club Road; West Palm Beach FL; 33406 | Location of pumps: Northeast corner of Water Conservation Area 2. Lat: 26.21.22 / Long: 80.18.00 (western terminus of Loxahatchee Road). | Jeffrey Smith | Lead Environmental Scientist | jesmith@sfwmd.gov | (561) 682-2516 |  | Owner Of the Facility | Jeffrey Smith | (561) 682-2516 |  | jesmith@sfwmd.gov | 09/06/2017 03:00 AM | 09/06/2017 03:15 AM | Palm Beach |  |  | 26.356117 | -80.300069 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=324
South Beaches AR Valve | 20176839 | Malfunctioning AR valve leaked at the corner of South Patrick Drive and Anchor Drive in Indian Harbor Beach. Discovered at 2pm. AR Valve was replaced and flow stopped by 5pm. 1,000 gallons leaked and some went to swale that leads to nearby canal but it does not look like the flow made it to the canal. Signs were posted at the canal just in case. The area was washed down. | 09/06/2017 10:07 AM | South Beaches WWTF | 2800 South A1A ; Melbourne Beach FL; 32951 |  | Shelley Locklear | Environmental Specialist | shelley.locklear@brevardfl.gov | (321) 633-2093 |  | Owner Of the Facility | Shelley Locklear | (321) 633-2093 |  | shelley.locklear@brevardfl.gov | 09/05/2017 02:00 PM | 09/05/2017 05:00 PM | Brevard |  |  | 28.157589 | -80.602157 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=323
Forcemain Break | 20176821 | Cause of Incident: Contractor hit an ARV on an 8¿ sanitary sewer force main causing a 1.5¿ hole in pipe. Location of Incident (directions) Woodfield Country Club ¿ Just west of intersection of Woodfield Circle and NW 55th Diagonal Estimated amount of spillage: 4,500 gallons Estimated affected area: Swale area near break and storm drain east of break. Corrective Action: Lift Stations were immediately shut down and isolated break by valves. Made repair to pipe with plug on saddle. Bodies of water effected: Storm water pond by break Storm Drains effected: Yes ¿ catch basin east of the break Signs/Notification and Actions: Signs posted by storm water pond ¿ door hangers on properties backing up to pond Clean Up: Attempting to vactor ~ 9,000 gallons from storm drain. Disinfected With: Lime/HTH Back to Normal: Yes Date: 9/5/2017 Time: 14:30hrs. Comments: FL0026344 SWP #2017-6821 | 09/05/2017 04:27 PM | City of Boca Raton Force Main | NW 56th and NW 55th Diagonal; Boca Raton FL; 33431 | Just east of Woodfield Circle and NW 55th Diagonal in Woodfield Country Club | Lisa M. Wilson-Davis | Operations & Environmental Compliance Manager | lwilsondavis@myboca.us | (561) 338-7310 |  | Owner Of the Facility | Lisa M. Wilson-Davis | (561) 338-7310 |  | lwilsondavis@myboca.us | 09/05/2017 12:00 PM | 09/05/2017 02:30 PM | Palm Beach |  |  | 26.398868 | -80.159604 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=322
801 Bryan Place SSO Q234230 | 20176819 | 9/5/2017, a neighbor reported an overflowing manholes at 700 and 801 Bryan Place at 8:15 AM. Approximately 6,750 gallons of untreated sanitary sewage overflowed a manhole and entered a storm drain that discharges into the New River. Sewer Crews were able to pump out the sewer system to stop the overflow at 10:30 AM. Vacuum and tankers trucks are working 24/7 to keep the system pumped down. | 09/05/2017 03:11 PM | GTL Regional Wastewater Facility | FL |  | Lawrence Teich | Environmental Resources Supervisor | lteich@fortlauderdale.gov | (954) 828-7844 |  | Representative | Lawrence Teich | (954) 828-7844 |  | lteich@fortlauderdale.gov | 09/05/2017 08:15 AM | 09/05/2017 10:30 AM | Broward |  |  | 26.116586 | -80.151487 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=321
Test |  | Test | 09/05/2017 02:43 PM | Test | Test; Test FL | Test | Test | Test | Test@gmail.com | (407) 407-4077 |  | Test | Test | (407) 407-4077 |  | Test@gmail.com | 09/05/2017 02:40 PM | 09/05/2017 02:40 PM | Seminole |  |  | 28.694538 | -81.313525 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=320
City of Webster Lift station over flow | 20176820 | The City of Webster had a lift station electrical failure which led to a spill of 2,500 gallons. It was contained on sight and lime was spread over effected area. | 09/05/2017 01:44 PM | Lift station #10 | 447 NW 6th Ave ; webster FL; 33597 |  | Michael Edwards | Public Works Director City of Webster | medwards@websterfl.com | (352) 254-0850 |  | Public Works Supervisor City of Webster | Michael Edwards | (352) 254-0850 |  | medwards@websterfl.com | 09/04/2017 12:00 PM | 09/04/2017 12:30 PM | Sumter |  |  | 28.616087 | -82.062072 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=319
Force main break | 20176764 | Date/Time reported: 9/2/17 @ 2:30pm Description: Force main break Incident Date/Time: 9/2/17 @ 7:00am Incident Location: 122 N. Marie Drive County: Bay (3) District: NW District Caller Name: Angie Stokes Affiliation: Utilities Administrative Asst. Permitted Utility?: Yes Permitted Utility Name: City of Panama City Permitted Utility ID: 0170909 (Millville) Facility Type: Domestic Wastewater Wastewater Characteristics: Untreated Cause: Force main break Initial Spill Volume: 10,000 gallons Volume Recovered: 0 Final Spill Volume: 10,000 gallons Water Body Affected: Watson Bayou Clean-up Actions: Wash down street Clean-up Actions Status: Completed | 09/05/2017 11:14 AM | Force main break | 122 N. Marie Drive; Panama City FL; 32401 | at the intersection of Tyndall Drive and Marie Drive | Angie Stokes | Administrative Assistant | astokes@pcgov.org | (850) 872-3164 |  | Operator Of the Facility | Chris Lightfoot | (850) 872-3164 |  | clightfoot@pcgov.org | 09/02/2017 07:00 AM | 09/02/2017 03:00 PM | Bay |  |  | 30.148474 | -85.639211 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=318
cooking oil | 1189292 | Incident Report # 1189292 INCIDENT DESCRIPTION *Report taken at 09:46 on 04-SEP-17 Incident Type: FIXED Incident Cause: UNKNOWN Affected Area: STORM DRAIN Incident was discovered on 04-SEP-17 at 09:30 local incident time. Affected Medium: WATER / STORM DRAIN | 09/05/2017 09:09 AM | Shell Point retirement community | 14701 kings Crown way suite 100 ; fort myers FL; 33908 |  | Mindy Zmuda | Office Coordinator | mindyzmuda@shellpoint.org | (239) 454-2190 | 2131 | office Coordinator | Tony Arias | (239) 433-7902 |  | tonyarias@shellpoint.org | 09/04/2017 09:30 AM | 09/04/2017 12:00 PM | Lee |  |  | 26.516791 | -81.99658 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=317
3858 Roan Court E |  | On September 2, 2017 a force main break occurred at 8 PM on an existing asbestos cement force main currently in the process of being replaced. Approximately 300 gallons of sewage was discharged. One (1) storm drain was effected. Notified customers in the immediate area. Utilized vac-trucks to remove spilled sewage and pumped out storm basin. Approximately 2 gallons of 1,000 part per million chlorine solution was used to disinfect the area. | 09/05/2017 09:07 AM | Roan Lane 8-inch Force Main | 3858 Roan Court East; West Palm Beach FL; 33403 |  | Brent Weidenhamer, PE | Wastewater Department Manager | bweidenhamer@sua.com | (561) 627-2900 | 494 | Wastewater Department Manager | Brent Weidenhamer, PE | (561) 627-2900 |  | bweidenhamer@sua.com | 09/02/2017 08:00 PM | 09/03/2017 02:00 AM | Palm Beach |  |  | 26.816307 | -80.0958 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=316
1145 Court St. |  | Overflow did not exceed 1,000 gallons. State watch was not notified. | 09/05/2017 08:38 AM | Marshall Street Plant | 1641 Harbor Dr.; Clearwater FL; 33765 |  | Andrew Blauvelt | Public Utilities Supervisor I | andrew.blauvelt@myclearwater.com | (727) 562-4960 | 7216 | Operator Of the Facility | Andrew Blauvelt | (727) 562-4960 |  | andrew.blauvelt@myclearwater.com | 09/01/2017 04:25 PM | 09/01/2017 04:25 PM | Pinellas |  |  | 27.960741 | -82.789664 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=315
City Of Orlando |  | Contractors Bauer hose fitting from bypass pump was driven over by vehicle on South Parramore Ave. Fitting disconnected from the force of the vehicle. Standby crews responded reattached the clamp, recovered 800 gallons on sanitary sewer with Hi-Vac, disinfected impacted soil with Simple Green. No storm drains impacted by SSO. | 09/04/2017 01:32 PM | Conserv II | 5420 L.B.McLeod Road FL |  | Daron Johnson | SEM Manager | daron.johnson@cityoforlando.net | (407) 246-2273 |  | Manger of Collection System | Daron Johnson | (407) 246-2273 |  | daron.johnson@cityoforlando.net | 09/04/2017 09:30 AM | 09/04/2017 10:15 AM | Orange |  |  | 28.52931 | -81.388826 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=314
IQ/ Reclaimed water/ Reuse spill of IQ 530 | 20176784 | Cause of spill was isolation valve was left open and when went to start daily Reuse feed to customer, most of water was not going to customer; 195,000 gallons reported; no clean up required other than close isolation valve-clean up sidewalk of sand build up-barricade/tape off sinkhole from spill area; State Warning Officer inquired of any road erosion/ under mining; answer - no. | 09/03/2017 11:20 AM | Loxahatcee River District | 2500 Jupiter Park Drive; Jupiter FL; 33458 |  | kevin skellenger | field superintendent | kevin.skellenger@lrecd.org | (561) 747-5709 | 130 | field superintendent | Albrey Arrington | (561) 747-5700 |  | albrey@lrced.org | 09/02/2017 01:05 PM | 09/02/2017 01:15 PM | Palm Beach |  |  | 26.935269 | -80.16118 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=313
wastewater spill of lift station 157 | 20176783 | sanitary spill of 500 gallons from gravity system manhole; spill went into retention pond; address given is 820 Jupiter Park Drive; cause of failure was pump station failure; clean up is complete and signage posted for No swimming- no fishing till water sampling results are complete. | 09/03/2017 10:50 AM | Loxahatchee River District | 2500 jupiter park drive; Jupiter FL; 33458 |  | kevin skellenger | Field Superintendent | kevin.skellenger@lrecd.org | (561) 747-5709 | 130 | field superintendent | Albrey Arrington | (561) 747-5700 |  | albrey@lrecd.org | 09/02/2017 12:00 PM | 09/02/2017 01:30 PM | Palm Beach |  |  | 26.926634 | -80.143679 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=312
City of Hollywood 10" Force Main Break | 20176758 | A wastewater force main broke, due to pipe failure. On Saturday, September 2, 2017, at approximately 8:30 AM, the City of Hollywood Dept. Public Utilities was informed of a wastewater discharge near 1201 N 70 Avenue 33024, a force main break was verified. The pipe break was an 10-inch asbestos cement pipe. From the time of notification up until approximately 11:15 AM several Lift Stations were shut off to make the repair. The pipe was repaired and surrounding area were restored around 8:45 PM of the same day 9/2/17. The spill did enter the roadway and public access areas, however there was no discharge to stormdrains. The affected areas are being cleaned up with HTH and vacuum trucks. The discharge amount for the sewage spill is being calculated but is estimated to be +4,000 gallons. The COH will update this report once a true estimate of the spill amount is complete. | 09/03/2017 12:20 AM | City of Hollywood SRWWTP collection system | 1201 N 70 Avenue ; Hollywood FL; 33024 |  | Kassandra Myers | Water Quality Manager | kmyers@hollywoodfl.org | (954) 812-4426 |  | Compliance Manager | Francois Domond | (954) 921-3048 |  | FDOMOND@hollywoodfl.org | 09/02/2017 08:30 AM | 09/02/2017 08:45 PM | Broward |  |  | 26.019995 | -80.228317 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=311
10016 Moon Lake Road Spill | 20176765 | PVC backcheck valve broke, causing a large leak. Wet well overflowed to adjacent wooded area. Station was isolated from force main via isolation valve. Broken valve was capped and station returned to service. Replacement valve will be installed later. | 09/02/2017 07:26 PM | Shady Hills Wastewater Treatment Faclity | 14220 Hays Road; Spring Hill FL; 34610 | Permit # FLA012741 | Jams Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Environmental Compliance Specialist | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 09/02/2017 01:00 PM | 09/02/2017 02:20 PM | Pasco |  |  | 28.30305 | -82.617502 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=310
Trucious/Glissade--Beacon Square Spill | 20176752 | Excessive rains and infiltration caused pump station 6-27 to spill. Sludge trucks and vactor were dispatched to site to retreive liquids until station satisfied. FDEP and SWP notified. Volume is undetermined but not to exceed 3000 gallons | 09/02/2017 07:59 AM | New Port Richey Wastewater Treatment Facility | 4730 Main Street; New Port Richey FL; 34654 | Permit # FLA127434 | James Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Environmental Compliance Specialist | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 09/01/2017 09:35 PM | 09/01/2017 11:00 PM | Pasco |  |  | 28.219906 | -82.742447 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=309
700 Bryan Place SSO Q233260 | 20176375 | 9/1/2017, a neighbor reported an overflowing manhole at 700 Bryan Place at 8:12 AM. Approximately 864 gallons of untreated sanitary sewage overflowed and entered a manhole that discharges into the North Fork New River. Sewer Crews were able to pump out the sewer system to stop the overflow at 3:00 PM. Vactor and tankers trucks are working 24/7 to keep system pumped down. | 09/01/2017 03:27 PM | GTL Regional Wastewater Facility | FL; 33309 |  | Troy Balint | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 09/01/2017 08:10 AM | 09/01/2017 03:00 PM | Broward |  |  | 26.116385 | -80.150391 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=308
Fiesta Village WWTP Sodium Hypochlorite discharge | 20176716 | Approximately 320 gallons of 12% Sodium Hypochlorite discharged from a storage tank system under repair. Discharge confined to area surrounding the concrete tank pad. Source removal of impacted area will be completed. | 09/01/2017 12:40 PM | Fiesta Village Advanced Wastewater Treatment Plant | 1366 San Souci Drive; Fort Myers FL; 33919 |  | Eugene McCartney | Acting Lead Operator | emccartney@leegov.com | (239) 481-1953 |  | Operator Of the Facility | Eugene McCartney | (239) 481-1953 |  | emccartney@leegov.com | 08/31/2017 10:00 PM | 09/01/2017 07:00 AM | Lee |  | N | 26.543333 | -81.904167 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=307
Sanitary Sewer Overflow | 20176688 | Sewer Spill of 1730 gallons from tropical storm Harvy | 09/01/2017 08:49 AM | CWRF | 2980 Old Chemstrand Rd ; Pensacola FL; 32533 |  | Catherine Matthews | Communications Coordinator II | scada.operations@ecua.fl.gov | (850) 969-6500 | 6500 | Operator Of the Facility | Doug Gibson | (850) 969-6513 |  | Douglas.Gibson@ecua.fl.gov | 08/31/2017 07:45 AM | 08/31/2017 09:00 AM | Escambia |  | N | 30.426538 | -87.276785 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=306
Sanitary Sewer Overflow | 20176711 | Pump station control panel malfunction. 1200 gallons spilled. Vactored up all standing water in ditch and limed affected area. Recovered 1100 gallons (100 gallons estimated seeped into ground). No surface water affected. | 08/31/2017 07:25 PM | Pump Station 55 | 204 Spartina Ave.; St. Augustine FL; 32084 |  | Glabra Skipp | Environmental Compliance Analyst | gskipp@citystaug.com | (904) 825-1055 |  | Environmental Compliance Analyst | Glabra Skipp | (904) 825-1055 |  | gskipp@citystaug.com | 08/31/2017 05:15 AM | 08/31/2017 07:05 AM | St. Johns |  |  | 29.877095 | -81.297684 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=305
810 Lake Shore Drive |  | August 31, 2017 from approximately 7:40 to 8:30 600 gallons of sewer overflowed from manhole due to grease build-up. One (1) storm drain adjacent to the spill was effected. Notified customers in the immediate area. Utilized vac-trucks to remove spilled sewage and pumped out storm basin. Approximately 4 gallons of 1,000 part per million chlorine solution was used to disinfect the area. | 08/31/2017 02:30 PM | Manhole overflow | 810 Lake Shore Drive; Lake Park FL; 33403 |  | Brent Weidenhamer | Wastewater Department Manager | bweidenhamer@sua.com | (561) 262-6341 |  | Manager | Brent Weidenhamer | (561) 627-2900 |  | bweidenhamer@sua.com | 08/31/2017 07:40 AM | 08/31/2017 08:30 AM | Palm Beach |  |  | 26.800077 | -80.052141 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=304
Trucious/Glissade--Beacon Square | 20176656 | Excessive rains and infiltration caused pump station 6-27 to spill. Sludge trucks and vactor were dispatched to site to retreive liquids until station satisfied. 20lbs lime spread to affected area.dep and swp contacte. Volume is undetermined but not to exceed 5000 gallons | 08/31/2017 02:07 PM | New Port Richey Wastewater Treatment Facility | 4730 Main Street; New Port Richey FL; 34654 | Permit # FLA127434 | James Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Environmental Compliance Specialist | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 08/29/2017 04:00 PM | 08/29/2017 04:30 PM | Pasco |  |  | 28.220011 | -82.741762 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=303
Arcadia/Mile stretch Road | 20176655 | Excessive rains and infiltration into sewer system caused pump station to overflow. Amount of spill is undetermined. Sludge trucks and vactors were dispatched to assist retreiving iquids from station until satisfied. 20lbs of lime spread to area. Due to heavy rains no sewage was retreived from site. No waterways were affected by spill. Email to FDEP and SWP contacted was completed. | 08/31/2017 01:35 PM | New Port Richey Wastewater Treatment Facility | 4730 Main Street; New Port Richey FL; 34654 | Permit # FLA127434 | James Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Environmental Compliance Specialist | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 08/29/2017 03:30 PM | 08/29/2017 04:00 PM | Pasco |  |  | 28.188067 | -82.731766 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=302
C.O.B. Reclaimed Water Tank Overflow. | 20176703 | Storms in area disabled equipment and telemetry monitoring storage tank level. 275,000 gallons overflowed tank into onsite storm drain system. | 08/31/2017 12:29 PM | City of Bradenton W.W.T.P. | 1810 First St. W.; Bradenton FL; 34208 | US-41 and 17th Ave. W. | William J. Quigley | Superintendent | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/29/2017 08:30 AM | 08/29/2017 10:30 AM | Manatee |  |  | 27.480101 | -82.526362 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=301
SW 2 Street between SW 8 Ave & SW 9 Ave | 20176694 | - The 30¿ force main has been isolated. - Clean up crews are being dispatched. - 23,730 gallons was reported released - Samples have been collected from the New River - State Watch office SWO# 2017-6694, FDEP Local, and Broward County were notified by 10.31, 10:15, and 10:40 respectively | 08/31/2017 11:53 AM | George T. Lohmeyer | SW 2nd Street; Fort Lauderdale FL; 33309 |  | Lawrence Teich | Environmental Resource Supervisor | lteich@fortlauderdale.gov | (954) 828-7844 |  | City Environmental Resource Supervisor | Lawrence Teich | (954) 828-7844 |  | lteich@fortlauderdale.gov | 08/31/2017 08:00 AM |  | Broward |  | N | 26.120315 | -80.152451 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=300
Air Relief Valve leak | 20176680 | Sewage spill which was due to a leak from an air relief valve in the vicinity of 2421 SW 41 Avenue in the city of Fort Lauderdale. The section of the main that was leaking has been repaired and the flow was stopped completely at 8:36 p.m. The area has been cleaned up by utility crews. | 08/31/2017 11:21 AM | Broward County NRWWTP (ID # FL0031771) | 22421 SW 41 AVE; Fort Lauderdale FL; 33317 |  | Mike Kelly | Utilities Superintendent | mkelly@broward.org | (954) 831-0821 |  | Operator Of the Facility | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 08/30/2017 03:05 PM | 08/30/2017 08:35 PM | Broward |  | N | 26.0917 | -80.202734 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=299
8/29/2017/ SSO NI FL/HUD DEMLAR LS | 20176649 | Technicians were called out to Delmar PS by the SCADA system. Upon arrival, the technicians found that electrical components in the pump station had been damaged by lightning or electrical surge. During period of malfunction, all contributing lift stations were manually controlled to avoid further SSO. On 8/28/2017, starters were found damaged and were repaired and on 8/29/2017, breakers and main breakers and controls were found damaged upon arrival. All electrical components were replaced. Damaged electrical components were replaced and repaired to restore normal operations.. Pumper trucks were brought in to clean up the release. Release did enter the drainage ditch and mixed with rain water, but the entire drainage ditch was cleaned with pumper trucks and disinfected with lime. | 08/31/2017 10:27 AM | DELMAR PS (NI FLORIDA: HUDSON COLLECTION SYSTEM | SE CORNER OF THE INTERSECTION OF SEA RANCH DR AND; DELMAR DR; HUDSON FL; 34667 |  | COREY WITTENZELLNER | MANAGER | COREY.W@UG-FL.COM | (813) 267-8352 |  | Operator Of the Facility | COREY WITTENZELLNER | (813) 267-8352 |  | COREY.W@UG-FL.COM | 08/29/2017 03:00 PM | 08/29/2017 04:00 PM | Pasco |  |  | 28.356893 | -82.700415 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=298
8/28/2017 SSO NI FL/HUD DELMAR LS | 20176649 | Technicians were called out to Delmar PS by the SCADA system. Upon arrival, the technicians found that electrical components in the pump station had been damaged by lightning or electrical surge. During period of malfunction, all contributing lift stations were manually controlled to avoid further SSO. On 8/28/2017, starters were found damaged and were repaired and on 8/29/2017, breakers and main breakers and controls were found damaged upon arrival. All electrical components were replaced. Damaged electrical components were replaced and repaired to restore normal operations.. Pumper trucks were brought in to clean up the release. Release did enter the drainage ditch and mixed with rain water, but the entire drainage ditch was cleaned with pumper trucks and disinfected with lime. | 08/31/2017 10:22 AM | DELMAR PS (NI FLORIDA: HUDSON COLLECTION SYSTEM | SE CORNER OF THE INTERSECTION OF SEA RANCH DR AND; DELMAR DR; HUDSON FL; 34667 |  | COREY WITTENZELLNER | MANAGER | COREY.W@UG-FL.COM | (813) 267-8352 |  | Operator Of the Facility | COREY WITTENZELLNER | (813) 267-8352 |  | COREY.W@UG-FL.COM | 08/28/2017 01:30 PM | 08/28/2017 02:00 PM | Pasco |  |  | 28.35694 | -82.70063 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=297
SSO Manhole overflows NW 15th Terr 4th-5th Streets | 20176690 | An overflow from several manholes in the area spilled onto the streets and swale areas. Stormdrains were impacted in a couple of areas. The total volume that spilled was calculated to be 875 gallons. 700 gallons were recovered by use of Vactor trucks. The remaining volume entered the storm drain system that has an outfall at the New River. Overflow caused in part to a collapsed gravity main. | 08/31/2017 09:51 AM | GTL Regional Wastewater Facility | FL; 33309 |  | T | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/30/2017 10:30 PM | 08/31/2017 02:30 AM | Broward |  |  | 26.126312 | -80.162596 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=296
Q232709 728 NW 4th Ave | 20176679 | 6" sanitary sewer clean-out overflowed approximately 675 gallons onto a swale area and into the road entering a storm drain that discharges into the New River. The crew was able to recover approximately 400 gallons of the spill volume. The spilled was stopped at 7:00pm and the area cleaned up. | 08/30/2017 10:16 PM | GTL Regional Wastewater Facility | FL; 33334 |  | Troy Balint | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/30/2017 04:45 PM | 08/30/2017 07:00 PM | Broward |  |  | 26.131993 | -80.14785 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=295
Broad St. @ the entrance to Carpenters Park | 20176671 | Two sewage spills occurred on August 30, 2017, at approximately 2:00 p.m. The estimated spillage was approximately 500 gallons at each site. They occurred at Willing St. at North Riverwalk and Broad St. at the entrance to Carpenters Park, Milton, FL, 32570. The responsible permittee, City of Milton Water & Sewer Department; WWT Facility Permit #FL0021903, 5438 Alabama Street, Milton, Fl. 32570; Phone (850) 983-5434, Fax: (850) 983-5439, has attempted to contact all appropriate entities. Please note below. The discharge has ceased and, by-pass pumping was not used. The spillage was from a manhole caused by excessive rainfall. The untreated domestic spillage was not contained, and did enter the Blackwater River. The Water/ Sewer Department disinfected the area of the spill by applying chlorine bleach and Ban-O. Water samples will be collected and the results will be faxed over to Dana Vestal with FL. D.E.P. @ 850-595-8097. Organizations Contacted: FDEP State Warning Point ¿ Talked to Taylor at 3:24 p.m. on 8/30/17. Florida Department of Environmental Protection ¿ Left voice message with Dana Vestal at 3:30 p.m. on 8/30/17. Florida Department of Health ¿ Left voice message with Lisa at 3:38 p.m. on 8/30/17. | 08/30/2017 05:18 PM | manhole @ Carpenters Park Broad St. Entrance | ; Milton FL; 32570 |  | Jo Robey | Admin. Assistant | Jo.Robey@ci.milton.fl.us | (850) 983-5434 |  | Admin Assistant | Joe Cook | (850) 698-9244 |  | joe.cook@ci.milton.fl.us | 08/30/2017 02:00 PM | 08/30/2017 03:00 PM | Santa Rosa |  |  | 30.631763 | -87.037857 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=294
North Riverwalk @ Willing Street | 20176670 | Two sewage spills occurred on August 30, 2017, at approximately 2:00 p.m. The estimated spillage was approximately 500 gallons at each site. They occurred at Willing St. at North Riverwalk and Broad St. at the entrance to Carpenters Park, Milton, FL, 32570. The responsible permittee, City of Milton Water & Sewer Department; WWT Facility Permit #FL0021903, 5438 Alabama Street, Milton, Fl. 32570; Phone (850) 983-5434, Fax: (850) 983-5439, has attempted to contact all appropriate entities. Please note below. The discharge has ceased and, by-pass pumping was not used. The spillage was from a manhole caused by excessive rainfall. The untreated domestic spillage was not contained, and did enter the Blackwater River. The Water/ Sewer Department disinfected the area of the spill by applying chlorine bleach and Ban-O. Water samples will be collected and the results will be faxed over to Dana Vestal with FL. D.E.P. @ 850-595-8097. Organizations Contacted: FDEP State Warning Point ¿ Talked to Taylor at 3:24 p.m. on 8/30/17. Florida Department of Environmental Protection ¿ Left voice message with Dana Vestal at 3:30 p.m. on 8/30/17. Florida Department of Health ¿ Left voice message with Lisa at 3:38 p.m. on 8/30/17. | 08/30/2017 05:09 PM | manhole @ North Riverwalk | Willing St. @ North riverwalk; Milton FL; 32570 |  | Jo Robey | Admin. Assistant | Jo.Robey@ci.milton.fl.us | (850) 983-5434 |  | Admin Assistant | Joe Cook | (850) 698-9244 |  | jo.cook@ci.milton.fl.us | 08/30/2017 02:00 PM | 08/30/2017 03:00 PM | Santa Rosa |  |  | 30.623935 | -87.036306 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=293
Aloha Gardens Collection System (FGUA) Pasco County LS #12 | 20176669 | A wastewater spill was found occurring at LS #12 (2341 Chatlin Road, Holiday) @ 730 am 08/30/2017; part of the Aloha Gardens Collection system. The spill is believed to be attributed to the elevated collection system and increased flows being delivered to the station due to the >7.0" of rain received in the local area since Friday 8/25/2017. The two Lift Station pumps which discharge to the Pasco County Utilities force main are unable to consistently keep up with the flows being received. The spill is currently ongoing (intermittently). The entire spill has been contained within the onsite disposal pond (old effluent disposal pond). Determining an estimate to the volume of the spill is difficult due to the fact that the discharge is not continuous. The discharge is contingent to the head pressure of the force main and is dictated by other lift stations contributing to the force main. Current volume is estimated at 15-20 gallons per minute when discharging: however the station has not continuously discharged. | 08/30/2017 04:31 PM | Aloha Gardens Collection System (FGUA) Pasco County LS #12 | 2341 Chatlin Road ; Holiday FL; 34691 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 |  | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 08/30/2017 07:30 AM | 09/05/2017 07:00 AM | Pasco |  | N | 28.193441 | -82.760916 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=292
7564 Centurion Parkway North Transformer spill | 20176642 | 2500 kVA TX leaked out entire contents of reservoir. Non-PCB oil to pavement and stormdrain. Surface water impacts TBD. For updates, see https://www.jea.com/environment/environmental_incident_reporting/ | 08/30/2017 04:07 PM | JEA transformer located on Vistakon campus | 7564 Centurion Parkway North ; Jacksonville FL; 32256 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/30/2017 02:40 AM | 08/30/2017 02:50 AM | Duval |  |  | 30.237699 | -81.546433 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=291
Land O'Lakes WWTP CCC UD Spill | 20176644 | During a heavy rain event the flow at the Land O Lakes WWTP surged above 6.0 mgd. The design capacity of this facility is 3.5 mg. This caused the effluent transfer station to surcharge. We attempted to pump the additional flow directly to the reuse crom tank, when this failed, we resorted to pumping the excess amount to the storm water pond next to the C.C.C. The total amount discharged is estimated at 6000 gallons. At no time did this facilitly fail to meet reuse standards for their effluent flow. | 08/30/2017 03:49 PM | Land O'Lakes Wastewater Treatment Facility | 6003 Parkway Boulevard; Land O'Lakes FL; 34639 | (Permit # FLA012731) | James Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Environmental Compliance Specialist | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 08/29/2017 01:30 PM | 08/29/2017 04:45 PM | Pasco |  |  | 28.239853 | -82.437524 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=290
Q232378 NW 15th Terrace between 4th and 5th Streets | 20176666 | A surcharge of the sanitary sewer system that is serviced by Lift Station A-18 occurred causing untreated sewage to flow onto the street from several manholes. The overflow entered the storm drains in the area that outfall into the North Fork New River. The total volume of the overflow was estimated at 1,000 gallons. Half of that volume was recovered from the roads before entering the storm system. | 08/30/2017 03:42 PM | GTL Regional Wastewater Facility | FL; 33309 |  | Troy | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/30/2017 09:10 AM | 08/30/2017 11:00 AM | Broward |  |  | 26.126392 | -80.162655 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=289
Land O'Lakes WWTP CCC UD Spill | 20176644 | During a heavy rain event the flow at the Land O Lakes WWTP surged above 6.0 mgd. The design capacity of this facility is 3.5 mg. This caused the effluent transfer station to surcharge. We attempted to pump the additional flow directly to the reuse crom tank, when this failed, we resorted to pumping the excess amount to the storm water pond next to the C.C.C. The total amount discharged is estimated at 6000 gallons. At no time did this facilitly fail to meet reuse standards for their effluent flow. | 08/30/2017 02:40 PM | Land O'Lakes Wastewater Treatment Facility | 6003 Parkway Boulevard; Land O'Lakes FL; 34639 | (Permit # FLA012731) | James Hircock | Environmental Compliance Specialist | jhircock@pascocountyfl.net | (813) 235-6189 | 6905 | Utilities Compliance Officer | James Hircock | (727) 247-0391 |  | jhircock@pascocountyfl.net | 08/30/2017 01:30 AM | 08/30/2017 04:45 AM | Pasco |  | N | 28.239 | -82.437 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=288
Sanitary Sewer Overflow | 20176660 | Sewage spill of quantity to be determined. | 08/30/2017 01:28 PM | Central Water Reclamation Facility | FL |  | Robert Gordon | Communications Coordinator II | scada.operations@ecua.fl.gov | (850) 969-6500 |  | Operator Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/30/2017 08:50 AM | 08/30/2017 10:30 AM | Escambia |  |  | 30.426454 | -87.276782 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=287
Morris Bridge Transformer Fire | 20176633 | Electric fault caused fire to start in transformer for well #153. As a result of the fire, there was a spill of non-PCB electrical insulating oil to the ground. Quantity unknown but less than 145 gallons capacity of transformer. Unknown amount remains in the transformer. Spill contained and no additional leakage. | 08/29/2017 05:44 PM | Morris Bridge Wellfield - Well # 153 | 17101 Bruce B. Downs Blvd.; Tampa FL |  | Tampa Bay Water / Thea Dunmire | Environmental Management & Regulatory Compliance Senior Manager | tdunmire@tampabaywater.org | (727) 337-1112 |  | Operator Of the Facility | Thea Dunmire | (727) 337-1112 |  | tdunmire@tampabaywater.org | 08/28/2017 07:30 PM | 08/29/2017 07:00 AM | Hillsborough |  |  | 28.114912 | -82.331383 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=286
wastewater overflow near 6700 N. Rivershore Dr. | 20176607 | On August 28, the City of Tampa Wastewater Department became aware of a wastewater overflow near 6700 N. Rivershore Dr. due to high flow rates associated with heavy rain storms. The wastewater discharged into the Hillsborough River from a manhole located adjacent to the river. The volume of the overflow is estimated at 39,000 gallons. | 08/29/2017 04:40 PM | City Of Tampa Wastewater Department | 2545 Guy Verger Blvd; Tampa FL; 33605 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastewater Department | Eric Weiss | (813) 274-8039 |  | Eric.weiss@tampagov.net | 08/28/2017 08:30 PM | 08/28/2017 10:30 PM | Hillsborough |  |  | 28.00826 | -82.464836 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=285
Pittman Hill Rd. | 20176629 | Told them that 10,000 gallons of treated effluent went into the woods at 733 Pittman Hill Rd. The line is not active now and is currently off line and does not effect out ability to operate our facilities. It should be fixed within the next few days and we will notify our local DEP office when repairs are complete. There is currently not an active spill occurring. | 08/29/2017 03:58 PM | City of Marianna WWTP Sprayfield | 2832 Davey St., Marianna, FL 32448; Marianna FL; 32448 | Turn on to Pittman Hill Rd. off of Laramore Rd. Travel approximately 4.5 miles until you get to 733 Pittman Hill Rd. | David Melvin | Foreman | melvind@cityofmarianna.com | (850) 526-5428 |  | Foreman | Rick Harrell | (850) 573-6340 |  | water@cityofmarianna.com | 08/29/2017 07:00 AM | 08/29/2017 09:00 AM | Jackson |  |  | 30.619056 | -85.253896 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=284
Behind Victoria Dr in Loughman, FL 33837 | 20176628 | On August 28, 2017 at 4:30 PM, PCU discovered a 8¿ reclaimed water pipeline break at the Oak Hills Rapid Infiltration Basin (RIB) site behind Victoria Drive in Loughman. Flow to the RIB site was terminated at 5:09 PM. Based on the metered volumes leaving the Northeast Regional Wastewater Treatment Facility through the public access reuse system, the operator estimates the loss of highly treated reclaimed water to be approximately 9 million gallons. The discharge flowed into a near-by wooded area on County property bordering a wetland system. It is believed the line break occurred as the result of an act of vandalism involving a tractor. A section of the RIB's berm was also damaged in the incident. PCU will bring in a licensed contractor to begin immediate repairs to the berm and affected infrastructure. State Watch Office was contacted at 3:11 PM on August 29, 2017 as a precaution and the incident number is #2017-6628. | 08/29/2017 03:30 PM | Northeast Regional WWTF; FLA 012967 | 200 Westview Drive; Davenport FL; 33837 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 08/28/2017 04:30 PM | 08/28/2017 05:10 PM | Polk |  |  | 28.209964 | -81.554327 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=283
PCU SCB AWWTF Service Area DS021 8-24-2017 | 20176410 | The is a resubmittal of the pdf that was sent to pollution.notice@dep.state.fl.us on 8/24/2017 per DEP employee, Mike Lynch's instructions on 8/29/2017. Michelle Maccini (Pinellas County, Utilities, Water Quality Division, Largo, FL) contacted the SWP Hotline on 8/24/2017. The incident occurred at 10350 118th Terrace N. Largo, FL. The incident started at 7:00 am and ended at 9:15 am (2.25 hrs). The sewage (2000 gallons) from two overflowing manholes flowed into a storm drain system discharging to a nearby canal, feeding into Lake Seminole. The blockage was cleared and the area was rinsed down, sanitized and debris was removed. Surface water samples were collected and cautionary signs were posted. First manhole Latitude 27.880197; Longitude 82.781733 Second Manhole: Latitude 27.880181; Longitude 82.781287 | 08/29/2017 03:02 PM | South Cross Bayou AWWTF (FL0040436) | 7401 54th Ave. N.; St. Petersburg FL; 33709 |  | Sheri Lovely | Technical Program Coordinator | slovely@pinellascounty.org | (727) 582-2379 |  | Water Quality Division Employee | Michelle Maccini | (727) 582-2379 |  | mmaccini@pinellascounty.org | 08/24/2017 07:00 AM | 08/24/2017 09:15 AM | Pinellas |  |  | 27.880134 | -82.781799 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=282
Line break S. Francisco and E El Paso Clewiston | 20176481 | Cast Iron force main leak. Pipe is 4.5 to 5 feet below the surface of the road. The crew located the leak and repaired the pipe. Approximately 10,000 gallons of untreated sewage was released. Surrounding area was treated with lime. | 08/29/2017 02:34 PM | City of Clewiston WWTP | 115 W. Ventura Ave.; Clewiston FL; 33440 | The spill occurred in the E. El Paso block of S. Francisco St. | Lynne Mila | Compliance Officer | lynne.mila@clewiston-fl.gov | (863) 983-1454 |  | Employee for the City of Clewiston | Lynne Mila | (678) 200-8707 |  | lynne.mila@clewiston-fl.gov | 08/25/2017 06:55 PM | 08/25/2017 07:55 PM | Hendry |  |  | 26.74859 | -80.923099 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=281
PCU WED WRF SA DS 335 8-25-17 | 20176459 | Michelle Maccini (Pinellas County Utilities, Water Quality Division, Largo FL) contacted the SWP Hotline. The incident occurred at 1427 Tampa Rd., Palm Harbor, FL. The incident started at 8:05 am and ended at 9:30 am on 8-25-17. SSO was not contained onsite. A 10" force main broke and released 10,000 gallons of untreated sewage into the storm drain system. A 5 foot section of is in the process of being replaced; utility crews prevented additional overflows by controlling collection system retention times prior to the site of the break. The cause of the break is not know at this time. Clean-up of the area is also in progress. Water Quality staff traced the storm drain system to a retention pond west of the SSO; however, based on the distance from the break to the pond, it is not known if the SSO will actually impact the retention pond. As a precautionary measure, signs have been posted and samples are being collected. The retention pond's outlet is 6 to 8 inches above the water level; under current conditions, if the retention pond has been impacted, it would be contained. | 08/29/2017 01:52 PM | William E. Dunn WRF FL0128775 | 4111 Dunn Drive; Palm Harbor FL; 34683 |  | Matthew Wotowiec | Water Quality Monitoring Manager | mwotowiec@pinellascounty.org | (727) 582-2341 |  | Pinellas County Utilities Employee | Michelle Maccini | (727) 582-2379 |  | mmaccini@pinellascounty.org | 08/25/2017 08:05 AM | 08/25/2017 09:30 AM | Pinellas |  |  | 28.068142 | -82.75979 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=280
Spanish Main RV Resort | 20176627 | Received notification from operator that while onsite today (at approximately 1000 am) found effluent disposal pond discharging through the emergency overflow to the adjacent ditch. Heavy rains in the local area are believed to have contributed to the elevated pond levels. The operator has reported over 1.2" of rain since his last visit. Flows were calculated at 0.034 mgd. The discharge has not stopped at this point. SWP # 2017-6627 The Owners are currently hauling from the pond in an attempt to lower and prevent discharge from Occurring. A total of 5500 gallons was hauled on 8/28; and it is anticipated that an additional 11,000 will be hauled today 8/29. The operator has collected samples from the discharge for CBOD/TSS/Fecal/Nitrate | 08/29/2017 01:08 PM | Spanish Main RV Resort | 12110 Spanish Main Resort Trail; Thonotosassa FL; 33592 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 |  | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 08/29/2017 10:00 AM | 10/30/2017 09:00 AM | Hillsborough | Hillsborough | Y | 28.06505 | -82.302958 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=279
13455 Wilcox Rd | 20176626 | Heavy rain caused the alarms to go off at Lift Station # 20 which was unable to keep up; two manholes (36-2010.1 & 36-2010) overflowed across the ground, into the catch basing & creek. | 08/29/2017 01:01 PM | City of Largo WWRF | 13455 Wilcox Rd.; Clearwater FL; 33774 |  | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 08/28/2017 08:30 PM | 08/28/2017 09:30 PM | Pinellas |  |  | 27.891276 | -82.825482 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=278
Mid County WWTP Master L/S Power Failure | 20176618 | WWTP Master Lift station main circuit breaker tripped out due to heavy rain and lightning. This caused L/S to completely fill up to containment area spilling over onto ground which made it's way to curlew creek. Approximately 1500 gallons was released. I would estimate that at least 600 gallons made it to the creek.Dave Worrell was called in due to C&A alarm high level L/S alarm, the operator on call was able to reset the breaker, stopping the spill. Lift station was back to normal operation by 7:15pm. Fecal colony samples were taken in three spots on creek and sent to AEL laboratories. | 08/29/2017 12:23 PM | Utilities Inc. of Florida-Mid County | 2299 spanish vistas drive; Dunedin FL; 34698 | Belcher rd. north from main street to Spanish vistas drive, turn right into back entrance of Doral Village, follow road straight to double gates of WWTP. Master L/S is located on east side of property near fence line by creek. | Seyd Matteson | Lead Operator | sjmatteson@uiwater.com | (727) 787-7978 |  | Operator Of the Facility | Seyd Matteson | (727) 787-7978 |  | sjmatteson@uiwater.com | 08/28/2017 06:30 PM | 08/28/2017 07:30 PM | Pinellas |  |  | 28.037551 | -82.741605 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=277
Manhole Overflows | 20176553 | Manholes at Parker and SR 70 and at Parker and Magnolia are currently overflowing due to extreme rainfall and flooding in the area. | 08/29/2017 11:44 AM | William Tyson WRF | 223 S Parker Ave; Arcadia FL; 34266 |  | Julie Karleskint | Engineer, Hazen and Sawyer | jkarleskint@hazenandsawyer.com | (941) 960-4983 |  | Engineer | AJ Berndt | (863) 558-2091 |  | aberndt@arcadia-fl.gov | 08/25/2017 10:00 PM |  | DeSoto |  |  | 27.220474 | -81.874574 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=276
SWWRF Headworks | 20176612 | Heavy and intense rainfall caused a rapid increase in flow that resulted in an overflow out of plant headworks, that lasted approximately ¿ hour of approximately 1000 gallons of raw sewage. The plant is under construction, with standing water from rain that mixing with the overflow of raw sewage. The mixed water was contained in depressions and construction excavation in the general area of the headworks. A significant portion was being collected in process area drains and was routed back to the front of the treatment process. | 08/29/2017 11:13 AM | Southwest Water Reclamation Facility | 3800 54th Ave S; St. Petersburg FL; 33711 |  | Frank L. Niles | Water Reclamation Operations Specialists | frank.niles@stpete.org | (727) 892-5640 |  | Person reporting pollution. | George K. Wise | (727) 893-7497 |  | george.wise@stpete.org | 08/28/2017 08:10 PM | 08/28/2017 08:30 PM | Pinellas |  |  | 27.718515 | -82.684848 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=275
Wastewater overflow at 2900 Perry Avenue | 20176604 | On August 28, the City of Tampa Wastewater Department became aware of a wastewater overflow at 2900 Perry Ave. due to high flow rates associated with heavy rain storms. The wastewater discharged into the Hillsborough River from an emergency overflow pipe that connects to the West River Inceptor sewer. The overflow started at approximately 6:45pm and ended at approximately 11:05pm. The volume of the overflow is estimated at 290,000 gallons. | 08/29/2017 11:00 AM | City Of Tampa Wastewater Department | 2545 Guy Verger Blvd; Tampa FL; 33602 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastewater Department | Eric Weiss | (813) 274-8039 |  | Eric.weiss@tampagov.net | 08/28/2017 06:45 PM | 08/28/2017 11:05 PM | Hillsborough |  |  | 27.969961 | -82.479112 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=274
405897 | 20176609 | DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION WASD Incident #: 405897 Version: 2 Version Type: Supplementary Incident Version Created On: 08/29/17 07:25 AM Job Order #: 1003487410 Location of Discharge: 8340 NW 54 ST DORAL 33166 Latitude: 25.8225058348693 Longitude: -80.3324793563932 Reported by WASD Employee? Yes Employee ID: 00008954 Employee Title: WDS Reported by: FLOYD PINCKNEY Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Contractor Involved? Yes (Private Contractor) Private Contractor Name: D & Y ENGINEERING Path of Flow: East and West On: 54 STREET Discharge Caused by Asset Type: Force Main Discharge Due to/Caused by: Force Main Broken Other Cause Additional Discharge Cause: BRKN BY CONTRACTOR Pipe Material: DIP (Ductile Iron Pipe) Pipe Size in inches: 12 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? Yes Number of Storm Drain(s) Impacted: 1 Distance in Feet to Storm Drain(s): 600 Direction: West Did Discharge Go into Surface Water? No Weather Conditions: Cloudy Estimated Quantity of Sewage Released in Gallons: 67,598 Estimated Time Release Started: 08/28/17 09:20 PM Estimated Time Action Taken at Site: 08/28/17 10:15 PM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 08/28/17 11:00 PM Spill Contained? Yes Area Cleaned? No Area Disinfected? No Spill Recovered? No Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 08/28/17 10:15 PM AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone 2017-6609/CLAUDIA 08/29/17 07:38 AM RER RER Compliance Desk Phone DERM/SELINA 08/29/17 07:38 AM WASD WASD Bertha Goldenberg Phone GOLDENBERG 08/29/17 07:38 AM DEP DEP Notification Group E-mail 08/29/17 07:38 AM DOH DOH Notification Group E-mail 08/29/17 07:38 AM EPA EPA Notification Group E-mail 08/29/17 07:38 AM HMS Hazardous Materials Subcommittee Group E-mail 08/29/17 07:38 AM RER RER Notification Group E-mail 08/29/17 07:38 AM SFWM SFWM Notification Group E-mail 08/29/17 07:38 AM WASD WASD Interdepartmental Personnel E-mail 08/29/17 07:38 AM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Widly Nerrete (NERETTE) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ 08/29/17 10:39 AM * Fields on red are the ones that changed from previous version Page 1 of 1 | 08/29/2017 10:45 AM | Miami-Dade W&S Collection System | 8340 NW 54 ST DORAL 33166 ; Doral FL; 33166 |  | Floyd Pinckney | WDS | floyd.pinckney@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 08/28/2017 09:20 PM | 08/28/2017 11:00 PM | Miami-Dade |  |  | 25.822581 | -80.331823 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=273
1250 Flora Branch Blvd | 20176622 | Manhole overflow due to grease blockage. ~100 gallons of wastewater to catchbasin & detention pond. Detention pond in overflow to Flora Branch. JEA will collect fecal coliform samples. For updates see https://www.jea.com/environment/environmental_incident_reporting/ | 08/29/2017 09:26 AM | Blacksford collection system | 1250 Flora Branch Road; Fruit Cove FL; 32259 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/28/2017 05:45 PM | 08/28/2017 06:35 PM | Duval |  |  | 30.111412 | -81.59291 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=271
Sanitary Sewer Overfow - City of Orlando | 20176486 | While conducting a capital improvement project on South Parramore Street and Citrus Avenue, a car struck the 6" bypass pump hose installed by contractors and a total of 5500 gallons of sanitary sewer were released after the incident. City of Orlando crews responded to the event and provided support for reconnection of line to stop leak. | 08/28/2017 02:49 PM | City of Orlando Capital Improvement Project | Intersection of Parramore Ave and Citrus Street; Orlando FL; 32811 | Take I-4 East to Gore street Exit and turn Left. Proceed down Gore and turn left on Parramore Street. The next intersection is citrus street. | Daniel Friedline | Public Outreach Coordinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | Authorized City of Orlando Representative | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 08/26/2017 02:30 PM | 08/26/2017 03:30 PM | Orange |  |  | 28.529312 | -81.388901 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=270
Fiesta Village Partial Filter Bypass | 20176581 | 8/27/2017 @ 2352-0500 Fiesta Village temporarily bypassed the effluent filters partially due to high influent flows. | 08/28/2017 02:40 PM | Fiesta Village Advanced Wastewater Treatment Plant | 1366 San Souci Dr.; Fort Myers FL; 33919 | Cypress Lake Dr, South Fiesta Way, Left Seville, Right Tropi | Darryl Parker | Lead Operator | dparker3@leegov.com | (239) 481-1953 |  | Operator Of the Facility | Darryl Parker | (239) 481-1953 |  | dparker3@leegov.com | 08/27/2017 11:52 PM | 08/28/2017 05:00 AM | Lee | Lee | Y | 26.3226 | 81.5415 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=269
Reuse Release | 20176570 | Due to heavy rains everything is at max capacity with nowhere for reuse effluent to go. On 8/27 at approximately 1900 hours reuse started discharging from a holding pond spillway. This Continued through 8/30/2017 at 1300 hours. The total amount discharged was estimated at 8.809 mg. | 08/28/2017 01:35 PM | East WRF | 11550 Operations Way; Bonita Springs FL; 34135 |  | Andy Koebel | Director of Operations | akoebel@bsu.us | (239) 992-0711 |  | Operator Of the Facility | Andy Koebel | (239) 992-0711 |  | akoebel@bsu.us | 08/27/2017 07:00 PM | 08/30/2017 01:00 PM | Lee | Lee | Y | 26.37213 | -81.769331 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=268
Landings Golf Course reuse discharge | 20176571 | 8/27/2017 @ 1615 the Landings Golf Course reuse customer pond level instrumentation failed indicating a low pond level which allowed reclaim water to flow to pond when actual level was above normal levels and was discharging; operator on duty shut customer off with manual valve at time of discovery 1750. Total reuse flow amount entering pond while pond system was discharging was 52,470 gallons. Instrumentation is investigating the cause of malfunction at this time. | 08/28/2017 01:20 PM | Fiesta Village Advanced Wastewater Treatment Plant | 1366 San Souci Dr.; Fort Myers FL; 33919 | Cypress Lake Dr, South Fiesta Way, Left Seville, Right Tropi | Darryl Parker | Lead Operator | dparker3@leegov.com | (239) 481-1953 |  | Operator Of the Facility | Darryl Parker | (239) 481-1953 |  | dparker3@leegov.com | 08/27/2017 04:15 PM | 08/27/2017 05:50 PM | Lee | Lee | Y | 26.554559 | -81.918148 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=267
4584 S. Suncoast Blvd, Homosassa, FL |  | D.A.B. Construction Inc. / on the Homosassa & US19 project was removing soil and debris and dug too deep and hit an 8" force main spilling approximately 700 - 800 gallons of raw sewage. The sewage was contained in the stormwater drainage swale. Citrus County Utilities valved off the force-main and turned off lift stations. The road contractor, D.A.B, had A-Able septic company clean the area using a pump truck, lime the affected area, and then D.A.B repaired the force-main. D.A.B. Construction Inc. had a Supervisor to employee communication problem. | 08/28/2017 01:00 PM | Meadowcrest Collection System - 4584 S Suncoast Blvd. | 4584 S. Suncoast Blvd.; Homosassa FL; 34446 |  | Charles Thompson | Maintenance Supervisor | Charles.Thompson@citrusbocc.com | (352) 400-0846 |  | Maintenance Supervisor | Gary Loggins | (352) 527-7650 |  | Gary.Loggins@citrusbocc.com | 08/28/2017 10:30 AM | 08/28/2017 11:00 AM | Citrus |  |  | 28.794554 | -82.572993 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=266
5531 Tropics Drive | 20176569 | Initial call was received by Public Works. I went on site immediately and dispatched crews to the site. The vac truck was on site when I arrived and crews were popping man hole lids to trace the issue. A minute or two later an inlet sock was placed at the storm inlet by another crew. Issue was found at the Warren Liftstation. It did not call out or sound alarms. Crews kicked on pumps to manual and immediately stopped the manhole lid from overflowing. Crews met me back at the manhole site and started the clean up of the site. Vaccuming up the raw sewage that had a puddle formed, then spraying down the area with water and vaccuming it up. After that, crews put down lime. Inlet sock was removed and crews departed the site. | 08/28/2017 11:58 AM | City of New Port Richey | FL |  | Zachary Thull | Utilities Operations Manager | ThullZ@CityOfNewPortRichey.org | (727) 841-4536 |  | Utilities Operations Manager | Zachary Thull | (727) 841-4536 |  | ThullZ@cityofnewportrichey.org | 08/28/2017 08:05 AM | 08/28/2017 08:15 AM | Pasco |  |  | 28.239441 | -82.711844 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=265
SWUCI Collection System |  | A collection system gravity line began backing up due to a grease build up located on Scenic Gulf Drive between Kenny D¿s restaurant and the Leeward Key Condominium in Walton County. The backup was removed and the line cleared. An estimated 100 gallons of untreated wastewater escaped a manhole behind Kenny D¿s. The area affected was disinfected and cleaned up. No wastewater entered any surface waters. | 08/28/2017 11:54 AM | South Walton Utility Company, Inc. COllection System | 369 Miramar Beach Drive; Miramar Beach FL; 32550 |  | Joe Ream | Water/Wastewater Director | jrr@swuci.org | (850) 837-2988 | 112 | Operator Of the Facility | Joe Ream | (850) 837-2988 |  | jrr@swuci.org | 08/27/2017 07:35 PM | 08/27/2017 10:30 PM | Walton |  |  | 30.380681 | -86.396753 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=264
405595 | 20176566 | DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION WASD Incident #: 405595 Version: 3 Version Type: Supplementary Incident Version Created On: 08/28/17 11:06 AM Job Order #: 1003486154 Location of Discharge: NW 38 AVE & NW 145 ST Reported by WASD Employee? Yes Employee ID: 00009317 Employee Title: WDS Reported by: NASH HOWARD Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Contractor Involved? Yes (County Contractor) County Contractor Name: AMERICAN ENGINEERING Path of Flow: North and South On: 38 AVE Discharge Caused by Asset Type: Force Main Discharge Due to/Caused by: Force Main Broken Other Cause Pipe Material: ACP (Asbestos Cement Pipe) Pipe Size in inches: 10 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? No Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Cloudy Estimated Quantity of Sewage Released in Gallons: 1,404,996 Estimated Time Release Started: 08/26/17 08:30 AM Estimated Time Action Taken at Site: 08/26/17 09:30 AM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 08/26/17 12:00 PM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Spill Recovered? No Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 08/26/17 09:30 AM AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone Henry-inc# 2017-6566 08/28/17 11:15 AM RER RER Compliance Desk Phone Steve 08/28/17 11:15 AM WASD WASD Bertha Goldenberg Phone Bertha 08/28/17 11:15 AM DEP DEP Notification Group E-mail 08/28/17 11:15 AM DOH DOH Notification Group E-mail 08/28/17 11:15 AM EPA EPA Notification Group E-mail 08/28/17 11:15 AM HMS Hazardous Materials Subcommittee Group E-mail 08/28/17 11:15 AM RER RER Notification Group E-mail 08/28/17 11:15 AM SFWM SFWM Notification Group E-mail 08/28/17 11:15 AM WASD WASD Interdepartmental Personnel E-mail 08/28/17 11:15 AM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Jerry Diaz (JDIAZ) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ 08/28/17 11:22 AM * Fields on red are the ones that changed from previous version Page 1 of 1 | 08/28/2017 11:30 AM | Howard Nash | NW 38 ave & NW 145 street ; Miami FL; 33054 |  | Howard Nash | WDS | howard.nash@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 08/26/2017 08:30 AM | 08/26/2017 12:00 PM | Miami-Dade |  |  | 25.905971 | -80.26188 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=263
405728 |  | DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION WASD Incident #: 405728 Version: 3 Version Type: Supplementary Call Center Comments: N/A Incident Version Created On: 08/27/17 10:10 PM Job Order #: 1003486355 Location of Discharge: 6855 SW 152 ST PALMETTO BAY 33158 Additional Location Description: NORTH/SOUTH ON SW 152 ST Latitude: 25.6299342193008 Longitude: -80.3044060219922 Reported by WASD Employee? Yes Employee ID: 00024168 Employee Title: WATER DISTRIBUTION SUPER. Reported by: ISRAEL CAMACHO Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Contractor Involved? No Path of Flow: North and South On: 152 Discharge Caused by Asset Type: Force Main Discharge Due to/Caused by: Force Main Leaking Due to Corrosion Additional Discharge Cause: SPLIT ON THE PIPE Pipe Material: CI (Cast Iron) Pipe Size in inches: 8 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Rainy Estimated Quantity of Sewage Released in Gallons: 24,838 Estimated Time Release Started: 08/27/17 01:37 PM Estimated Time Action Taken at Site: 08/27/17 02:10 PM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 08/27/17 04:30 PM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Spill Recovered? Yes Recovered Amount in Gallons: 2,200 Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 08/27/17 02:20 PM AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone ANDRES 08/27/17 10:20 PM RER RER Compliance Desk Phone PEDRO 08/27/17 10:20 PM WASD WASD Bertha Goldenberg Phone LVM 08/27/17 10:20 PM DEP DEP Notification Group E-mail 08/27/17 10:20 PM DOH DOH Notification Group E-mail 08/27/17 10:20 PM EPA EPA Notification Group E-mail 08/27/17 10:20 PM HMS Hazardous Materials Subcommittee Group E-mail 08/27/17 10:20 PM RER RER Notification Group E-mail 08/27/17 10:20 PM SFWM SFWM Notification Group E-mail 08/27/17 10:20 PM WASD WASD Interdepartmental Personnel E-mail 08/27/17 10:20 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Michael A. Cabrejos (E312898) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ 08/28/17 11:00 AM * Fields on red are the ones that changed from previous version Page 1 of 1 | 08/28/2017 11:12 AM | Miami Dade Water & Sewer Department Collection System | 6855 SW 152 St ; Palmetto Bay FL; 33158 | Palmetto Bay | Israel Camacho | W&S Distribution Supervisor | israel.camacho@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 08/27/2017 01:35 PM | 08/27/2017 04:30 PM | Miami-Dade |  |  | 25.629965 | -80.30437 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=262
C.O.B. W.W.T.P. Influent Structure Overflow | 20176565 | Due to heavy rain/ Inflow the plant Influent structure overflowed intermittently between 4:30 pm thru 7:00 pm. 5,000 gallons of sewage flowed off site to storm drain flowing to the Manatee River. | 08/28/2017 11:07 AM | City of Bradenton W.W.T.P. | 1810 First Street W.; Bradenton FL; 34208 | US-41 and 17th Ave. W. | William J. Quigley | Superintendent | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/27/2017 04:30 PM |  | Manatee |  |  | 27.484316 | -82.564842 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=261
405445 | 20176457 | DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION WASD Incident #: 405445 Version: 3 Version Type: Supplementary Incident Version Created On: 08/25/17 02:22 PM Job Order #: 1003485635 Location of Discharge: 10820 SW 200 DR UNINCORPORATED MIAMI-DADE 33157 Additional Location Description: REAR BETWEEN BLDG A & B Latitude: 25.5807887885164 Longitude: -80.3682782696299 Reported by WASD Employee? Yes Employee ID: 00029656 Employee Title: PIPE FITTER SUPERVISOR Reported by: BILLY GRAVES Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Contractor Involved? Yes (Private Contractor) Private Contractor Name: V ENGINERRING & CONSULTING COR Path of Flow: North On: REAR OF BLDG A & B Discharge Caused by Asset Type: Force Main Discharge Due to/Caused by: Force Main Broken Other Cause Additional Discharge Cause: BROKEN BY CONTRACTOR Pipe Material: PVC (Polyvinyl Chloride) Pipe Size in inches: 4 Type of Water Discharge: RAW SEWAGE Did Discharge Go to Public Access Area? No Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? No Weather Conditions: Rainy Estimated Quantity of Sewage Released in Gallons: 78,116 Estimated Time Release Started: 08/25/17 09:30 AM Estimated Time Action Taken at Site: 08/25/17 09:45 AM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 08/25/17 10:30 AM Spill Contained? Yes Area Cleaned? Yes Area Disinfected? Yes Method of Disinfection: Lime/Vactor Spill Recovered? Yes Recovered Amount in Gallons: 2,000 Public Notified? Yes Method of Public Notification: Post Signs Public Notified On: 08/25/17 09:45 AM AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone OPER#318 2017-6456 08/25/17 02:28 PM RER RER Compliance Desk Phone NAVILA BERNAL 08/25/17 02:28 PM WASD WASD Bertha Goldenberg Phone BERTHA LVM 08/25/17 02:28 PM DEP DEP Notification Group E-mail 08/25/17 02:28 PM DOH DOH Notification Group E-mail 08/25/17 02:28 PM EPA EPA Notification Group E-mail 08/25/17 02:28 PM HMS Hazardous Materials Subcommittee Group E-mail 08/25/17 02:28 PM RER RER Notification Group E-mail 08/25/17 02:28 PM SFWM SFWM Notification Group E-mail 08/25/17 02:28 PM WASD WASD Interdepartmental Personnel E-mail 08/25/17 02:28 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Julio C. Acosta (E313378) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ 08/25/17 04:56 PM * Fields on red are the ones that changed from previous version Page 1 of 1 | 08/28/2017 10:54 AM | Miami Dade Water & Sewer Department Collection System | 10820 SW 200 Dr; Miami FL; 33157 | Rear between building A & B | Billy Graves | Pipefitter Supervisor | billy.graves@miamidade.gov | (305) 274-9272 |  | Operator Of the Facility | Marcelo M. Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 08/25/2017 09:30 AM | 08/25/2017 10:30 AM | Miami-Dade |  |  | 25.58035 | -80.368958 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=260
SSO Broken 18" Forcemain@741 Bayshore Dr. 8/28/2017 Q#231103 | 20176563 | A leak coming out of the ground was reported to the City at 6:16 AM 8/28/2017. Crews responded and the pipe was isolated and the leak stopped at 8:30 AM 8/28/2017. An 18" cast iron force main break is the cause of the sanitary sewer overflow. The overflow has impacted the Intracoastal Waterway. An estimate of volume of >100,000 gallons. | 08/28/2017 10:51 AM | GTL Regional Wastewater Facility | FL; 33309 |  | Troy | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/28/2017 03:50 AM | 08/28/2017 08:30 AM | Broward |  | N | 26.133343 | -80.108326 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=259
C.O.B. Manhole Overflow 800 Block Virginia Drive. | 20176557 | Due to heavy rains, manhole overflowed 1,300 gallons of sewage. Spill was Vacuumed up, Street Sweeper cleaned road. Lime applied to area effected. | 08/28/2017 10:34 AM | City of Bradenton W.W.T.P. | 1810 First Street W.; Bradenton FL; 34208 | US-41 and 17th Ave. W. | William J. Quigley | Superintendent | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/27/2017 10:30 AM | 08/27/2017 11:00 AM | Manatee |  |  | 27.492875 | -82.58043 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=258
C.O.B. Manhole Overflow 2700 block of 22nd Ave. W. | 20176556 | Due to heavy rains, manhole overflowed 1,500 gallons of sewage. Spill was Vacuumed up, Street sweeper cleaned road and Lime applied to area affected. | 08/28/2017 10:23 AM | City of Bradenton W.W.T.P. | 1810 First Street W.; Bradenton FL; 34208 | US-41 and 17th Ave. W. Bradenton. | William J. Quigley | Superintendent | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/27/2017 10:30 AM | 08/27/2017 11:00 AM | Manatee |  |  | 27.483049 | -82.596801 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=257
COB L/S #14 Spill | 20176555 | Overflow of Lift Station #14 due to Heavy Rains/ Inflow 2,900 gallons sewage spilled. All sewage Vacuumed up, cleaned with Street Sweeper and Limed. Preventative Action Taken: N/A ****ANY SPILL OVER 1,000 GALLONS NEEDS TO BE REPORTED TO THE STATE WARNING POINT 1-800-320-0519**** FDEP Notified Date: 8/28/2017 * Notified State Warning Point. Yes Time: 10:00 am Incident # 2017-6555 Method: X " E-mail:Lance.Kautz@dep.state.fl.us " Ph: (813) 470-5903 Party Contacted: Lance Kautz Samples Taken? N/A Samples Results: N/A Event End Date: 8/27/2017 Event End Time: 11:15 am | 08/28/2017 10:13 AM | City of Bradenton W.W.T.P. | 1810 First St. W.; Bradenton FL; 34208 | US-41 and 17th Ave. W. Bradenton | William J. Quigley | Superintendent | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/27/2017 10:30 AM | 08/27/2017 11:15 AM | Manatee |  |  | 27.484164 | -82.580885 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=256
Lift Station MC#20 Overflow 8-27-17 | 20176552 | Received high level alarm at lift station MC #20. Pump truck hauled two loads (~10,000 gallons) of influent prior to the station becoming overwhelmed. Approximately 1,200 - 1,400 gallons overflowed, due to excessive rainfall combined with a high tide event, in to the fenced lift station retention area. The area affected was the retention area with in the lift station fence. No offsite discharge. No stormwater drains or surface waters affected. A valve was shut off and this lift station was bypassed to another to help relieve the flow to this station. The standing sewage was pumped and the affected area was limed. We will monitor the weather and tides to try and predict impacts on our system. Continue to address I&I in the collection system. | 08/28/2017 09:17 AM | Meadowcrest Collection System - Lift Station #20 | 7465 W. Stuart Lane; Homosassa FL; 34446 |  | Charles Thompson | Maintenance Supervisor | charles.thompson@citrusbocc.com | (352) 400-0846 |  | Maintenance Supervisor | Gary Loggins | (352) 527-7650 |  | Gary.Loggins@citrusbocc.com | 08/27/2017 07:30 PM | 08/27/2017 08:30 PM | Citrus |  |  | 28.813897 | -82.557903 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=254
GRU Wastewater Collection System | 20176522 | At 11 AM on August 27, 2017, GRU was notified of a wastewater release occurring at SW 8th Place and SW 61st Street. When crews arrived, they observed a manhole overflowing at that location. A jet truck was utilized to clear a blockage formed by residential grease. By 12:15 pm, the blockage was cleared and the overflow was stopped. The wastewater release flowed into a storm conveyance and percolated into sandy soil. An estimated 1,500 gallons was released from the manhole. No surface waters were impacted by the release and no wastewater was recoverable. Advisory signs were placed at the release site. State warning point, ACEPD and the health department were notified in a timely manner. FDEP event number is 2017-6522. Coordinates of the spill are 29.644967, -82.409655. Educational materials stressing the importance of keeping fats, oils and grease out of the collection system will be distributed to the neighborhood. A sign indicating the cause of the spill was posted in the impacted area. This collection system flows to the Kanapaha Water Reclamation Facility (FL0112895). | 08/28/2017 08:55 AM | GRU Wastewater Collection System | 800 Block of SW 61st Street; Gainesville FL; 32607 |  | Jennifer McElroy | Supervising Utility Engineer | mcelroyja@gru.com | (352) 393-1291 |  | Supervising Engineer | Tiffany Small | (352) 393-1492 |  | smalltn@gru.com | 08/27/2017 11:00 AM | 08/27/2017 12:15 PM | Alachua |  |  | 29.644973 | -82.409697 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=253
Mosaic Four Corners Mine Water Release 8/27/2017 | 20176528 | Turbid water from the mine recirculation ditch was discharged through the NPDES D-001 outfall for a short time before flocculent application was initiated. The turbidity reading at the outfall was 52.0 NTU at the onset of discharge and was >29 NTU above the NPDES background instream sampling location. Approximately 7.1 inches of rain was recorded at a nearby rain gauge since the gauge was last read on 8/25/2017. The outfall was closed and the discharge diminished to de minimis flow at 1:00 PM on 8/28/17 and completely stopped at 11:00 PM on 8/28/17. | 08/27/2017 07:09 PM | Mosaic Four Corners Mine | 11200 SR 37 South; Bradley FL; 33835 |  | Amy Young | Sr. EHS Specialist | amy.young@mosaicco.com | (863) 581-5692 |  | Site Environmental Specialist | Jackie Barron | (941) 322-6811 |  | Jackie.Barron@mosaicco.com | 08/27/2017 08:30 AM | 08/28/2017 11:00 PM | Hillsborough, Manatee |  | N | 27.644766 | -82.100808 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=252
Fuel Spill |  | There was a fuel spill @ Beall's Distribution facility in Manatee County located @2100 47th Terrace East, Bradenton, FL, 34208. Fuel was spilled into parking lot and through the drain into the nearby retention lake. Amount is unknown at this time but it is around 500 or more gallons. | 08/27/2017 04:58 PM | Beall's Distribution Center 817 | 2100 47th Terrace East, Bradenton, FL, 34208; Bradenton FL; 34208 |  | George Pastujov | Director, Safety and Business Continuity | GPASTUJOV@BEALLSINC.COM | (941) 744-4647 |  | Operator Of the Facility | George Pastujov | (941) 744-4647 |  | GPASTUJOV@BEALLSINC.COM | 08/27/2017 07:00 AM |  | Manatee |  |  | 27.456006 | -82.538129 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=251
Bradenton WRF | 20176523 | On 8-26-17 the Influent structure was hydraulically overloaded causing 1500 - 2500 gallons to overflow into the collection system. The operators bypassed the structure and the bypass ceased. | 08/27/2017 02:26 PM | Bradenton WRF | 1810 first streeet west ; bradenton FL |  | William Waitt | Chief Operator | william.waitt@cityofbradenton.com | (603) 490-8969 |  | Operator Of the Facility | william waitt | (603) 490-8969 |  | william.waitt@cityofbradenton.com | 08/26/2017 10:10 PM | 08/26/2017 10:15 PM | Manatee |  |  | 27.387724 | -82.551909 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=250
Master Lift Station | 20176495 | Breaker tripped causing pumps to stop. Approximately 25,000 gallons spilled before it was reset . Everything was contained on site . Lime was spread on the area. | 08/26/2017 09:14 PM | Bonita Springs WWRF | 8890 Ten-Eight st.; Bonita Springs FL; 34135 | N on Tamiami trail to old us 41. Take right. Half mile on right. | Andy Koebel | Director of Operations | AKoebel@bsu.us | (239) 992-0711 |  | Operator Of the Facility | Andy Koebel | (239) 992-0711 |  | AKoebel@bsu.us | 08/26/2017 07:30 PM | 08/26/2017 07:45 PM | Lee |  |  | 26.375723 | -81.804483 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=249
City of Hollywood 10" Force Main Break | 20176470 | A wastewater force main broke, due to pipe failure. On Friday, August 25, 2017, at approximately 5:00 PM, the City of Hollywood Dept. Public Utilities was informed of a wastewater discharge near 1121 N 70 Avenue 33024, a force main break was verified. The pipe break was an 10-inch asbestos cement pipe. From the time of notification up until approximately 9 PM several Lift Stations were shut off to make the repair. The pipe was repaired and surrounding area were restored by 5:00 AM on 8/26/17. The spill did enter the roadway and public access areas, however there was no discharge to stormdrains. The affected areas are being cleaned up with HTH and vacuum trucks. The discharge amount for the sewage spill is being calculated but is estimated to be +5,000 gallons. The COH will update this report once a true estimate of the spill amount is complete. | 08/26/2017 01:18 PM | City of Hollywood Department of Public Utilities | 1121 N 70 Avenue Hollywood FL 33024; Hollywood FL; 33024 |  | Kassandra Myers | Water Quality Manager | kmyers@hollywoodfl.org | (954) 921-3414 |  | Utility Compliance Contact | Francois Domond < | (954) 921-3048 |  | FDOMOND@hollywoodfl.org | 08/25/2017 05:00 PM | 08/26/2017 05:00 AM | Broward |  |  | 26.019515 | -80.228301 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=248
Sewage Spill 8.24.17 |  | Bay County was contacted at 10:35 am regarding the spill and responded to the site immediately. The GPS location of Spill is: 29¿57'57.6"N 85¿26'55.1"W A pipe defect on the 14 inch force main coming from Mexico Beach caused the wastewater spill. Approximately 8,000 gallons of raw wastewater spilled onto the ground. The spill did not impact any surface water. The damaged force main was isolated with valves near the spill site location. SIS pumped and hauled wastewater from the Mexico Beach master lift station to the Military Point AWTF while the force main was repaired. After the repair work was completed the impacted grounds were treated with lime. | 08/25/2017 03:57 PM | Mexico Beach force main | FL |  | Josie Penton for Albert Bock | Environmental Consultant | josie.penton@dep.state.fl.us | (850) 767-0045 |  | FDEP/Environmental Consultant | Albert Bock | (850) 628-5402 |  | abock@baycountyfl.gov | 08/23/2017 10:30 AM | 08/23/2017 03:00 PM | Bay |  |  | 29.965641 | -85.448266 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=247
2017 08 25 Pool Truck Crash FD Case 2017-010113 |  | Auto accident involving a pool truck. Occurred at Westview Dr/University Dr in Coral Springs,FL. FD case 2017-010113, PD case 17-008464. 2-3 gallons of liquid chlorine were spilled during the crash, and leaked into the grass. | 08/25/2017 12:35 PM | City of Coral Springs Communications Center | 2801 Coral Springs Dr; Coral Springs FL; 33065 |  | Patrick Thurman | Communications Shift Supervisor | pwt546@aol.com | (954) 344-1800 |  | Communications Center Employee | Steven Frey, Assistant Fire Cheif | (954) 344-5934 |  | sfrey@coralsprings.org | 08/25/2017 11:50 AM |  | Broward |  |  | 26.298293 | -80.250204 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=246
Sanitary Sewer Overflow | 20176427 | A contractor jacking and boring hit the City's force main, causing approximately 2,000 gallons of sewage to spill. Contents of the spill were removed via vacuum truck. No waterways were affected. | 08/24/2017 07:41 PM | 6080 US 1 North | ; St. Augustine FL; 32095 |  | Glabra Skipp | Environmental Compliance Analyst | gskipp@citystaug.com | (904) 825-1055 |  | Environmental Compliance Analyst | Glabra Skipp | (904) 825-1055 |  | gskipp@citystaug.com | 08/24/2017 01:00 PM | 08/24/2017 02:00 PM | St. Johns |  |  | 29.981793 | -81.364193 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=245
4760 Sand Lake Road, Orlando, FL 32819 | 20176435 | A contractor cracked a 2¿ reuse water line onsite at the South Water Reclamation Facility while digging trench. The affected area includes unpaved ground north of the Automatic Backwash Filters and south storm water retention pond. There was and still is 3 feet of freeboard before any water could have flowed through the overflow structure and enter into Shingle Creek. There is no potential risk to public health, safety or welfare at this time. | 08/24/2017 06:24 PM | South Water Reclamation Facility | 4760 Sand Lake Road, Orlando, FL 32819; Orlando FL; 32825 |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Engineer II | Troy E. Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 08/23/2017 01:15 PM | 08/23/2017 04:55 PM | Orange |  |  | 28.445793 | -81.440654 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=244
Avalon Road & Water Spring Boulevard | 20176434 | A Field Services investigation revealed that a 20 inch ductile iron reclaimed water main was the source of the discharge. The main was found to have a failure at the joint where the spigot end of the pipe was completely separated from the bell. No other apparent damage was observed. The reclaimed water main is an Orange County owned asset but Water Conserve II provides the reclaimed water for this area. Water Conserve II staff responded initially and shut down the reclaimed water to isolate the system and stop the leak. The reclaimed water main break was located on the west side of Avalon Road approximately 1300 feet north of 15504 Water Spring Boulevard. The main runs parallel to the road approximately 65 feet outside the edge of the pavement, positioned to accommodate an upcoming road widening. Reclaimed water flooded the road, roadside drainage swales and surrounding area. The discharge was absorbed into unpaved surface, and also pooled in the depression created at the main break. Some discharge flowed into a small wetland south of the break. Sand was displaced by the force of the water and deposited around the perimeter of the break. It was also pushed into the tree line just outside of the wetland area. The wetland had been delineated as part of the construction project to install the 20-inch main (which was completed in April 2016) and using the construction drawings as a guide, it appears the disturbed area stops just short of the wetland line. Please see attached map for detail. There was no discharge into storm drains or any other body of water. Most of the overflowed volume of reclaimed water was absorbed into the sandy soil commonly found in the area. New end time for the event is 5:30 AM on 8-24-17 | 08/24/2017 06:21 PM | Orange County Utilities Reclaimed Water System | FL |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Engineer II | Troy E. Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 08/23/2017 10:30 PM | 08/24/2017 06:30 AM | Orange |  | N | 28.407252 | -81.636147 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=243
Test Site D1C Minor Hydraulic Fluid Leak | 20176421 | Rental Equipment on site working on tower. Main hydraulic feed line failure resulting in discharge of approx. >25 gal. hydraulic fluid. SWS, a licensed contractor, retained to clean site per EPA/Military Regs. SWS notified by Military Personnel that due to mission programming work could commence until Tuesday, Aug. 29, 2017. | 08/24/2017 04:40 PM | Tyndall AFB | ; Panama City FL; 32404 | E Hwy 98 Approx. 4 mi. East of Tyndall Main Gate. South side of Hwy 98. | Michael Wilson | Branch Manager | pcm269@sunbeltrentals.com | (850) 872-9226 |  | Branch Manager | Michael Wilson | (850) 872-9226 |  | pcm269@sunbeltrentals.com | 08/24/2017 09:30 AM | 08/24/2017 10:30 AM | Bay |  |  | 30.000474 | -85.508419 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=242
City of Largo Lift Sation #2 Overflow | 20176422 | Clogged air release valve caused untreated sewer water to flow through 2 inch conduit onto area surrounding Lift Station #2. The discharge of raw sewage was estimated to be approximately 2,540 gallons. Staff responded to the site, turned off the valve and the overflow ceased. The affected area was rinsed clean and about 500 gallons was vacuumed. A portion of the discharge reached a nearby storm sewers (about 2,040 gallons). The City's contractor for the lift station reconstruction project was contacted with information about the overflow cause and advised of the need to correct the problem. | 08/24/2017 03:18 PM | FL0026603 - Lift Station #2 | 400 Lake Ave NE; Largo FL | 400 Lake Avenue | Vivian Gleaves | Environmental Manager | vgleaves@largo.com | (727) 518-3061 |  | Wastewater Department Manager | Vivian Gleaves | (727) 518-3061 |  | vgleaves@largo.com | 08/24/2017 09:50 AM | 08/24/2017 10:10 AM | Pinellas |  |  | 27.920275 | -82.770763 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=241
Private Sanitary Sewer Overflow - City of Orlando | 20176042 | At approximately 1545 PM on 08-23-17, a private contractor digging with a backhoe in the area of 5309 McCoy Road hit a 2" Force Main from a privately owned lift station. The private force main did not have a shut off valve installed prior to the publicly owned force main it feeds into and subsequently 60,000 gallons of sanitary sewer overflowed from the area. The Water Reclamation Division was notified and provided support while a shutoff valve and line repair were installed. The sanitary sewer overflow did make contact with the storm water retention areas but 54000 gallons were captured and returned to the sanitary sewer. All areas impacted by the sanitary sewer have been sanitized and cleaned and all materials returned to the sewer system for processing. | 08/24/2017 02:46 PM | Fast Park and Relax | 5309 McCoy Road; Orlando FL; 32812 | Take SR 528 East to the Conway Road Exit. Turn Left on Conway Road and proceed one half mile to Mccoy Road. Turn Right on McCoy Road and the facility is on the left. | Daniel Friedline | Public Outreach Cooridinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | Authorized Representative of the City of Orlando | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 08/23/2017 03:45 PM | 08/24/2017 05:00 AM | Orange |  |  | 28.452107 | -81.317343 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=240
Lago Vista Sewer Spill | 20176411 | On August 24, 2017, at approximately 7:00 AM, a raw wastewater spill began near 1200 Lago VistaCt in Poinciana. A grease blockage occurred between the master manhole and lift station #104, causing a spill inside a nearby clubhouse; the spill flowed to a floor drain which is believed to flow to a stormwater retention. Personnel were not able to determine whether the floor drain flows to stormwater or not, and the nearest water body leads to Lake Tohopekaliga, so surface water samples will be taken. The volume of the raw wastewater spill was estimated to be 10,000 gallons. The spill was stopped at approximately 10:30 PM that day. The State Watch Office was called and produced incident report #2017-6411. | 08/24/2017 02:26 PM | TWA Cypress West WRF | FL |  | Adrian Brene | Environmental Compliance Coordinator | environmental@tohowater.com | (407) 944-5016 |  | Environmental Compliance Coordinator | Adrian Brene | (407) 944-5016 |  | environmental@tohowater.com | 08/24/2017 07:00 AM | 08/24/2017 10:30 AM | Osceola |  |  | 28.185992 | -81.413043 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=239
I-10 Diesel tank puncture | 20176376 | Semi truck was traveling eastbound on Interstate 10 when driver heard an object strike the bottom of the truck. He pulled the truck off the freeway at exit 136 and noticed the drivers side fuel tank leaking. The tank was ruptured with a small hole causing approximately 30 gallons of diesel fuel to spill on the ground. Emergency personnel arrived on scene. SWS Environmental was contacted to clean up spill. | 08/24/2017 02:11 PM | Ruptured fuel tank on a semi truck on I-10 east at exit 136. | FL |  | Alexander Moreira | AMG Certified Trucking | amgcertified@att.net | (832) 758-8752 |  | Owner Of the Facility | Alexander Moreira | (832) 758-8752 |  | amgcertified@att.net | 08/22/2017 10:35 PM | 08/22/2017 11:00 PM | Jackson |  |  | 30.754957 | -85.276903 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=238
Seven Springs Wastewater Treatment Facility | 20176413 | Manager phoned to report that a spill was observed at 0900 am this morning from the master lift station at the Seven Springs wastewater treatment plant @ 2850 Seven Springs Boulevard, New Port Richey, FL Upon further investigation it was found that one of the four Master station pumps was not operational (and has been removed for repair), the remaining pumps were not pumping a full capacity; causing the station to fill and subsequently discharge to the adjacent grounds. It is estiamted that 2000 gallons of wastewater was discharged in total. The area affected was contained to the treatment plant grounds, along side of the station and to an adjacent storm retention area. Maintenance was able return one pump to full capacity and pump down the station until the additional two pumps could be pulled and inspected. The discharge had ceased by 0915 am. A Vac truck is being utilized to recover any standing contents of the spill; the affected area will be limed and cleaned. | 08/24/2017 01:26 PM | Seven Springs WWTP | 2850 Seven Springs Blvd; New Port Richey FL; 34652 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 |  | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 08/24/2017 09:00 AM | 08/24/2017 09:15 AM | Pasco |  | N | 28.199458 | -82.694591 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=237
Hydraulic oil spill / Temporary Pumps / L-28 Canal | 20176412 | Temporary hydraulic pumps installed on the L-28 Canal on western perimeter of Water Conservation Area-3A pursuant to DEP Emergency Order (OGC 17-0867). Third party reported hydraulic oil sheen associated with pumps in the early afternoon on 8/23/17. Pumps were secured and absorbents booms were deployed by District upon notification as precautionary measure. Pumps are being pulled for maintenance check on 8/24/17. Regulatory reporting being performed as precautionary measure. Cause and volume of release, if any, is unknown. NRC Incident Report #1188239. | 08/24/2017 11:46 AM | L-28 Canal Temporary Pumps | N/A; Miami FL; 34141 | L-28 Canal about 9.5 miles north of Tamiami Trial in unincorporated Miami-Dade County. | Jeffrey Smith | Lead Environmental Scientist | jesmith@sfwmd.gov | (561) 682-2516 |  | Owner Of the Facility | Jeffrey Smith | (561) 682-2516 |  | jesmith@sfwmd.gov | 08/23/2017 12:00 PM | 08/23/2017 01:00 PM | Miami-Dade |  |  | 25.919205 | -80.836442 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=236
City of Largo WWRF | 20176364 | There was an internal overflow at the headworks of the WWRF; the new bar screen was blinded as washwater was not cleaning the screen and no alarms sounded. WW overflowed from the headworks, down the road, through the ditch into the stormwater retention pond onsite and contained. The plant is under construction and still under contract; cause under investigation. | 08/23/2017 03:34 PM | City of Largo WWRF | 5100 150th Ave North ; Clearwater FL; 33760 |  | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 08/21/2017 05:00 PM | 08/21/2017 05:10 PM | Pinellas |  |  | 27.907921 | -82.703624 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=235
Discovery of groundwater contamination | 20176359 | Shortly after midnight (Eastern Time) a resident reported a strong odor of gasoline on the campus of Pensacola State College in Pensacola. Caller indicated the sprinkler system was on during the night of August 21 and there was a strong smell of gasoline in the area. Campus police were notified and the fire department was called and responded to the incident. No fire hazard was identified. A nearby former gas station in the area is currently under state funded cleanup with ongoing remediation managed by DEP¿s petroleum cleanup contractor, Escambia County Department of Health. Previous releases from the gas storage tanks at the nearby gas station created a contamination plume underground. It is suspected that the contamination has migrated into the irrigation well water used in the sprinkler system at the college. DEP conducted a site visit on August 22. Preliminary field tests indicate potential petroleum in the irrigation well water. DEP collected water samples from the Pensacola State College irrigation well and another nearby irrigation well for analysis in DEP¿s lab. Both irrigation well owners have discontinued use of their wells. The community is served by a public water system and the potable supply well would not be impacted by the groundwater at this site. | 08/23/2017 01:28 PM | Pensacola State College | 1000 College Blvd.; Pensacola FL; 32504 |  | Florida Department of Environmental Protection | State of Florida | brandy.m.smith@dep.state.fl.us | (850) 595-0695 |  | Florida DEP | Danny Deen (DOH Project Manager for cleanup site | (850) 712-3722 |  | Danny.Deen@flhealth.gov | 08/22/2017 12:10 AM | 08/22/2017 10:00 AM | Escambia |  |  | 30.480572 | -87.204527 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=234
3029 S Suncoast Blvd. Homosassa FL |  | D.A.B. Construction Inc. was directional boring on the Hwy-19 project in Homosassa and drilled into the 8" force main. Locate was missed marked. Citrus County Utilities valved off force-main and turned off lift stations. The road contractor, D.A.B, had A-Able septic company clean the area using a pump truck, lime the affected area, and then D.A.B repaired the force-main. Locates on US 19 project in Homosassa will be dug up & located every 50 feet and marked. | 08/23/2017 12:18 PM | Meadowcrest Collection System | 3029 S. Suncoast Blvd.; Homosassa FL; 34446 |  | Charles Thompson | Maintenance Supervisor | Charles.Thompson@citrusbocc.com | (352) 400-0846 |  | Maintenance Supervisor | Gary Loggins | (352) 527-7650 |  | Gary.Loggins@citrusbocc.com | 08/22/2017 09:30 AM | 08/22/2017 10:00 AM | Citrus |  |  | 28.817229 | -82.57689 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=233
111 West Clay Ave Brandon, Florida 33510 | 20176371 | Hillsborough County Public Utilities Discharge Report: Date: 8/22/17 Location: 111 West Clay Ave Brandon, Florida 33510 A contractor was excavating in preparation to replace a 20-inch valve when a two-inch corporation stop failed allowing untreated waste water to flow to the neighboring property. At approximately 8:30 AM, the contractor was excavating around the 20-inch pipe line when a two-inch corporation stop failed and released approximately 16,800 gallons of raw waste water. The operations staff and contractor called in pumper truck(s) to transfer the wastewater to the Valrico Advanced Wastewater Treatment Plant and shut down the Clay Avenue pump station system (wastewater) pumps. The spill lasted for approximately four (4) hours. The construction company replaced and completed repairs to the two-inch corporation stop at approximately 1:30 PM. The wastewater pump station was turned back on and the plant resumed normal operations. Hillsborough County is completing the SIR/SSO Report for the incident. The Operation staff and Project Manager made contact with regulatory agencies as required. Regulatory Agency Notification: EPC @ Daniel Moore at approximately 9:00 AM. State Warning Point was notified @ 3:00 PM, Incident #2017-6371. FDEP left message with Erica Peck. PUD Environmental @ 8:30 AM, left message for Adam Wood. There is no immediate impact to residences or businesses. Residents with questions or concerns regarding this spill can contact Glenn Yaney with Public Utilities at (813) 448-4090 or Yaneyg@HCFLGov.net. | 08/23/2017 11:14 AM | VALRICO AWWTP - FL0040983 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | RICHARD CUMMINGS | (813) 209-3003 |  | CUMMINGSR@HILLSBOROUGHCOUNTY.ORG | 08/22/2017 08:30 AM | 08/22/2017 01:30 PM | Hillsborough |  |  | 27.944971 | -82.286028 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=232
reuse water spill on nb central blvd | 20176350 | A reuse water spill on northbound Central Blvd. on 8-21-17, approximately 15000 gallons spilled from a broken 2" fitting. The spilled reuse water flowed across road and into swale where it was absorbed into ground. No water reached any waterways or storm sewer. | 08/22/2017 10:53 AM | loxahatchee river district | 2500 jupiter park dr; jupiter FL; 33458 |  | adrian sanchez | foreman | adrian.sanchez@lrecd.org | (561) 262-3464 |  | foreman | albrey arrington | (561) 747-5700 |  | albrey@lrecd.org | 08/21/2017 12:50 PM | 08/21/2017 01:20 PM | Palm Beach |  |  | 26.895996 | -80.110992 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=231
Forest Creek LS Overflow | 20176331 | At least 1,000 gallons of raw sewage spilled from lift station #4 in Pace due to an equipment malfunction. Caller advised there was potential for the spill to have entered Legend Creek nearby, but they were unable to confirm that. Clean-up actions have been completed by the RP. | 08/21/2017 04:30 PM | Pace Water System, Inc. | 4401 Woodbine Rd.; Pace FL; 32571 |  | Rachel Lee | Utility Engineer | rlee@pacewater.org | (850) 994-5129 |  | Pace Water System Engineer | Rachel Lee | (850) 994-5129 |  | rlee@pacewater.org | 08/19/2017 04:00 PM | 08/19/2017 08:00 PM | Santa Rosa |  | N | 30.621194 | -87.16581 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=230
MPS 450 | 20176340 | Contractor’s piping connected to the force main line separated at joint above ground. The wastewater spill entered storm drains which drained to a canal. Aerators have been placed into the canal. The spill also entered the roadway and public access areas. The areas are being cleaned up with HTH and vacuum trucks. | 08/21/2017 01:40 PM | MPS 450 | 3701 N State Rd. 7; Lauderdale Lakes FL; 33319 |  | Metason Phillip | Utilities Superintendent | mphillip@broward.org | (954) 831-0829 |  | First Responder | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 08/20/2017 04:48 PM | 08/21/2017 01:50 AM | Broward | Broward | Y | 26.171532 | -80.204089 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=229
5000 Ortega Farms Blvd | 20176347 | Grease blockage in force-main caused manhole to overflow with sewer. Estimated 2000 gallons was released, recovered 2500 gallons of the spill and wash down water. No waterway affected. See https://www.jea.com/environment/environmental_incident_reporting/ for further details. | 08/21/2017 01:21 PM | 5000 Ortega Farms Blvd | 5000 Ortega Farms Blvd; Jacksonville FL; 32210 |  | Glenn Davis | Incident Response | Davige@jea.com | (904) 591-4777 |  | Incident Response | Glenn Davis | (904) 591-4777 |  | davige@jea.com | 08/19/2017 09:00 PM | 08/19/2017 10:35 PM | Duval |  | N | 30.252362 | -81.718427 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=228
2965 Chance Court | 2017315 | A sewage spill at 5:30 PM, August 18, 2017 was reported flowing from the manhole at 2965 Chance Court, Villages, Florida at an estimated 150 gpm for 45 minutes before corrections could be made. Spill flowed to a stormwater collection inlet connected to a stormwater retention area. Spill did not contaminate any state waters, recreational areas or wetlands. Signs have been placed around the perimeter of the water retention area warning residents of the potential hazard. Wastewater collection system is permitted under FLA499951. FDEP contacted by phone 3;00 PM, 8/19/2017. | 08/21/2017 11:24 AM | Central Sumter Utilities | FL |  | Russ Vaughn | Manager | russ.vaughn@ch2m.com | (352) 267-4002 |  | Manager | Russ Vaughn | (352) 267-4002 |  | russ.vaughn@ch2m.com | 08/18/2017 05:30 PM | 08/18/2017 06:15 PM | Lake |  | N | 28.860436 | -81.949396 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=227
City of Lakeland - Oleander |  | On August 21, 2017 we received a call at 6:50AM about a manhole overflowing on Oleander St. Crew arrived on site and cleared a grease blockage in the main line at 7:30AM. An estimated 450 gallons of raw sewage was released. Crews washed down and cleaned up the area. | 08/21/2017 11:04 AM | City of Lakeland NPDES Permit No. FL0039972 | 1825 Glendale Street; Lakeland FL; 33803 |  | Richard Ruede | Wastewater Collection Manager | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 08/21/2017 06:50 AM | 08/21/2017 07:30 AM | Polk |  |  | 28.046602 | -81.947651 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=226
City of Cape Canaveral 601 Thurm Blvd. Cape Canaveral, FL 32 | 20176174 | Approximately 38,700 gallons of partially treated raw sewage spilled at the City of Cape Canaveral Water Reclamation Facility due to a temporary pump failures. Caller advised the spill was contained on-site at the facility, and no waterways were affected. Clean-up actions are currently underway by hired contractor (Florida Design Contractor). The City has contracted with Florida Design Contractor to refurbish the oxidation ditch. The first anoxic basin are currently being bypassed to allow for underground pipe work. The temporary pumps Florida Design Contractor put in malfunctioned (primary & backup) causing overflow of the West anoxic basin, and flow through newly installed but incomplete/open piping. It was discovered that the primary bypass pump fan belt broke, and the backup bypass pump battery malfunctioned preventing it from starting. Once the spill was discovered the tank was isolated and Florida Design Contractor called in their pump contractor to repair the malfunctioning pumps. Florida Design Contractor has taken full responsibility for the temporary equipment malfunction/spill and cleanup. | 08/21/2017 10:35 AM | City of Cape Canaveral Water Reclamation Facility | 601 Thurm Blvd.; Cape Canaveral, Florida 32927; Cape Canaveral FL; 32927 | 528 East to the beach turn right at the first light after entering Cape Canaveral (Central Blvd). Go to the stop sign turn left on to Thurm Blvd. (601 Thurm Blvd.). WFR is on the right side of Thurm Blvd. after passing Manatee park. | June A. Clark | Waste Water System Supervisor | J.Clark@cityofcapecanaveral.org | (321) 868-1240 | 405 | Operator Of the Facility | June A. Clark | (321) 868-1240 |  | J.Clark@cityofcapecanaveral.org | 08/13/2017 08:15 PM | 08/13/2017 09:30 PM | Brevard |  |  | 28.392605 | -80.617869 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=225
Force Main Break City of West Palm Beach | 20176326 | There was a 8" Force main break at 11th st. Rosemary Ave. that ran into the storm drain nearby which runs to the Intracoastal waterway. The spill happened around 5:00PM Saturday evening and was contained around 7:00PM. The estimated spillage was 20,000 gallons with 10,000 gallons captured with 8 Vactor trucks onsite vacuuming sewer until Lift station 020 was shut off to make repairs. After repairs were made we turned the system back on and there was a onsite Contractor disinfecting contaminated area with Lime while Vactor trucks vacuuming and hosing down the area. We also had our IPP group come out and test locations around outfall where possible sewage may have entered the Intracoastal waterway located at Palm Beach Lakes Boulevard and Flagler Drive. At the testing location we set out Contaminated water warning signs as a precaution for the Public until test results come back from the lab. There are also Turbidity Barriers setting out in front of the outfalls which were placed by our Storm water Department. | 08/20/2017 01:51 PM | West Palm Beach Fl 33401 | 11th st. Rosemary Avenue; West Palm Beach FL; 33401 | Take Banyan Avenue East to Rosemary Avenue make a left at the red light head North for about a 1/2 mile to where Rosemary turns at the dead end which is 11th st. and that's the location to the east from that dead end street to the east. | Derek Johnson | Utilities Coordinator Waste Water Collections | djohnson@wpb.org | (561) 723-9190 |  | Employee at City of West Palm Beach | Charles Phoenix | (561) 722-0914 |  | cphoenix@wpb.org | 08/19/2017 05:00 PM | 08/19/2017 07:00 PM | Palm Beach |  |  | 26.723573 | -80.056647 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=224
City of Bowling Green 100yr Flood Event | 20176312 | On 8/18/2017 The City experienced a 100yr flood event in less than 2hrs. Rainfall in some areas were as high as 8-inches. Even though the city has rehabbed collection system in high I&I priority areas, it is evident there are still some issues. Our charts recorders show 600gpm coming into facility for hours, thus causing an hydraulic overload to one facility trains. Plant 1 over flowed approximately 50k-60k gallons of treated bio-solids. Spill site was contained and disinfected with lime. State watch office was notified 8/19/2017 and the incident number is 2017-6312. | 08/19/2017 12:42 PM | City of Bowling Green Wastewater Treatment Facility | 596 Lake Branch Road; Bowling Green FL; 33834 |  | Evelyn Guffey | Utility Operator | Evelyn.Guffey@Hardeecounty.net | (863) 205-6181 |  | Operator Of the Facility | Jerry Torrance | (863) 605-8919 |  | Jerry.torrance@hardeecounty.net | 08/18/2017 06:00 PM | 08/19/2017 06:00 AM | Hardee |  |  | 27.627488 | -81.816339 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=223
Private Sanitary Sewer Overflow - City of Orlando | 20176295 | At approximately 1150 AM, City of Orlando received notification that a contractor had attempted to tie into a private force main located near 828 Lake Baldwin Lane. Instead of the permitted 3" wet tap type connection on the 4" force main line, the contractor severed the line completely to install an unnaproved tee and shut off valve. Not all sources of flow were properly identified by the contractor and approximately 2000 gallons of sanitary sewer poured out of the cut pipe, overflowed the dig site and began to run into the street. The vactor truck onsite was unable to keep up with the flow and the City of Orlando Water Reclamation Division provided an additional vactor onsite to help control the flow which allowed the contractor crews to install a valve and repair the line. Once the necessary repairs were made to restore the private sanitary sewer force main, all impacted surfaces were sanitized and cleaned and 3500 gallons of water were vactored from the impacted storm drains. | 08/18/2017 07:36 PM | Mission Homes LLC | 828 Lake Baldwin Lane; Orlando FL; 32803 | SR-50 East to Lake Baldwin Ln. Turn Left on Lake Baldwin Lane. | Daniel Friedline | Public Outreach Coordinator | daniel.friedline@cityoforlando.net | (407) 246-2657 |  | City of Orlando Authorized Representative | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 08/18/2017 11:50 AM | 08/18/2017 05:15 PM | Orange |  |  | 28.555342 | -81.327336 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=222
Timber Springs Blvd & Bristol Estates Ln, Orlando, FL, 32828 | 20176292 | Field Services Division Staff discovered a failed 6 inch pvc force main. The pipe was found to have a split at the bottom. The affected areas include paved and unpaved ground on the north Right-of-way of Timber Springs Boulevard. The curb and storm water system were also affected. There is no potential risk to public health, safety or welfare at this time. The overflowed volume of wastewater was recovered from an adjacent storm water inlet box by Field Services Staff and it did not enter any nearby storm water retention ponds. | 08/18/2017 05:59 PM | Orange County Utilities - Wastewater Collection System | FL |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Engineer II | Troy E. Layton | (407) 254-9977 |  | Troy.Layton@ocfl.net | 08/18/2017 08:10 AM | 08/18/2017 09:40 AM | Orange |  |  | 28.537396 | -81.144297 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=221
BCWWS 6 Inch Force Main - LHP | 20176271 | 6 inch wastewater force main broke, due to pipe failure; estimated 250 gallons of raw sewage discharged to ground, no water body impact. Impacted soil was collected with vac-truck, and replaced with clean fill. | 08/18/2017 11:17 AM | Broward County NRWWTP Collection System | 4121 NE 22 Ave.; Lighthouse Point FL; 33064 |  | Carlos Morejon | Utilities Operations Manager | cmorejon@broward.org | (954) 831-0861 |  | Operator Of the Facility | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 08/17/2017 10:00 AM | 08/17/2017 03:00 PM | Broward |  |  | 26.282137 | -80.093156 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=220
4805 Raggedy Point Drive | 20176229 | Contractor broke 2 inch force main causing leak. Leak was isolated and repaired. Approximate volume of sewage leaked was 1360 gallons.Sewage was contained in adjacent ditch and recovered. Applied lime to wetted area and warning signs were posted. | 08/17/2017 03:13 PM | Flemin Island WWTP | 1770 Radar Road; Fleing Island FL; 32006 |  | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Wastewater Superintendent for CCUA | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 08/16/2017 04:25 PM | 08/16/2017 04:25 PM | Clay |  |  | 30.113717 | -81.695599 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=219
8104 Argyle Forest Blvd | 20176252 | Power failure caused lift station to overflow with sewer. Estimated amount released 55,000 gallons, total amount of spill contained on-site, no waterway impacted. Vacuumed sewer and applied hydrated lime to impacted area. https://www.jea.com/environment/environmental_incident_reporting/ | 08/17/2017 01:35 PM | 8104 Argyle Forest Blvd | 8104 Argyle Forest Blvd ; Jacksonville FL; 32244 |  | Glenn Davis | Incident Response | Davige@jea.com | (904) 591-4777 |  | Incident Response | Glenn Davis | (904) 591-4777 |  | davige@jea.com | 08/16/2017 05:35 PM | 08/16/2017 06:30 PM | Duval |  | N | 30.197741 | -81.807498 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=218
Brookledge fuel spill | 20176204 | Report #: 2017-6204 Status: Assigned Reported to SWO on: 8/15/2017 16:05 ET Severity: Local Incident Description: Petroleum Release This situation involves: Petroleum Spill Affected Sectors: DEP District - Northeast, DEP OER Jacksonville - Day Initial Report: Alachua County SO reports a petroleum release from a semi on I-75 SB at mile marker 380. The exact amount of the release is unknown but the semi truck holds a 100 gallon tank. No roadways are closed as a result of this incident. FHP, Alachua SO and FR are on scene responding. Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: Yes DEP callback requested: Unknown Incident Occurred: 8/15/2017 16:05 ET Most Recent Update Date/Time: 08/15/2017-16:17 ET Most Recent Update: N/A Affected Counties: Alachua Facility Name or Description: I-75 380S MILE MARKER Incident Location: Address: City: I-75 Zip: USNG: 17RLN6870872751 Coordinates: Lat: 29.57763, Long: -82.3555 | 08/16/2017 04:02 PM | Brookledge | I-75 southbound rest area mile marker 381; Gainesville FL; 32608 |  | Alan Chandler | manager | alan.chandler@aagenvironmental.com | (352) 472-7295 |  | cleanup contractor | Alan Chandler | (352) 472-7295 |  | alan.chandler@aagenvironmental.com | 08/15/2017 04:00 PM | 08/15/2017 08:00 PM | Alachua |  |  | 29.595568 | -82.366855 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=217
HWY 31 Broken ARV | 20176206 | Broken ARV on HWY 31 & Lana Cir. Incident occurred 1530 , Estimated 3,700 gallons of raw influent was leaked into the ditch. Zero recovery, affected area was limed for disinfection. | 08/16/2017 11:02 AM | Desoto County Regional WWTP | 7728 S.E. HWY 31, ; Arcadia FL; 34266 |  | Alex Shannon | WW Systems Supervisor | a.shannon@desotobocc.com | (863) 491-7500 |  | Operator Of the Facility | Eddie Miller | (863) 491-7500 |  | e.miller@desotobocc.com | 08/15/2017 03:30 PM | 08/15/2017 04:00 PM | DeSoto |  | N | 27.169071 | -81.823497 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=216
Abnormal Event Report 8-15-17 W Gulf to Lake Hwy and 491 |  | On August 25, 2017, J.W.J. Construction was directional boring under S. Lecanto Hwy (aka 491) and drilled into the 6" force main. Approximately 200-300 gallons of sewage spilled into the stormwater drainage area where it was contained. Citrus County Utilities turned off the affiliated lift station. The area was cleaned with a pump truck and the affected area was limed. In future, when locating pipe in roadways that cannot be dug up to verify location, Citrus County Utilities will use ground penetrating radar to locates. Not required to report to SWO. | 08/16/2017 09:41 AM | Meadowcrest WWTP & Collection System | SE corner of intersection of W. Gulf to Lake Hwy and 491; Lecanto FL; 34461 |  | Charles Thompson | Maintenance Supervisor | Charles.Thompson@citrusbocc.com | (352) 400-0846 |  | Maintenance Supervisor | Gary Loggins | (352) 527-7653 |  | Gary.Loggins@citrusbocc.com | 08/15/2017 02:00 PM | 08/15/2017 02:10 PM | Citrus |  |  | 28.851647 | -82.487782 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=215
Wastewater Overflow at 8401 North Armenia Ave. | 20176192 | On August 15, 2017, the City of Tampa¿s Wastewater Department personnel were doing a follow up investigation of a force main blockage at 8401 N. Armenia Ave. When personnel arrived at the site they found an active wastewater overflow at the location due to a broken force main. The overflow was discharging into a storm drain adjacent to the break. Upstream pumping stations were shut down and the overflow stopped. Approximately 5000 gallons discharged into the storm drain. Repairs to force main have been completed and pump stations returned to normal operation. | 08/16/2017 07:28 AM | City of Tampa Wastewater Department | 2545 Guy N. Verger Blvd.; Tampa FL; 33605 |  | Jeff Hilton, P.E. | Wastewater Planning Head | jeffrey.hilton@tampagov.net | (813) 274-7844 |  | Wastewater Planning Head | Eric Weiss | (813) 274-8039 |  | eric.weiss@tampagov.net | 08/15/2017 07:30 AM | 08/15/2017 10:45 AM | Hillsborough |  |  | 28.025606 | -82.484156 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=214
SWO #2017-6202 Ascend Performance Materials | 20176202 | Ascend experienced a 580 gallon domestic wastewater release due to excessive rainfall resulting in the overflow. The overflow entered Eagle's Nest Creek which ultimately discharges into Eagle's Nest Swamp and Escambia River. The overflow occurred from 14:48 until 15:17 (29 minutes) | 08/15/2017 04:01 PM | Ascend Performance Materials | 3000 Old Chemstrand Road; Cantonment FL; 32533 |  | Shannon Nettles | Environmental Superintendent | stnett@ascendmaterials.com | (850) 968-7206 |  | Environmental Superintendent | Shannon Nettles | (850) 968-7206 |  | stnett@ascendmaterials.com | 08/14/2017 02:45 PM | 08/14/2017 03:45 PM | Escambia |  |  | 30.774097 | -87.371484 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=213
10991 Harts Road SSO | 20176195 | 6" forcemain struck by crew excavating the area. Wastewater contained in work pit. Line has been repaired. 16,800 gallons of wastewater was vacuumed up and lime was applied to the impacted area. Signs posted. See https://www.jea.com/environment/environmental_incident_reporting/ | 08/15/2017 01:38 PM | District II collection system | 10991 Harts Road; Jacksonville FL; 32218 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/15/2017 10:20 AM | 08/15/2017 01:05 PM | Duval |  | N | 30.433989 | -81.658818 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=212
East Water Reclamation Facility - 1621 S. Alafaya Trail, Orl | 20176179 | During excavation work, a contractor broke two sodium hypochlorite feed lines to the Phase 2 chlorine contact chambers causing fluctuating total chlorine residual concentrations. The total chlorine residual dropped below 1.1 mg/L. This caused the automatic shut off of the Phase-2 effluent pumps to the PAR storage tank. All flow was automatically diverted to the Phase 3 effluent pump station via gravity overflow. Due to high peak flows entering the plant, the high volume of water caused the chlorine contact chamber to overflow approximately 3500 gallons of chlorinated effluent. Approximately, 300 gallons of sodium hypochlorite leaked into the ground and was contained on-site. The majority of the overflow spilled onto surrounding grass areas and flowed to an onsite storm water swale. There is minimal to no risk to public health, safety and welfare. A recovery of 6,000 gallons was made via the use of a vactor truck. The sodium hypochlorite that leaked oxidized and the affected soil will be excavated and properly disposed of. National Response Center notified on 8-15-2017 at 11:48 AM Incident Report # 1187281 | 08/15/2017 01:19 PM | East Water Reclamation Facility | 1621 S. Alafaya Trail, Orlando FL 32828; Orlando FL; 32828 |  | Eduardo C. Hernandez | Engineer II | eduardo.hernandez@ocfl.net | (407) 836-6839 |  | Engineer II | Mark Robinson | (407) 254-6791 |  | Mark.Robinson@ocfl.net | 08/14/2017 08:30 PM | 08/14/2017 08:45 PM | Orange |  | N | 28.522632 | -81.203167 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=211
Gulf Harbors / Lindricks Services | 20176187 | Incident address: 4453 Marine Parkway Emergency call received to sewer spilling on Saturday 08/12/2017 @ 0833 am. Maintenance technician responded to site and met with customer who showed him a crack in the road with a milky substance discharging. He could not determine it was sewer by the appearance, drilling by a contractor for power conduit was occurring down the street. Additional follow up was performed 08/14/2017 and it was determined that there was a sewer line break causing sewage to discharge out of the road. Technicians were able to turn off station station upstream of the crack in the road, and the discharge was stopped. A hauler is currently contracted to haul the upstream lift station when needed to maintain the collection system, until such time that the sewer break can be located and repaired. The discharge was stopped by Noon on 08/14/2017; crews are still attempting to locate the break to complete the repair. The spill contents did extend through to the adjacent yard and discharge to a canal to the Gulf of Mexico. It is estimated the volume of discharge was between 950-1200 gallons, and was occurring intermittently with the lift station pumps at the upstream station. Fecal samples are being collected up and down stream of the point of discharge | 08/15/2017 09:04 AM | Gulf Harbors/Lindrick Services | 4453 Marine Parkway,; New Port Richey FL; 34654 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 | 207 | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 08/12/2017 08:30 AM | 08/14/2017 12:00 PM | Pasco |  | N | 28.237302 | -82.73963 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=210
Sawgrass Dr West | 20176186 | A contractor hit a sewer line. The spill made its way to a stormwater pond on sawgrass drive. The line was repaired, site cleaned up and limed, pond posted with warning signs and water quality sampling has begun. Stormwater pond fecal coliform results have been below 800 CFU limits since 8/15 | 08/15/2017 08:37 AM | Sawgrass WWTF | 10047 Sawgrass Dr West; Ponte Vedra Beach FL; 32082 |  | Tony Cubbedge | Env Div Mgr | twcubbedge@sjcfl.us | (904) 209-2620 |  | Env Div Mgr for Utility | Tony Cubbedge | (904) 209-2620 |  | twcubbedge@sjcfl.us | 08/14/2017 05:30 PM | 08/14/2017 07:30 PM | St. Johns |  | N | 30.185146 | -81.375852 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=209
Sanitary Sewer Overflow | 20176183 | Sewer Spill of Quantity to be Determined | 08/15/2017 08:26 AM | CWRF | 2980 Old Chemstrand Rd ; Pensacola FL; 32533 |  | Catherine Matthews | Communications Coordinator 11 | scada.operations@ecua.fl.gov | (850) 969-6500 | 6500 | Operator Of the Facility | Doug Gibson | (850) 969-6513 |  | Douglas.Gibson@ecua.fl.gov | 08/14/2017 05:35 PM | 08/14/2017 08:20 PM | Escambia |  |  | 30.519075 | -87.176941 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=208
City of Bowling Green Treated Effluent Main Line Break | 20176087 | City of Bowling Green had an 8" treated effluent line break at wastewater facility on 8/9/17. Approximately 150k gallons were spilled but contained on-site. Affected area was disinfected by lime. Repairs were made and completed on 8/10/17. | 08/14/2017 02:53 PM | City of Bowling Green Wastewater Treatment Facility | 596 Lake Branch Road; Bowling Green FL; 33834 - 608 |  | Evelyn Guffey | Utility Operator | Evelyn.Guffey@hardeecounty.net | (863) 773-3465 | 8502 | Operator Of the Facility | Jerry Torrance | (863) 605-8919 |  | Jerry.torrance@hardeecounty.net | 08/09/2017 06:00 PM | 08/10/2017 08:00 AM | Hardee |  |  | 27.628664 | -81.817143 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=207
Fairway Country Club | 20176161 | Operator arrived to the wastewater site at 0545 am this morning (08132017) and found and overflow of solids had occured onto the adjacent parking lot grounds. Estimated discharge 5000 gallons. No discharge was occurring upon arrival. Upon further review it was found that the area of the facility had received 3.5" of rain through the night increasing the hydraulics at the treatment plant and subsenquently causing the effluent filters to overflow to the back wash lift station. The rate in which the flow was being received at the back wash station overwhelmed the station which created an overflow of the backwash water and solids to discharge. The operator was able to hose down the affected area and clean up the spill by directing contents to plant drain, which re-enters the wastewater treatment plant | 08/13/2017 08:05 PM | Fairways Country Club | 14205 Colonial Drive; Orlando FL; 32826 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 | 207 | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 08/12/2017 10:00 PM | 08/13/2017 05:45 AM | Orange |  |  | 28.573523 | -81.173702 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=206
Condenser Water Release | 20176152 | On 08/13/17, at approximately 00:03 while performing routine maintenance activities, a plant operator noticed circulating water from the cooling pond discharging out of a broken 2-inch port on one of the condenser cooling water heat exchangers (waterbox). By 01:01 the waterbox was isolated and the leak stopped. Upon investigation, the station Environmental Specialist determined that 3,000 gallons or less of cooling pond water was released to the ground. At 03:16, a notification was made to the FL State Watch Office. This spill did not impact Waters of the U.S. The cooling pond water is not of a hazardous nature. | 08/13/2017 07:04 PM | Duke Energy Hines Energy Complex | 7700 County Road 555; Bartow FL; 33830 |  | Tommy Oneal | Lead Environmental Specialist | tommy.oneal@duke-energy.com | (813) 422-4941 |  | Station Environmental Field Support | Ana Gibbs | (888) 266-3853 |  | ana.gibbs@duke-energy.com | 08/13/2017 12:05 AM | 08/13/2017 01:05 AM | Polk |  |  | 27.789028 | -81.871202 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=205
UF Power Cogeneration Area | 20176148 | Status: Closed Assigned To: DEP Reported to SWO on: 8/12/2017 20:46 ET Severity: Local Incident Description: Diesel Fuel Release This situation involves: Petroleum Spill Affected Sectors: DEP District - Northeast, DEP OER Jacksonville On-Call Initial Report: Alachua County 911 reports a 1,000 gallon diesel fuel release at the location below in Gainesville due to a leak from a generator on the University of Florida campus. The release is on-going and has entered a storm drain that flows into a stream, potentially flowing into Lake Alice. University of Florida PD, a hazmat team and UF's Health and Safety Officer are on scene. Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: Yes DEP callback requested: Unknown Incident Occurred: 8/12/2017 20:11 ET Most Recent Update Date/Time: 08/12/2017-21:52 ET Most Recent Update: N/A Affected Counties: Alachua Facility Name or Description: Incident Location: Address: 1281 Newelle Rd. City: Gainesville Coordinates: Lat: 29.640677, Long: -82.34228 | 08/13/2017 02:53 PM | UF Power Cogeneration Area | 1200 Newell Road; Gainesville FL; 32610 |  | Alan Chandler | manager | alan.chandler@aagenvironmental.com | (352) 472-7295 |  | cleanup company | Alan Chandler | (352) 472-7295 |  | alan.chandler@aagenvironmental.com | 08/12/2017 09:25 PM |  | Alachua |  |  | 29.64058 | -82.346513 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=204
wastewater overflow at Chelsea St. and North 22nd St. | 20176147 | On August 12, 2017, Wastewater Department personnel received notification of an overflow at the intersection of 22nd Street and Chelsea Street. Personnel responded to the site and found wastewater overflowing from a broken air release valve on a force main. The wastewater flowed into storm drain that discharges into a retention pond adjacent to the break. Technicians were able to expose the broken pipe and close a valve between the broken pipe and the force main which stopped the overflow. Approximately 7500 gallons discharged from the broken pipe. | 08/13/2017 12:31 PM | City Of Tampa Wastewater Department | 2545 Guy Verger Blvd; Tampa FL; 33605 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastewater Department | Eric Weiss | (813) 274-8039 |  | Eric.weiss@tampagov.net | 08/12/2017 02:25 PM | 08/12/2017 07:00 PM | Hillsborough |  |  | 27.985309 | -82.434913 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=203
wastewater overflow at Chelsea St. and North 22nd St. | 20176147 | On August 12, 2017, Wastewater Department personnel received notification of an overflow at the intersection of 22nd Street and Chelsea Street. Personnel responded to the site and found wastewater overflowing from a broken air release valve on a force main. The wastewater flowed into storm drain that discharges into a retention pond adjacent to the break. Technicians were able to expose the broken pipe and close a valve between the broken pipe and the force main which stopped the overflow. Approximately 7500 gallons discharged from the broken pipe. | 08/13/2017 12:31 PM | City Of Tampa Wastewater Department | 2545 Guy Verger Blvd; Tampa FL; 33605 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastewater Department | Eric Weiss | (813) 274-8039 |  | Eric.weiss@tampagov.net | 08/12/2017 02:25 PM | 08/12/2017 07:00 PM | Hillsborough |  |  | 27.985309 | -82.434913 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=202
UF Health Shands, A18 |  | On August 13, 2017, approximately 7:30 pm there was a release of 400 gallons diesel fuel into a storm drain. This occurred from a malfunction of an auto fill to a day tank from the main storage tank that feeds a generator. The storm drain leads to a near by creek that feeds Lake Alice. Gainesville Fire and Rescue responded immediately and AAG Environmental was called at 7:45 pm and responded within 45 minutes and assumed clean up operations. Chris Gilbert Alachua County DEP was on scene and review the event and the plans for clean up. | 08/13/2017 02:13 AM | Shands Teaching Hospital | 1600 SW Archer Road; Gainesville, Florida 32610 FL; 32610 |  | Christopher J. Leavitt | Safety Officer | leavic@shands.ufl.edu | (352) 594-4615 |  | Safety Officer | Christopher J. Leavitt | (352) 594-4615 |  | leavic@shands.ufl.edu | 08/13/2017 01:25 AM |  | Alachua |  |  | 29.641806 | -82.34092 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=201
CLEARWATER NORTHEAST WRF - FL0128937 | 20176135 | ON AUGUST12, 2017 FROM 9:21 AM TILL 9:25 AM THE CHLORINE RESIDUAL DROPPED BELOW THE STATE REQUIRED MINIMUM FOR FOUR MINUTES CAUSING 270,000 GALLONS TO BE RELEASED TO THE RECLAIM STORAGE TANK DUE TO A BLOCKAGE IN THE CHLORINE FEED LINE. THE STAFF PUT THE PLANT INTO REJECT AND REPAIRS WERE COMPLETED AT 10:45 AM. THIS IS AN ISOLATED INCIDENT AND WE ARE MAKING THE NECESSARY ADJUSTMENTS TO MINIMIZE THE POSSIBILITY OF A REOCCURRENCE. | 08/12/2017 03:56 PM | City of Clearwater Northeast Water Reclamation Facility | 3290 sr 580 Clearwater Florida 33761; Clearwater FL; 33761 |  | Ron Nelson | Chief Operator | ron.nelson@myclearwater.com | (727) 224-7691 |  | Chief Operator Marshall Street Facility | Jason Jennings | (727) 224-7477 |  | jason.jennings@myclearwater.com | 08/12/2017 09:20 AM | 08/12/2017 09:25 AM | Pinellas |  | N | 28.030758 | -82.704657 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=200
Yankee Lake WRF reclaimed water spill | 20176136 | PVC fitting on the facility irrigation system broke causing a 9200 gallon reclaimed water spill. Reclaimed water did not enter into any surface or storm water systems. | 08/12/2017 02:36 PM | Yankee Lake WRF | 501 Yankee Lake Road; Sanford FL; 32771 |  | David Engstrom | Chief Wastewater Operator | DEngstrom@seminolecountyfl.gov | (407) 665-2840 |  | Operator Of the Facility | David Engstrom | (407) 665-2840 |  | DEngstrom@seminolecountyfl.gov | 08/12/2017 02:28 PM | 08/12/2017 02:30 PM | Seminole |  |  | 28.827379 | -81.395235 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=199
SWO #2017-6084 2851 W Prospect Rd | 20176084 | Status: Closed Assigned To: DEP / Bridjette Bucell Reported to SWO on: 8/10/2017 11:33 ET Severity: Local Incident Description: Wastewater Release This situation involves: Wastewater or Effluent Release Affected Sectors: DEP District - Southeast, DEP OER West Palm - Day Initial Report: A private citizen called to report an ongoing wastewater overflow at the incident address. An unknown amount of raw sewage has been overflowing from several manholes on her street and entering nearby storm drains since last night. No response/clean-up reported has been taken. Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: Yes DEP callback requested: Yes Contact: On-Scene Contact Incident Occurred: 8/10/2017 11:33 ET Affected Counties: Broward Incident Location: Address: 2851 W Prospect Road City: Ft. Lauderdale Coordinates: Lat: 26.191498, Long: -80.18244 Reporting Party: Name: Collettee Quimones, Private Citizen ¦Call Back Number 1: 9545495988 Name of System: City of Ft. Lauderdale Pump Station Type of system: Unknown Release occurred from a: Manhole Type of wastewater: Raw Sewage Release enter a storm water system: Yes Storm drain discharges: Tamarac Park Pond Notification 08/10/2017-12:28 / DEM-Johnson | 08/11/2017 04:21 PM | E-8 Lift Station - Tuscan Villas | 2851 W PROSPECT RD, ; Fort Lauderdale FL; 33309 |  | Lawrence Teich | Environmental Resource Supervisor | lteich@fortlauderdale.gov | (954) 828-7844 |  | Regulatory Compliance for the Faclility | Lawrence Teich | (954) 828-7844 |  | lteich@fortlauderdale.gov | 08/09/2017 08:45 AM | 08/10/2017 10:55 PM | Broward |  |  | 26.191899 | -80.182206 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=198
US-1 MM 110.5 Fuel Spill | 20176116 | Discharge of approximately 150 gallons of fuel to the roadway, shoulder, and grassy swale as the result of an accident from a commercial vehicle | 08/11/2017 03:52 PM | US-1 | MM 110.5 FL |  | Michael Miller | Sr Environmental Scientist | Michael.Miller@dot.state.fl.us | (305) 796-5808 |  | Consultant for Facility Owner (FDOT) | Michael | (305) 796-5808 |  | michael.miller@dot.state.fl.us | 08/11/2017 12:45 PM |  | Monroe |  |  | 25.213415 | -80.425635 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=197
Manila Bay Drive. Orlando, FL 32821 | 20176117 | A contractor struck reclaim water main RWPM118703 while performing directional drilling across Gateway Avenue. A volume of 13,000 gallons of reclaim water overflowed and affected unpaved ground on the west side right-of-way of Gateway Avenue. There is no potential risk to public health, safety or welfare at this time. The overflowed volume of reclaim water was completely absorbed into the ground and did not enter any nearby storm drains or ponds. | 08/11/2017 02:45 PM | Orange County Reclaim Water System | FL |  | Eduardo C. Hernandez | Engineer II | eduardo.hernandez@ocfl.net | (407) 836-6839 |  | Engineer II | Troy Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 08/10/2017 04:10 PM | 08/10/2017 05:10 PM | Orange |  |  | 28.415793 | -81.449143 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=196
McLane Transportation | 20176104 | Reported to SWO on: 8/11/2017 06:31 ET Severity: Local Incident Description: Diesel Spill This situation involves: Petroleum Spill Affected Sectors: DEP District - South, DEP OER Ft. Myers On-Call Initial Report: 300 gallons of diesel spilled to the roadway and shoulder of I-75 in the Sarasota area due to a punctured fuel tank of a tractor-trailer. No waterways or storm drains affected. Local fire department is on scene. No clean-up actions reported. Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: Yes DEP callback requested: No Incident Occurred: 8/11/2017 05:22 ET Most Recent Update Date/Time: 08/11/2017-06:37 ET Most Recent Update: N/A Affected Counties: Sarasota Facility Name or Description: I-75 200S MILE MARKER Incident Location: Address: City: I-75 Zip: USNG: 17RLL5751408126 2 Coordinates: Lat: 27.18846, Long: -82.43844 | 08/11/2017 01:54 PM | None | I-75 at mile marker 200; Osprey FL; 34229 |  | Alan Chandler | manager | alan.chandler@aagenvironmental.com | (352) 472-7295 |  | cleanup contractor | Alan Chandler | (352) 472-7295 |  | alan.chandler@aagenvironmental.com | 08/11/2017 06:30 AM | 08/11/2017 12:40 PM | Sarasota |  |  | 27.191141 | -82.439146 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=195
Eagle Pines Apartments Lift Station | 20176089 | On 8/9/17 we became aware that both pumps at the lift station had evidently failed resulting in the collection vault overflowing. The vault was immediately pumped by a septic tank company and repairs to the pumps begun. The system has two pumps. One is the primary, with the second pump designed to kick in if the first pump fails. It appears due to the impellers of the pumps being blocked with various items that should not have been in the sewer, both pumps had failed. On 8/10/17 one pump was successfully repaired and returned to service. Repairs are underway on the second pump and it is hoped to be back on line 8/11/17. At the direction of DEP, lime was applied to the area surrounding the lift station. At this time the station is operating properly as one pump is adequate for normal operations. | 08/11/2017 11:59 AM | Eagle Pines Apartments/Condos | 445 Appleyard Drive; Tallahassee FL 32304; Tallahassee FL; 32304 | Directly across from Tallahassee Community College. Appleyard Drive runs between Pensacola St and W. Tenn St | Barry L Bumgarner | Managing Member | Barry@phoenixsouth.com | (850) 566-9855 |  | Owner Of the Facility | Barry L Bumgarner | (850) 566-9855 |  | Barry@phoenixsouth.com | 08/09/2017 02:10 PM | 08/10/2017 03:15 PM | Leon |  |  | 30.444614 | -84.337402 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=194
Escambia / Wastewater Release/Lee & E Streets | 20175702 | Approximately 150 gallons of raw sewage overflowed from a manhole and entered a nearby storm drain in Pensacola. No other waterways were affected. | 08/11/2017 11:48 AM | Emerald Coast Utility Authority | FL |  | Robert Gordon | ECUA | Robert.Gordon@ecua.fl.gov | (850) 969-6500 |  | Operator Of the Facility | Robert Gordon | (850) 969-6500 |  | Robert.Gordon@ecua.fl.gov | 07/29/2017 01:00 PM | 07/29/2017 02:00 PM | Escambia |  |  | 30.42651 | -87.229732 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=193
wastewater overflow at 19440 Bruce B. Downs Blvd | 20176066 | On August 9, 2017, the City of Tampa¿s Wastewater Department became aware of a wastewater overflow at 19440 Bruce B. Downs Blvd. The overflow occurred when a Hillsborough County contractor was trying to relocate a valve to provide a connection on City¿s force main for a Hillsborough County pumping station. The contractor believed the section of pipe where the valve was located was inactive and removed the valve. When the valve was removed wastewater discharged from pipeline into the excavated area around the valve. It was determined that an upstream valve was partially open which allowed wastewater to discharge from the pipeline. The contractor located the upstream valve and closed it which stopped the overflow. The wastewater that discharged was contained within the excavated area and vactor trucks were used to return the wastewater to the City¿s collection system. | 08/10/2017 08:56 PM | City Of Tampa Wastewater Department | 2545 Guy Verger Blvd; Tampa FL; 33602 |  | Charlie Lynch | Chief Engineer Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer for Wastewater Department | Eric Weiss | (813) 274-8039 |  | Eric.weiss@tampagov.net | 08/09/2017 12:30 PM | 08/09/2017 02:00 PM | Hillsborough |  |  | 28.151587 | -82.353652 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=192
OCWS Sanitary Sewer Overflow - Bay Dr. Nieville | 20176096 | This afternoon a contractor hit and ruptured a 4¿ sanitary sewer force main. The incident occurred at the intersection of Bay Drive and Ward Cove Drive in unincorporated Niceville. An estimated 6,000 gallons of wastewater flowed south overland (sidewalk) on the west side of the Bay Drive right-of-way, until it entered a storm drain at the intersection of Bay Drive and the southern entrance of Marina Cove Drive. This storm drain discharges into unnamed wetlands on the west side of Bay Drive between Marina Cove Drive and Lido Circle West. These wetlands ultimately discharge into Choctawhatchee Bay. OCWS crews have repaired the force main and have completed cleanup/disinfection of the affected areas | 08/10/2017 06:11 PM | Okaloosa Coounty Water and Sewer | 1804 Lewis Turner Blvd. Suite 300; Fort Walton Beach FL; 32547 |  | Darren Alford | Wastewater Operations Manager | dlalford@co.okaloosa.fl.us | (850) 651-7133 |  | Operator Of the Facility | Mark Wise | (850) 651-7171 |  | mwise@co.okaloosa.fl.us | 08/10/2017 12:30 PM | 08/10/2017 02:30 PM | Okaloosa |  |  | 30.488189 | -86.450179 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=191
BCWWS 6inch Force Main Break | 20176093 | Wastewater force main broke, due to a pipe failure. Estimated 800 gallons discharged to ground, no water body impact. Discharge was collected with vac-truck, recovered 500 gallons; remove soil and replace with clean fill. | 08/10/2017 04:47 PM | Broward County NRWWTP Collection System | 3230 SW 40 Avenue; West Park FL |  | Mike Kelly | Utility Superintendent | mikelly@broward.org | (954) 831-0821 |  | Operator Of the Facility | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 08/10/2017 09:30 AM | 08/10/2017 12:30 PM | Broward |  |  | 25.981281 | -80.183015 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=190
SSO 08/08/2017 BT |  | The Breakaway Trails Lift Station level probe had ragged up and pumps did not turn on. Approximately 50 gallons of SSO went on the surrounding ground and area was raised with potable water. Probe was cleaned and lift station is fully operational | 08/10/2017 11:52 AM | City of Ormond Beach WWTP | 550 N Orchard St; Ormond Beach FL; 32174 |  | Sammy Butler Sr | Chief Plant Operator | butler@ormondbeach.org | (386) 676-3592 |  | Operator Of the Facility | Sammy Butler Sr | (386) 676-3592 |  | butler@ormondbeach.org | 08/08/2017 09:30 AM | 08/08/2017 10:15 AM | Volusia |  |  | 29.239387 | -81.279047 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=189
SSO 08/08/2017 BT |  | The Breakaway Trails Lift Station level probe had ragged up and pumps did not turn on. Approximately 50 gallons of SSO went on the surrounding ground and area was raised with potable water. Probe was cleaned and lift station is fully operational | 08/10/2017 11:52 AM | City of Ormond Beach WWTP | 550 N Orchard St; Ormond Beach FL; 32174 |  | Sammy Butler Sr | Chief Plant Operator | butler@ormondbeach.org | (386) 676-3592 |  | Operator Of the Facility | Sammy Butler Sr | (386) 676-3592 |  | butler@ormondbeach.org | 08/08/2017 09:30 AM | 08/08/2017 10:15 AM | Volusia |  |  | 29.239387 | -81.279047 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=188
Palm Beach co SRWRF Secondary Effluent Spill FL0041424 | 20176079 | On August 9, 2017, at approximately 2:30 PM Palm Beach Co Southern Region Water Reclamations Facility suffered a network/Programmable Logic controller communication failure. This failure failed all effluent pumps and transfer pumps. All pumps then had to be started locally at the effluent pump station by operations staff. By the time these pumps were started and up to speed the wet well had overflowed approx. 200 thousand gallons of treated effluent into the storm water ponds. The duration of the overflow was 15 minutes. (2:45 to 3:00 PM. The treated effluent was contained in the storm water pond (onsite) and there was no overflow into the adjacent canals, Chlorine residual was approximately .9 PPM for the duration. The cause of the network failure is unknown, and continued efforts or being made to solve and correct the problem. | 08/10/2017 11:20 AM | Southern Region Water Reclamation Facility | 12751 Hagen Ranch Rd ; Boynton Beach FL; 33437 |  | Rex Mcclung | Superintendent | rwmcclung@pbcwater.com | (561) 381-5307 |  | Operator Of the Facility | Rex Mcclung | (561) 381-5307 |  | rwmcclung@pbcwater.com | 08/09/2017 02:45 PM | 08/09/2017 03:00 PM | Palm Beach |  |  | 26.487374 | -80.168659 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=187
Main Gate backup |  | Less than 20 gallons of wastewater backed up into a building when the lift station lost power. Transformer to lift station was replaced and lift station is functioning now. | 08/10/2017 09:00 AM | Main Gate | 240 Stenstrom Road; Wauchula FL; 33873 | Once in Wauchula, go south on US Hwy 17 to Stenstrom Road. Turn right and head west on Strenstrom. Location will be on the right. | Olivia Minshew | Assistant City Manager | ominshew@cityofwauchula.com | (863) 773-9193 |  | Owner of public utility | Andy Maddox | (863) 781-1976 |  | andy@cityofwauchula.com | 08/09/2017 02:00 PM | 08/09/2017 05:00 PM | Hardee |  |  | 27.533421 | -81.812744 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=186
Sanitary Sewer Overflow | 20176070 | SEWAGE SPILL OF QUANTITY TO BE DETERMINED | 08/09/2017 08:47 PM | Central WRF | FL; 32571 |  | Nicholas Ellis | Communications Coordinator | nicholas.ellis@ecua.fl.gov | (850) 969-6500 |  | Owner Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/09/2017 03:30 AM |  | Escambia |  |  | 30.390815 | -87.25398 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=185
ARV | 20176053 | Corroded ARV had been leaking. Call came in about raw sewage odor in the morning. Leaking air release valve was found near location of call approximately 12:45pm. | 08/09/2017 03:28 PM | Air Release Valve | 23851 Amalfi Coast Rd.; Estero FL; 34135 | From Imperial Parkway and Coconut Road travel South about 2000 ft. Incident occurred about 50 feet East of Roadway | Andy Koebel | Director of Operations | akoebel@bsu.us | (239) 992-0711 |  | Operator Of the Facility | Andy Koebel | (239) 992-0711 |  | akoebel@bsu.us | 08/09/2017 12:45 PM | 08/09/2017 02:30 PM | Lee |  |  | 26.390619 | -81.78364 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=184
Reclaimed Water Line - 16th St. | 20176042 | A contractor made a cut into a live reclaimed water line by mistake, causing approximately 3,780 gallons of reclaimed water to spray out on to the ground and street. The majority of the reclaimed water was contained in the immediate area and either soaked into the ground or was spread across the roadway by traffic. It is estimated that less than 500 gallons actually made it to the closest storm drain. Pipe repairs were made and the leak stopped. | 08/09/2017 01:32 PM | City of St. Petersburg - Reclaimed Water System | 1045 16th St. S; St. Petersburg FL; 33705 |  | Frank Niles | Water Reclamation Facility Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person making the notification. | Robert Labrie | (727) 892-5621 |  | robert.labrie@stpete.org | 08/08/2017 04:45 PM | 08/08/2017 07:45 PM | Pinellas |  |  | 27.759832 | -82.654758 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=183
Weems and Sons Logging | 20176020 | Severity: Local Incident Description: Diesel Fuel Release This situation involves: Petroleum Spill Affected Sectors: DEP District - Northeast, DEP OER Jacksonville - Day Initial Report: AAG Environmental reported a diesel fuel release of 80 gallons due to a vehicle accident on SR 24. The release was contained and cleanup actions have been taken. The reporting party is plans to remove the impacted soil. Injuries: Unknown Fatalities (Unconfirmed by State Medical Examiner): Unknown Environmental impact: Unknown Incident Occurred: 7/25/2017 14:41 ET Most Recent Update Date/Time: 08/08/2017-16:40 ET Most Recent Update: N/A Affected Counties: Levy Facility Name or Description: SR 24 Incident Location: Lat: 29.3663, Long: -82.7242 Coordinates: Lat: 29.3663, Long: -82.7242 | 08/09/2017 09:48 AM | Shoulder of SR 24 | between Bronson and Otter Creek; Bronson FL; 32621 | on SR 24 between Bronson and Otter Creek | Alan Chandler | responder | alan.chandler@aagenvironmental.com | (352) 472-7295 |  | responder | Alan Chandler | (352) 472-7295 |  | alan.chandler@aagenvironmental.com | 07/25/2017 02:20 PM | 07/25/2017 06:10 PM | Levy |  |  | 29.372296 | -82.719326 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=182
8/7/17 Oil Sheen Oberved on Alafia River Near Mosaic |  | An oil sheen of approximately 100 by 200 feet was observed on the Alafia River, near the maritime operations at Mosaic Fertilizer's Riverview Facility. Activities at the site are not known to have caused the sheen. In the absence of a responsible party reporting the incident to the State Watch Office and the National Response Center, Mosaic Fertilizer did so. | 08/08/2017 06:00 PM | Mosaic Fertilizer, LLC | 8813 US Hwy 41 S; Riverview FL; 33578 |  | Dharma Ramos | EHS Manager | dharma.ramos@mosaicco.com | (813) 671-6369 |  | Operator Of the Facility | Nichelle Foster | (813) 500-6322 |  | nichelle.foster@mosaicco.com | 08/07/2017 05:45 PM | 08/07/2017 06:00 PM | Hillsborough |  |  | 27.856718 | -82.392533 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=181
DWU WWTP | 20176025 | At about 1:18am this morning (8/8) for about 11 minutes, DWU had an overflow of two effluent splitter boxes. The water that spilled was treated for Part IV Reclaimed water, but at the time of overflow the water was being rejected, rather than going to our RIBs. During this time chlorine residuals were above 1.0mg/L. This treated Part IV reclaimed water was contained on site. There was about 3,400 gallons believed to have overflowed. No reclaimed water entered any water bodies. | 08/08/2017 05:53 PM | Destin Water Users Wastewater Treatment Plant | 14 Industrial Park Lane; Destin FL; 32541 | End of Industrial Park Lane, off Airport Road | Monica Autrey | Operations Manager | mautrey@dwuinc.com | (850) 699-3665 |  | Operator Of the Facility | Lockwood Wernet | (850) 200-2028 |  | lwernet@dwuinc.com | 08/08/2017 01:15 AM | 08/08/2017 01:30 AM | Okaloosa |  |  | 30.394168 | -86.478579 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=180
Sanitary Sewer Overflow | 20176023 | A surveying company installed a rebar stake, hitting the City's 4" force main. City crews responded, repaired the force main and cleaned up the affected area. Approximately 4,320 gallons spilled with 3,600 gallons recovered. Estimate 720 gallons entered Robinson Creek via nearby storm drain. | 08/08/2017 05:41 PM | Residential | 29 Oak Street; St. Augustine FL; 32084 |  | Glabra Skipp | Environmental Compliance Analyst | gskipp@citystaug.com | (904) 825-1055 |  | Environmental Compliance Analyst | Glabra Skipp | (904) 825-1055 |  | gskipp@citystaug.com | 07/17/2017 05:00 PM | 08/08/2017 09:00 AM | St. Johns |  |  | 29.920234 | -81.320096 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=179
8/7/2017 Reuse Facility Filter overflow | 20176008 | On 8/7/2017 at around 6 pm the ECR facility's effluent had high TSS ( the plant is recovering from several power events which have caused problems with the air supply to the basins which has in turn affected the level of treatment and plant process.). The filters at the Reuse facility became overwhelmed and subsequently overflowed. The plant lift station which is a support system for the filter backwash tank also became overwhelmed and overflowed as well.The result was a spill of approximately 9,163 gallons. The spill was cleaned up and HTH applied. | 08/08/2017 05:26 PM | ECRWRF (FLA 041360) | 4375 Easley Drive; West Palm Beach FL; 33417 |  | Shemeez Mosadee | Plant Superintendent | smosadee@wpb.org | (561) 835-7400 |  | Plant Superintendent | Shemeez Mosadee | (561) 835-7400 |  | smosadee@wpb.org | 08/07/2017 06:00 PM | 08/07/2017 08:30 PM | Palm Beach |  |  | 26.740489 | -80.1299 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=178
8 Inch Force Main Break, SR 520 & Wilson Ave., Cocoa, FL | 20175669 | On July 27, 2017, an 8 inch ac pipe force main broke on State Road 520 at the intersection with Wilson Ave. in Cocoa. A report came in at 6:30 p.m. A Wastewater Collections crew responded and shut off Lift Stations 8 and 9 and closed valves north and south of the break. It is estimated that about 8,000 gallons of sewage was spilt. The break was located on the northern, east bound lane of SR 520. The pipe was approximately 11 feet deep. A contractor was called to repair the force main at 7:00 pm on July 28, 2017. The pipe was repaired quickly and placed back in service and lift Stations 8 and 9 were turned back on. During this time lift station 8 was gravity feeding to lift station 2 and lift station 9 was being pumped out by our Vac Con truck. No other areas were effected by the force main being down. The wastewater Collection crew cleaned up the area with the Vac Con truck and Pine Oil Disinfectant was put at the area. | 08/08/2017 05:25 PM | SR 520 & Wilson Ave., Cocoa, FL | FL |  | Donald W. Downs | Conservation/Public Relations Officer | ddowns@cocoafl.org | (321) 433-8705 |  | Cocoa Utilities Depatment employee | Donald W. Downs | (321) 433-8705 |  | ddowns@cocoafl.org | 07/27/2017 06:30 PM | 07/28/2017 08:00 PM | Brevard |  |  | 28.355623 | -80.736279 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=177
Lift Station #14; 213 1/2 Citrus Ave in Bartow | 20176021 | Approximately 3,040 gallons of domestic wastewater overflowed on the ground from a manhole due to grease blockage in a sewer line. Clean-up action was immediately initiated and completed at 11:00 am on August 8, 2017. The affected area was limed and the line was cleaned out to prevent recurrence. State Watch Office was contacted at 4:58 PM on August 8, 2017. | 08/08/2017 05:15 PM | Heritage Place WWTF; FLA 012943 | 214 Citrus Ave; Bartow FL; 33830 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 08/08/2017 08:30 AM | 08/08/2017 10:00 AM | Polk |  |  | 27.910767 | -81.724385 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=176
Diesel release from vehicle collision | 20175656 | Collision of military vehicle (large transporter) with F150 pickup truck attached to trailer with boat occurred on 26 July 2017. On 27 July 2017, at time of discovery of fuel loss, original estimate was determined at potentially 120-130 gallons based off typical schedule for filling the tanks of the military vehicle and this was reported initially to the State Watch Office. However, after moving the boat (where initially thought the diesel had ended up) visual inspection determined that much less (potentially 25 gallons) had actually leaked out than originally estimated and reported. Tanks on boat still intact with no loss of fuel. Trenches dug and lined with oil-absorbing socks/booms, and bermed to capture any runoff. Contaminated soil covered and contained for removal. Final estimation for amount of diesel loss will be determined per the remediation report. | 08/08/2017 10:31 AM | Camp Blanding Joint Training Center | 5629 State Road 16 West; Starke FL; 32091 | From main gate of the installation at 5629 SR 16 W, left onto Ave B, left on Daytona Beach Cir, slight left on Florala St, left on Pasco st, corner of Pasco and Minden St. | Jessika Blersch | Environmental Specialist III | jessika.s.blersch.nfg@mail.mil | (904) 682-3286 |  | Environmental Specialist | Jessika Blersch | (904) 682-3286 |  | jessika.s.blersch.nfg@mail.mil | 07/27/2017 01:00 PM |  | Clay |  |  | 29.980169 | -81.979535 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=175
2513 Brownwood Dr in Lakeland | 20176000 | Approximately 3,000 gallons of domestic wastewater backed-up out of a manhole, flowed down the roadway and into a storm water retention pond behind 2210 Blackwoods Dr. Further investigation confirmed that the gravity system became hydraulically overloaded (surcharged) when both pumps at near-by Lift Station #233 were turned back on following a power outage. One pump at the lift station was turned off while clean-up actions were performed. The affected area was washed down. Approximately 500 gallons were recovered and disposed of according to regulatory requirements at 1:45 PM on August 7, 2017. Signs will be posted and samples taken at the pond within the next few days as a precaution. | 08/08/2017 10:07 AM | Southwest Regional WWTF; FLA 012954 | 2000 4th Street ; Mulberry FL; 33860 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 08/07/2017 12:45 PM | 08/07/2017 01:45 PM | Polk |  |  | 27.935195 | -82.003141 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=174
Roadway at 3009, 3025, 3145 Park Ridge Ave in Lakeland | 20175998 | Approximately 5,320 of domestic wastewater discharged onto the ground , down the roadway across a grassy area leading to a storm water retention pond behind 3100 Kearns Rd. Further investigation confirmed that near-by Lift Station #233 (Sundance Village) lost power. A temporary generator was brought to the lift station to manage flow operations until power could be restored. The affected areas were washed down and treated with lime disinfectant. TECO restored power at 2:00 AM on August 8, 2017. Signs will be posted and samples taken at the pond within the next few days as a precaution. | 08/08/2017 09:58 AM | Southwest Regional WWTF; FLA 012954 | 2000 4th Street; Mulberry FL; 33860 |  | John A. Belangia | Polk County Utilities | johnbelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison; Polk County Utilities | (863) 298-4214 |  | markaddison@polk-county.net | 08/07/2017 11:15 AM | 08/07/2017 12:30 PM | Polk |  |  | 27.933053 | -82.001538 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=173
404097 | 20175985 | Summary Information for MDWASD Spill Report Incident # 404097 Version 2. Location of Discharge: SW 152 ST & SW 153 AVE UNINCORPORATED MIAMI-DADE 33187. 25.625438 -80.440430 Estimated Quantity of Sewage Released: 17,859 gallons to Ground. Water Discharge Type: Raw Sewage. Spill was stopped on: 08/07/17 03:00 PM. Please do not respond to this e-mail. For more detailed information, see attached report. Miami-Dade Water and Sewer Department - Emergency Communications Section (305) 274-9272. | 08/07/2017 04:41 PM | Miami-Dade W&S Collection System | SW 152 St & SW 153 Ave; Miami FL; 33186 | 200 FEET OFF OF 153RD AVE 25.625438 -80.440430 | Israel Camacho | WDS | israel.camacho@miamidade.gov | (305) 215-1183 |  | Operator Of the Facility | Marcelo Garcia | (305) 274-9272 |  | marcelo.garcia@miamidade.gov | 08/07/2017 02:00 PM | 08/07/2017 03:00 PM | Miami-Dade |  |  | 25.625548 | -80.440496 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=172
Howard F. Curren AWTP Low Chlorine | 20175976 | On August 7th an operator at the Howard F. Curren AWTP was adjusting the Methanol feed system when it was temporally set too low causing the chlorine residual to drop below 1.0 mg/l from 5:15am-5:25am with a low point of .94 (lab measured). During this time approximately 319,444 gallons was discharged over the weir before it was de-chlorinated prior to being discharged to the plant's out fall. This also caused the final effluent pH to temporarily drop below 6.5 (6.48 measured). The plant discharge met all other surface water quality standards. | 08/07/2017 03:42 PM | Howard F. Curran AWTP | 2700 Maritime Blvd.; Tampa FL; 33605 |  | Jeff Hilton,P.E. | Wastewater Planning Head | Jeffrey.hilton@tampagov.net | (813) 744-7844 |  | Wastewater Planning Head | Eric Weiss, P.E. | (813) 274-8039 |  | eric.weiss@tampagov.net | 08/07/2017 05:15 AM | 08/07/2017 05:25 AM | Hillsborough |  |  | 27.921364 | -82.43675 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=171
8/06/2017 ECR Reuse Crom Tank Overflow |  | The Reuse Crom Tank was being filled . The level became too high and chlorinated effluent started to spill over the top on 8/6/20 at 10:00pm. The operator noticed the tank level and stopped the overflow within 5 minutes of it going over. Approximately 300 gallons spilled onto the concrete pad around the tank. The area was cleaned and disinfected with HTH. | 08/07/2017 03:26 PM | ECRWRF (FLA 041360) | 4375 Easley Drive; West Palm Beach FL; 33417 |  | Shemeez Mosadee | Plant Superintendent | smosadee@wpb.org | (561) 835-7400 |  | Plant Superintendent | Shemeez Mosadee | (561) 835-7400 |  | smosadee@wpb.org | 08/06/2017 10:00 PM | 08/06/2017 10:30 PM | Palm Beach |  |  | 26.740326 | -80.129141 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=170
6403 Turtle Creek Blvd, Tampa, Fl. Pump Station 900898 | 41670 | On 08/07/17 @ 4:10AM a report was received from a citizen that water was gushing inside of a pump station that smelled bad on Turtle Creek Blvd. in Tampa. A Public Utilities employee was dispatched to investigate the complaint. They found the force main gate valve had been opened and the dust cap had been removed which released waste water onto the concrete slab of the pump station and the adjacent field. The name of the pump station is Turtle Creek 900898 located at 6403 Turtle Creek Blvd. The result of the SSO totaled approximately 5375 gallons. Line maintenance was dispatched and cleaned the area and washed down the slab. The area was limed. A check valve was installed on the pump out manifold along with chaining the gate valve wheels together so they cannot be tampered with in the future. Regulatory Agency notification was made to the DEP (Erica Cooper) at 11:22AM and the EPC (Nate Ostermann) at 11:28AM on 08/07/2017. There is no immediate impact to residences or businesses. | 08/07/2017 03:20 PM | Northwest Regional Wastewater Reclamation Facility FL0041670 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | RICHARD CUMMINGS | (813) 209-3003 |  | CUMMINGSR@HILLSBOROUGHCOUNTY.ORG | 08/07/2017 04:10 AM | 08/07/2017 04:55 AM | Hillsborough |  |  | 28.085744 | -82.562237 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=169
GTL Activate Sludge discharge | 20175984 | On Friday, August 4th at 4:00pm, Metro Equipment Services accidentally contacted a valve for the activated sludge line causing a 2,000 gallon discharge onto the asphalt within the plant fence-line. The valve was isolated and closed by 4:15pm. The spill was contained and did not impact and storm water systems or water bodies. The spilled volume was recovered with the use of Vactor trucks and returned to the head works of the plant. | 08/07/2017 03:01 PM | GTL Regional Wastewater Facility | 1765 SE 18th Street; Fort Lauderdale FL; 33309 |  | Troy Balint | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/04/2017 04:00 PM | 08/04/2017 04:15 PM | Broward |  |  | 26.099176 | -80.12534 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=168
Sanitary Sewer Overflow | 20175981 | 3,500 gallons and 50 gallons of it was recovered. | 08/07/2017 01:32 PM | Central Wastewater Reclamation Facility | FL |  | Robert Gordon | Communications Coordinator | scada.operations@ecua.fl.gov | (850) 969-6500 |  | Operator Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/04/2017 12:25 PM | 08/04/2017 02:45 PM | Escambia |  |  | 30.518995 | -87.27864 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=167
Lift Station #8 Mechanical Failure. |  | Lift station #8 mechanical failure causing overflow of lift station well and a manhole in close proximity to station; causing 2,000 gallons of raw sewage to enter storm drains to the Manatee River. | 08/07/2017 01:15 PM | City of Bradenton Lift Station #8 | 1500 1st Ave. W; Bradenton FL; 34208 | 1st Ave. W and Barcarrota Blvd. | William J. Quigley | Superintendent W.W.T.P. | bill.quigley@cityofbradenton.com | (941) 628-7855 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 08/07/2017 11:00 AM | 08/07/2017 11:30 AM | Manatee |  |  | 27.498981 | -82.575837 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=166
1080 Clearmont St, NE | 20175904 | Approximately 400,000 gallons of reuse water was released; 200,000 gallons captured. Water captured in SSewer pumped via lift station to active facility across the street. Contractor was onsite to replace process air piping within the facility. (The biological treatment process at this facility is not in operation) While digging, mini excavator hit ductile iron pipe which had no isolation valve, causing reuse water to continuously flow. Spill contained on site to ground, manhole and retention pond. | 08/07/2017 12:48 PM | City of Palm Bay, WRF | 1080 Clearmont St, NE; Palm Bay FL; 32905 |  | Matt Prendergast | Assistant Utilities Director | matthew.prendergast@pbfl.org | (321) 952-3499 |  | Owner Of the Facility | Matt Prendergast | (321) 952-3499 |  | matthew.prendergast@pbfl.org | 08/04/2017 09:15 AM | 08/04/2017 01:30 PM | Brevard |  |  | 28.023818 | -80.601115 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=165
2017-5962 Diesel Fuel Release ARMN 111134 Tampa | 20175962 | On 08/06/2017 at 1244 hours, CSX representative reported approximately 300 gallons of diesel fuel leaked from Reefer Unit ARMN 111134. The release occurred near MP S 841.80 on Track 16 in the Yeoman Yard in Tampa, Florida. Diesel staining was observed at two areas (East and West) along Track 16. The staining observed at both areas was approximately 20 feet (ft) long by 15 ft wide. The reefer unit was shut down and no drains or water ways were affected and all released product remained on CSX property. SWS and Arcadis were dispatched to conduct cleanup activities. Current extents of the eastern area measure approximately 24 feet long, 16 feet wide, and 1foot deep. A hardpan is present at a depth of one foot below land surface. Affected ballast was removed to the hardpan between Tracks 15 and 16, on Track 16, and between Track 16 and 17 and the area was backfilled. Delineation along Track 17 indicated approximately 40 feet of ballast is affected and will need to be removed. The western area will be excavated following completion of the eastern portion. Source removal was guided by visual observation. No native soil was encountered. | 08/07/2017 11:32 AM | CSX Transportation | 5656 Adamo Drive; Tampa FL; 33619 |  | Brooke Martin | Manager Hazardous Materials | brooke_martin@csx.com | (800) 232-0144 |  | CSX Employee | Brooke Martin | (800) 232-0144 |  | brooke_martin@csx.com | 08/06/2017 12:45 PM |  | Hillsborough |  |  | 27.95434 | -82.378758 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=164
IW Discharge Anomaly | 20175963 | At approximately 7:30 pm on 8/5/17 the on duty Water Quality Technician observed that the UV treatment system was functioning at a lower intensity level than required by permit during an on-going discharge event. This resulted in a potential discharge of partially treated industrial wastewater to the Hillsborough River. The technician ceased the discharge at 7:39pm. A review of the timeline showed an electrical anomaly occurred at 6:02pm, at which point 4 of the 10 UV lamps malfunctioned along with the intensity sensor for the system. 6 of the 10 UV lamps continued to function normally while approximately 63,000 gallons of industrial wastewater were discharged off site. It is not possible to determine the exact intensity level during this time of the discharge due to the sensor failure caused by the electrical anomaly. Out of an abundance of caution, we reported this event to the State Watch Office and the Department Southwest District Office on 8/6/17. | 08/06/2017 01:40 PM | SeaWorld Parks & Entertainment LLC -Busch Gardens | 3605 E. Bougainvillea Ave; Tampa FL; 33612 |  | Ron Cook | EHS Manager | ron.cook@buschgardens.com | (813) 918-8449 |  | Owner Of the Facility | Ron Cook | (813) 918-8449 |  | ron.cook@buschgardens.com | 08/05/2017 06:00 PM | 08/05/2017 07:40 PM | Hillsborough |  |  | 28.040576 | -82.426041 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=163
4201 Harbour Island Drive | 20175959 | Pinhole leak on cast iron line running under a bridge that crosses a saltwater canal. Wastewater released to salt marsh. Estimated 5 gallons released. Signs posted. | 08/06/2017 11:05 AM | Arlington East collection system | 4201 Harbour Island Drive; Jacksonville FL; 32225 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/05/2017 06:50 PM | 08/05/2017 09:35 PM | Duval |  | N | 30.37636 | -81.517266 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=162
6974 Sallie Avenue | 20175944 | Broken 3" forcemain under street. Water to stormwater conveyance. JEA contained wastewater in roadside ditch to prevent further release to catchbasin. Estimated 200 gallons released. Signs posted. | 08/06/2017 11:01 AM | SW collection system | 6974 Sallie Avenue; Jacksonville FL; 32210 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/05/2017 10:00 AM | 08/05/2017 04:00 PM | Duval |  | N | 30.295104 | -81.761482 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=161
2287 Broadway Avenue SSO | 20175963 | Blockage on trunkline cause manhole overflow to Mc Coys Creek. Line has been unstopped. Washed and vacuumed street and catch basin. Estimated 600 gallons released to McCoys Creek. Signs posted. | 08/06/2017 10:57 AM | District II collection system | 2287 Broadway Avenue; Jacksonville FL; 32209 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/05/2017 09:35 AM | 08/05/2017 11:50 AM | Duval | Duval | N | 30.333226 | -81.700457 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=160
Sanitary Sewer Overflow | 20175920 | Sewer spill of quantity to be determined | 08/06/2017 10:32 AM | CWRF | FL; 32503 |  | Cather | Communications Coordinator 11 | catherinelynn9fl@gmail.com | (850) 969-6500 | 6500 | Communications Coordinator 11 | Doug Gibson | (850) 969-6513 |  | Douglas.Gibson@ecua.fl.gov | 08/04/2017 01:10 PM | 08/04/2017 02:00 PM | Escambia |  | N | 30.383 | -87.276 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=159
Wastewater Overflow at 601 S. Harbour Island Blvd. | 20175947 | On August 5, 2017, Wastewater Department personnel received notification of an overflow at 601 S. Harbour Island Blvd. Personnel responded to the site and found wastewater overflowing from several manholes located in the parking garage. The wastewater was flowing into to floor drains that discharge into the Seddon Channel. After further investigation it was determined that the overflow was due to a partially clogged bypass pump at the Harbour Island pumping station. This station is currently being rehabilitated under a City contract. Bypass pumps are being used to bypass the flow to the station while the work is completed. The bypass pumping system is equipped with a second auxiliary pump; however, this pump failed to start due to a dead battery. The blockage in the primary pump was removed and the overflow stopped. The Contractor responsible for the rehabilitation project and the operation of the bypass pumping station is replacing the battery and is working to remove the wastewater that collected in the parking garage and clean up the area. | 08/05/2017 05:18 PM | City of Tampa Wastewater Department | 2545 Guy Verger Blvd.; Tampa FL; 33605 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastwater Department | Eric Weiss | (813) 274-8070 |  | eric.weiss@tampagov.net | 08/05/2017 11:30 AM | 08/05/2017 03:45 PM | Hillsborough |  |  | 27.938126 | -82.454935 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=158
GRU Wastewater Collection System | 20175936 | On 8/5/2017, at approximately 12:30 am, GRU WW crews were notified of a wastewater release at the intersection of SW 34th Street and Archer Road. Crews arrived on scene at 1:15 am and the release was stopped at approximately 6:30 am. An air release valve (ARV) failed and resulted in approximately 40,000 gallons of wastewater discharging onto the roadway. The release flowed approximately 30 feet into a stormwater inlet and should discharge to a fenced concrete stormwater ditch located in the vicinity of Windmeadows Boulevard and SW 30th Place. Due to elevated levels of precipitation, the stormwater system appears to be storing enough water to create backwater pressure that is currently preventing the wastewater release from flowing into the ditch. The stormwater system was inspected and there was sufficient freeboard to keep the flow contained in the pipes. GRU will work with local agencies to monitor the progress of the flow. The ARV is located in a manhole, which filled with wastewater during the release. To make the repair, crews had to excavate a portion of the roadway and reroute wastewater flows throughout the collection system. Crews worked for several hours to safely gain access to the valve to stop the release. The State Watch Office, FDEP, ACEPD, and the local health department have been notified. The SWO incident number for this event is 2017-5936. The coordinates for the release are 82¿22'21.892"W, 29¿37'35.225"N. The collection system flows to the Kanapaha Water Reclamation Facility (FL0027251). | 08/05/2017 07:52 AM | GRU Wastewater Collection System | SW 34th St and SW Archer Rd; Gainesville FL; 32608 |  | Jennifer McElroy | Supervising Utility Engineer | mcelroyja@gru.com | (352) 393-1291 |  | Supervising Engineer | Tiffany Small | (325) 393-1492 |  | smalltn@gru.com | 08/05/2017 12:00 AM | 08/05/2017 06:30 AM | Alachua |  |  | 29.626871 | -82.372541 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=157
Sanitary Sewer Overflow | 20175918 | sewage spill of quantity to be determined | 08/04/2017 05:51 PM | Central WRF | FL |  | Nick Ellis | Communications Coordinator | nicholas.ellis@ecua.fl.gov | (850) 969-6500 |  | Owner Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/04/2017 09:55 AM |  | Escambia |  |  | 30.426444 | -87.277034 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=156
Sanitary Sewer Overflow | 20175917 | sewage spill of quantity to be determined | 08/04/2017 05:46 PM | Central WRF | FL |  | Nicholas Ellis | Communications Coordinator | nicholas.ellis@ecua.fl.gov | (850) 969-6500 |  | Owner Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/04/2017 09:55 AM |  | Escambia |  |  | 30.426678 | -87.280201 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=155
Sanitary Sewer Overflow | 20175916 | sewage spill of quantity to be determined | 08/04/2017 05:36 PM | Central CWRF | FL |  | Steve Holcomb | Dir. of WW Infrastructure | stephen.holcomb@ecua.fl.gov | (850) 969-6647 |  | Owner Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/04/2017 10:45 AM |  | Escambia |  |  | 30.407114 | -87.220787 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=154
Sanitary Sewer Overflow | 20175915 | sewage spill of quantity to be determined | 08/04/2017 05:28 PM | Bayou Marcus WRF | FL |  | Steve Holcomb | Dir. of WW Infrastructure | stephen.holcomb@ecua.fl.gov | (850) 969-6647 |  | Owner Of the Facility | Doug Gibson | (850) 969-6513 |  | douglas.gibson@ecua.fl.gov | 08/04/2017 11:45 AM |  | Escambia |  |  | 30.436225 | -87.321713 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=153
Hwy 98 and 6th Street SSO | 20175921 | At around 12:40 we received a call of a sewer lateral overflowing at the Port Inn. Upon arrival and inspection it was discovered that a manhole was also overflowing and pump failure had occurred at the 1st Street lift station. We connected our by-pass pump and began pumping the system. Flow stopped at around 1:25-1:30 as the levels became normal. We estimate that around 200 gallons spilled into the outfall ditch in this area. Clean up and sampling have occurred. | 08/04/2017 03:01 PM | City of Port St. Joe | PO Box 278; Port St Joe FL; 32457 |  | John Grantland | Public Works Director | jgrantland@psj.fl.gov | (850) 229-8247 |  | Operator Of the Facility | John Grantland | (850) 229-8247 |  | jgrantland@psj.fl.gov | 08/04/2017 12:40 PM | 08/04/2017 01:25 PM | Gulf |  |  | 29.810633 | -85.302923 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=152
Event No. 122 | 20175914 | On August 3, 2017 at 4:00 PM an 8" force main broke causing approximately 1500 gallons of raw sewage to flow into a storm drain that flows into Lake May. The break occurred at 7th Street and Ave. F SW Winter Haven. Lake samples were collected on August 4th at 12:30 PM and sent to the lab for analysis. A warning sign was posted at the spill site. The line was repaired and back in service on August 3, 2017 at 5:00 PM. The exposed spill area was covered with lime. Lab samples were received August 7, 2017 with sample results of <5 CFU and the warning sign at the spill site was removed. | 08/04/2017 01:46 PM | City of Winter Haven WWTP # 3 FL0036048 | FL |  | Terry Carver | Wastewater Superintendent | Tcarver@mywinterhaven.com | (863) 291-5766 |  | Operator Of the Facility | Terry Carver | (863) 291-5766 |  | Tcarver@mywinterhaven.com | 08/03/2017 04:00 PM | 08/03/2017 05:00 PM | Polk |  | N | 28.015915 | -81.73499 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=151
5707 Waterford | 20175913 | Sheen on water observed in trench during excavation activities on 8/3 at 2 pm. Trench is confined to property and does not access a waterway. Sheen was removed with sorbent material and the sheen has not returned overnight. Water sample collected. Water to be pumped into frac tank and soil screening/sampling to be completed along sidewalls of trench to determine possible source. Incident has been reported to FDEP and DERM via DRF. DERM is involved with property under open case (HW-831). | 08/04/2017 01:22 PM | 5707 Waterford | 5707 Blue Lagoon Drive; Miami FL |  | Kathy Fleck / AECOM | Project Manager | kathy.fleck@aecom.com | (727) 215-7966 |  | Environmental Consultant | Kathy Fleck | (727) 215-7966 |  | kathy.fleck@aecom.com | 08/04/2017 01:11 PM |  | Miami-Dade |  |  | 25.782878 | -80.289939 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=150
Sewage blockage/SSO 321 N. Fort Lauderdale Beach Blvd. | 20175911 | At 12:01pm on 7/3/2017, A report of sewage overflowing from a manhole at 321 N. Fort Lauderdale Beach Blvd. A service worker was dispatched and arrived at the address at 1:00pm. He assessed the situation as a blockage in the gravity system. The blockage was cleared and the affected area cleaned. Approximately 100 gallons of untreated sewage reached the storm drain system that outfalls into the Intracoastal Waterway. | 08/04/2017 12:23 PM | GTL Regional Wastewater Facility | 1765 SE 18th Street; Fort Lauderdale FL; 33316 |  | Troy Balint | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Environmental Program Coordinator | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 08/03/2017 12:00 PM | 08/03/2017 04:00 PM | Broward |  |  | 26.127148 | -80.103866 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=149
SSO 08/04/2017 |  | A sanitary sewer overflow (SSO) was identified on August 04, 2017, at approximately 09:00 a.m. and repaired at 11:00 a.m. on August 4, 2017. The SSO was leaking around the repair that had been reported on July 28, 2017: FDEP Hotline Incident #2017-5675¿¿leak from a sanitary sewer (6-inch diameter cast-iron pipe) traversing an FDOT storm drain conflict structure located near 205 E. Granada.¿ Additional future repairs for permanent configuration will be considered due to the condition of the original piping material, piping/conflict structure configuration, and other unknown piping conditions. The estimated SSO was 300 gallons and deodorizing/disinfectant was used in the storm drain. Utilities staff completed the FDEP online ¿Public Notice of Pollution¿ form. | 08/04/2017 12:16 PM | City of Ormond Beach WWTP | 550 N Orchard St; Ormond Beach FL; 32174 |  | Sammy Butler Sr | Chief Plant Operator | butler@ormondbeach.org | (386) 676-3592 |  | Operator Of the Facility | Sammy Butler Sr | (386) 676-3592 |  | butler@ormondbeach.org | 08/04/2017 09:00 AM | 08/04/2017 11:00 AM | Volusia |  |  | 29.23682 | -81.239685 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=148
Clam Bayou Discharge | 20175902 | Sewer line stoppage caused manhole to overflow and discharge approximately 20,100 gallons of raw sewage. Of this, approximately 1500 gallons made it into a stormwater catch basin which eventually leads to Clam Bayou. Approximately 18,600 was vacuumed into trucks. Water levels in the manholes upstream and downstream of the stoppage were surcharged due to heavy flow volume. This situation masked the location of the clog in the main line. The cleanout cap was off to prevent wastewater from backing up into the home. Discharge from the cleanout was flowing across the grass to the stormwater catch basin. Area disinfected, signs posted and laboratory sampling/testing begun on the affected surface water. | 08/04/2017 11:04 AM | K13-215 | 2546 Kingston St. S; St. Petersburg FL; 33711 |  | Frank Niles | WRF Water Reclamation Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person reporting incident | Lane Longley | (727) 892-5612 |  | lane.longley@stpete.org | 08/03/2017 07:45 PM | 08/04/2017 05:30 AM | Pinellas |  |  | 27.744819 | -82.684008 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=147
1027 Caliente Drive SSO |  | Very slow leak to stormdrain originally reported as water leak. Leak was happening in area not close to JEA utility so it was thought to be a private issue. Upon excavation we discovered that there was bad pipes on both the JEA and customer sides. | 08/04/2017 10:16 AM | Arlington East collection system | 1027 Caliente Drive; jacksonville FL; 32211 | Very slow leak to stormdrain originally reported as water leak. Leak was happening in area not close to JEA utility so it was thought to be a private issue. Upon excavation we discovered that there was bad pipes on both the JEA and customer sides. | Eesa Ali | Environmental Scientist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/01/2017 03:25 PM | 08/02/2017 07:20 PM | Duval |  |  | 30.330769 | -81.604682 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=146
6680 103rd Street SSO | 20175895 | Broken 8" forcemain. Wastewater released to storm drain that leads to Fishing Creek. | 08/03/2017 08:14 PM | Southwest WRF collection system | 6680 103rd Street; Jacksonville FL; 32210 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/03/2017 10:20 AM | 08/03/2017 03:20 PM | Duval |  |  | 30.248358 | -81.754047 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=145
7500 Alphons St. SSO | 20175879 | Broken ARV on 20" force main, ongoing. Contained in a roadside swale. | 08/03/2017 11:28 AM | Mandarin WRF collection system FL0023493 | FL |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/03/2017 09:35 AM |  | Duval |  |  | 30.144575 | -81.516597 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=144
NEWRF Transfer Station overflow | 20175856 | Pump control system failed and caused approximately 3000 gallons of secondary clarifier effluent to overflow the pump station on to the ground. Contained inside facility grounds. | 08/03/2017 11:21 AM | Northeast Water Reclamation Facility | 1160 62nd Ave NE; St. Petersburg FL; 33702 |  | Frank Niles | WRF Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Reporter to Pollution Public Notice Webpage. | Craven Askew | (727) 893-7779 |  | craven.askew@stpete.org | 08/02/2017 04:45 PM | 08/02/2017 05:00 PM | Pinellas |  |  | 27.828039 | -82.618922 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=143
Helper Cooling Tower intake screen oil release | 1185947 | On 8/1/17 at 1615 during operator rounds the chief operator identified an oil release on the #4 Helper Cooling Tower (HCT) intake screen gear box leaking oil into the screen wash trench. The operator immediately placed a bucket under the leak to capture the oil. The traveling screen was found to be packed with sea grass and bound up, the gearbox anti-rotation pin failed from the torque and allowed the gearbox to rotate 180 degrees giving the oil fill/breather a leak path for the oil to leak out. The gearbox is located directly over the screen wash trench that is designed to carry debris away from the screen and discharge it into the discharge canal. Two (2) quarts of oil leaked into the trench and was released into the discharge canal. The Spill and Release Emergency Response Plan was activated on 8/1/17 at 1620, all notifications were made per the procedure (NRC Incident Report #1185947). The clean up of the oil in the screen wash trench was completed at 1700, the oil sheen in the discharge canal was quickly dispersed from the turbulent water and was not able to be recovered. | 08/03/2017 09:34 AM | Duke Energy Crystal River South Units 1 & 2 | 5760 Power Line Street, POC; Crystal River FL; 34428 |  | Sean Willard | Senior Environmental Specialist | Sean.Willard@duke-energy.com | (352) 501-5153 |  | Environmental Field Support | Ana Gibbs | (727) 820-4722 |  | Ana.Gibbs@duke-energy.com | 08/01/2017 04:15 PM | 08/01/2017 05:00 PM | Citrus |  |  | 28.960273 | -82.721777 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=142
Van Gundy Road SSO | 20175863 | Manhole overflows on 6600 (SWO 2017-5863) and 6628 (SWO 2017-5865) Van Gundy to stormdrain due to inflow. 1980 gallons total. | 08/03/2017 08:50 AM | JEA District II Collection system | 6600 and 6628 Van Gundy Road; Jacksonville FL; 32209 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/02/2017 03:45 PM | 08/02/2017 07:00 PM | Duval |  | N | 30.390302 | -81.701765 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=141
Lantana Avenue SSO | 20175864 | Manhole overflow due to inflow. Spill volume TBD. | 08/03/2017 08:46 AM | JEA District II Collection system | 2515 Lantana Avenue; Jacksonville FL; 32209 | Manhole overflow due to infiltration. Spill volume TBD. | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/02/2017 04:20 PM | 08/02/2017 07:00 PM | Duval |  | N | 30.379848 | -81.703817 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=140
McMillan st pump station infiltration | 20175866 | Manhole overflow to stormdrain due to inflow at W 22nd & Wilson (SWO 2017-5866), W 25th & Marlo (SWO 2017-5867) and 1999 W 30th Street (SWO 2017-5868) due to inflow impacting collection system. Spill volumes TBD. | 08/03/2017 08:39 AM | JEA District II Collection system | Intersection of Wilson Street and West 22nd Street; Jacksonville FL; 32209 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/02/2017 04:55 PM | 08/02/2017 09:00 PM | Duval |  | N | 30.357388 | -81.681187 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=139
Corner of Shoal Line Blvd & Hermosa Blvd | 20175845 | Flooding rains in the area caused the sewer collection system to become overwhelmed. Streets were flooded, sewage coming out of the manhole at the Hermosa lift station. | 08/02/2017 03:47 PM | Hermosa Lift station | Hermosa Blvd. ; Hernando Beach FL; 34607 | From us 19 go west on Cortez Blvd, turn South on Shoal line Blvd to the intersection of Shoal Line Blvd and Hermosa Blvd. | Larry Cooper | Collection / Electrical Mechanical Supervisor | lcooper@co.hernando.fl.us | (352) 754-4490 |  | Supervisor in charge of maintenance and repair | Darrell Rose | (352) 754-4490 |  | drose@co.hernando.fl.us | 08/02/2017 02:00 PM | 08/02/2017 04:00 PM | Hernando |  | N | 28.481319 | -82.650327 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=138
13101 Belcher Rd. S. | 20175836 | A contractor (Brooks & Freund, LLC), working on a project for Pinellas County, was excavating trees at a construction site and damaged a force main causing an overflow of untreated wastewater. The force main is part of the City of Largo's collection system (on easement within the building site) however it receives wastewater from five privately owned collection systems. An estimated 60,000 gallons were released between the time the line was damaged and approx. 4:15 pm when City staff could turn off the pumps for the privately owned systems that feed the main. The repair was completed by 6:30 pm. Wastewater flowed over land on the eastern border of the property and into the stormwater ditch. The contractor was directed to make arrangements to remove any wastewater remaining in the excavated area. City staff posted signs and samples were collected. Based on the draw down tests performed and the information above from T. Adams and D. Kubes, it¿s estimated that approximately 4,023 gallons was discharged from the Ranchero and Rosetree Village Lift Stations before the pumps were turned off. Tim Adams received a copy of the invoice from The Drain Team, who billed Brooks Freud LLC, to pump the rest of the wastewater from the excavated containment area at 13101 Belcher Rd. /Palms of Pinellas (2,750 gallons). Estimated discharge from Rosetree = (889 + 3134 = 4,023 gallons) Wastewater contained in Excavated hole (10¿ x 10¿ x 5¿) which was about 60 % full (3740 x 60% = 2244 gal.; The drain Team pumped 2,750 gallons from hole; disposed of to Grease Depot). Estimated Discharge from excavated hole 3740 ¿ 2750 = 990 gallons. The revised estimate discharged from this overflow is 5,013 gallons (4,023 + 990 = 5,013) | 08/02/2017 02:35 PM | Construction Site | 13101 Belcher Rd. S.; Largo FL; 33773 | The discharge was from a force main (on easement within the construction site) and overflowed towards the southeastern corner of the site and into the stormwater ditch. | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 08/01/2017 02:30 PM | 08/01/2017 04:15 PM | Pinellas |  | N | 27.891811 | -82.74375 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=137
Elgrove Whitewood Liftstation | 20175830 | Gallons lost 1200 Cause: Power Failure at Lift Station #1 Corrective and/or Safety Measures Initiated: Generator was hooked up to lift station until full power could be restored. Was there any health measures taken to protect surface waters and public health? No waters were threatened And public health was not an issue. Were there any clean-up measures taken? Manhole overflow was contained in the swale. Cleaned up area with Aqua Tech. and spread lime in affected area. | 08/02/2017 02:31 PM | Whitewood Liftstation #1 | 1145 Whitewood dr; Deltona FL; 32725 |  | Brian Terry | Lead Operator | bterry@deltonafl.gov | (386) 414-0208 |  | Operator Of the Facility | Jeff Elder | (386) 878-8977 |  | jelder@deltonafl.gov | 08/02/2017 08:50 AM | 08/02/2017 09:40 AM | Volusia |  |  | 28.893991 | -81.262712 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=136
Ammonia Purger water | 1185918 | SERC# 20175795 A CALLER REPORTED A RELEASE OF APPX. 10 POUNDS OF ANHYDROUS AMMONIA (WHICH MIXED WITH WATER) INTO A SEWAGE WHICH FURTHER LEADS TO LITTLE LAKE TRACY. THE CALLER STATED THAT THE CAUSE OF RELEASE IS FROM A PLUGGED DRAIN LINE. | 08/02/2017 02:29 PM | Burris Logistics | 100 Railroad ave; Haines City FL; 33844 |  | Andrew Bridegroom | Plant engineer | abridegroom@burrislogistics.com | (863) 255-3057 |  | Operator Of the Facility | Andrew Bridegroom | (863) 255-3057 |  | abridegroom@burrislogistics.com | 08/01/2017 09:00 AM | 08/01/2017 11:00 AM | Polk |  |  | 28.117284 | -81.634592 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=135
Kinder Morgan E-Crane Hydraulic leak | 20175833 | Discharge of 2-3 ounces of hydraulic oil into the water due to residual oil in a hose while removing hydraulic cylinder on a dock crane at the facility. | 08/02/2017 12:23 PM | Kinder Morgan Port Sutton Terminal | 4310 Pendola Point Rd.; Tampa FL; 33619 |  | Robert Filardo | EHS Specialist | bob_filardo@kindermorgan.com | (813) 853-6326 |  | EHS Specialist | David Vigh | (904) 583-3224 |  | david_vigh@kindermorgan.com | 08/02/2017 11:05 AM | 08/02/2017 11:05 AM | Hillsborough |  |  | 27.903476 | -82.41323 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=134
11005 Dale Stitik Dr, Tampa Fl. | 20175807 | Northwestern Hillsborough County ¿ On 08/01/17 at 09:30 AM there was a report of a sewer leak on a sanitary sewer force main at 11005 Dale Stitik Dr, in Tampa. ¿ A Public Utilities Department (PUD) employee was dispatched and found a leakage on the 12¿ force main on 11005 Dale Stitik Dr. The leak was isolated at 13:00, and a sleeve and new 8¿ valve was installed. Vacuum trucks were dispatched to contain the spill. ¿ The overflow was estimated at 35000 gallons, and was contained within the earthen berm of the excavation. Vacuum trucks recovered 35000 gallons of wastewater, and returned it to the North West Regional Water Reclamation Facility. There was no discharge to surrounding land. ¿ Regulatory Agency notification was made to the EPC via telephone at 3:34 PM, DEP at 3:41 PM, and SWP 3:47 PM (Incident#2017-5807). ¿ There is no immediate impact to residences or businesses. This information is provided in accordance with Emergency Order 62ER16-1: Public Notice of Pollution, issued by Governor Rick Scott on Monday, September 26, 2016 | 08/02/2017 10:11 AM | NORTHWEST REGINAL WRF FL0041670 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | RICHARD CUMMINGS | (813) 209-3003 |  | CUMMINGSR@HILLSBOROUGHCOUNTY.ORG | 08/01/2017 09:30 AM | 08/01/2017 01:00 PM | Hillsborough |  |  | 28.074154 | -82.608644 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=133
11291 Old St Augustine Road | 20175820 | Manhole overflows to retention ponds at 4366 Spurlina Dr S SWO 2017-5820, 4338 Windtree Dr SWO 2017-5821, Losco & Wandering Oaks Dr SWO 2017-5822 & 4532 Singletary Rd SWO 2017-5823 all related to the same grease blockage located on 11291 Old St Augustine Road. | 08/02/2017 08:25 AM | Mandarin WRF collection system FL0023493 | 11291 Old St Augustine Road; Jacksonville FL; 32257 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 08/01/2017 12:05 AM | 08/01/2017 02:40 PM | Duval |  |  | 30.171755 | -81.603135 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=132
403714 | 2175813 | WASD Incident #: 403714 Version: 2 Version Type: Supplementary Qualified UDP? No Call Center Comments: : Approx GPS coordinates are: 25¿ 44.698¿ N 80¿ 7.772¿ W. Incident Version Created On: 08/04/17 05:37 PM Job Order #: 1003467848 Location of Discharge: 3989 Rickenbacker CSWY UNINCORPORATED MIAMI-DADE 33149 Additional Location Description: Near the connec of the 90-inch and 120-inch pipes Reported by WASD Employee? No Reported by: water keepers Utility Name: Miami-Dade Water & Sewer Phone Number: (305) 274-9272 Path of Flow: Contained Discharge Caused by Asset Type: Central District WWTP Contractor Involved? No Discharge Due to/Caused by: Central District WWTP Other Cause Additional Discharge Cause: OCEAN OUTFALL PIPELINE Pipe Material: RCP (Reinforced Concrete Pipe) Pipe Size in inches: 90 Type of Water Discharge: SECONDARY EFFLUENT Did Discharge Go to Public Access Area? Yes Did Discharge Go into Storm Sewer? No Did Discharge Go into Surface Water? Yes Distance in Feet into Surface Water: 0 Body of Water Name: North Atlantic Ocean Type of Water: Marine Weather Conditions: Cloudy Estimated Quantity of Sewage Released in Gallons: 92,120 Estimated Time Release Started: 07/31/17 10:15 AM Estimated Time Action Taken at Site: 07/31/17 10:15 AM ACTION TAKEN Active Spill Observed? Yes Discharge Flow Stopped? Yes Discharge Stopped On: 08/03/17 05:00 PM Spill Contained? No Area Cleaned? No Area Disinfected? No Public Notified? No Spill Recovered? No AGENCIES NOTIFIED AGENCY NOTIFICATION POINT METHOD NOTIFIED TO NOTIFIED ON DEP FDEP State Warning Point Phone TAYLOR 217-5813 08/04/17 05:55 PM RER RER Compliance Desk Phone LESLI/ANSWERING SERVICE 08/04/17 05:55 PM WASD WASD Bertha Goldenberg Phone BERTHA 08/04/17 05:55 PM DEM DEM Notification Group E-mail 08/04/17 05:55 PM DEP DEP Notification Group E-mail 08/04/17 05:55 PM DOH DOH Notification Group E-mail 08/04/17 05:55 PM EPA EPA Notification Group E-mail 08/04/17 05:55 PM HMS Hazardous Materials Subcommittee Group E-mail 08/04/17 05:55 PM MD-BCC DIST11 E-mail 08/04/17 05:55 PM RER RER Notification Group E-mail 08/04/17 05:55 PM SFWM SFWM Notification Group E-mail 08/04/17 05:55 PM WASD WASD Interdepartmental Personnel E-mail 08/04/17 05:55 PM Future Contact Person: Marcelo Garcia Future Contact Person's Phone Number: (786) 552-8342 Form Completed by: Michael A. Cabrejos (E312898) Of: Water & Sewer Department DEP USE ONLY WRITTEN REPORT REQUESTED: ___ No/ ___ Yes DUE DATE: _________________________________ NAME: _____________________ TITLE: ________________________________ SIGNATURE: ______________ DATE: ___________ 08/04/17 05:55 PM * Fields on red are the ones that changed from previous version Page 1 of 1 DOMESTIC WASTEWATER DISCHARGE/ABNORMAL EVENT NOTIFICATION MIAMI-DADE COUNTY WATER AND SEWER DEPARTMENT EMERGENCY COMMUNICATIONS SECTION | 08/01/2017 07:55 PM | Miami-Dade W&S Central District Wastewater Treatment Plant | 3989 Rickenbacker Cswy; Miami Florida FL; 33149 | Location of Discharge: Approximate coordinates are: Lat. 25.745 N Long -80.130 W Additional Location Description: Near the connection of the 90-inch and 120-inch pipes | Marcelo Garcia | Emergency Communications Manager | marcg@miamidade.gov | (305) 274-9292 |  | Operator Of the Facility | Marcelo Garcia | (305) 274-9272 |  | marcg@miamidade.gov | 07/31/2017 10:15 AM | 08/03/2017 05:00 PM | Miami-Dade | Miami-Dade | Y | 25.745341 | -80.129174 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=131
Lift Station #100; 3595 Shepherd Rd, Lakeland, FL | 20175757 | Approximately 10,000 gallons of domestic wastewater discharged from the wet well at Lift Station #100 due to heavy rain and a power outage associated with Tropical Storm Emily at 11:03 AM on July 31, 2017. The discharge entered a near-by drainage ditch that feeds a storm water retention pond (ERP No. 40001105.002). Power was restored and the lift station was returned to normal operating conditions at 12:05 PM. Signs were posted around the pond as a precaution and sampling was done at 2:45 PM on August 2, 2017. State Watch Office was contacted at 1:09 PM on July 31, 2017 and the updated information was provided to them at 5:45 PM on August 2, 2017. | 08/01/2017 04:43 PM | Southwest Regional WWTF; FLA 012954 | 2000 4th Street; Mulberry FL; 33860 |  | John A. Belangia | Polk County Utilities | JohnBelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Mark Addison ; Polk County Utilities | (863) 298-4214 |  | MarkAddison@polk-county.net | 07/31/2017 11:03 AM | 07/31/2017 12:05 PM | Polk |  | N | 27.938668 | -82.018153 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=130
606 Paddington Lane, Lakeland, FL | 20175788 | Approximately 1,800 gallons of domestic wastewater discharged from a manhole in front of 606 Paddington Lane due to grease build-up in a gravity sewer line at 6:58 PM on July 31, 2017. The discharge flowed down the roadway to a near-by storm drain that feeds a storm water pond. Clean-up action was immediately initiated and completed at 1:00 AM on August 1, 2017. The affected area was vacuumed and washed down. Approximately 700 gallons was recovered and disposed in accordance with regulatory requirements. Signs have been posted around the pond as a precaution and sampling will be done in the next 24 to 48 hours. State Watch Office was contacted at 8:57 AM on August 1, 2017. | 08/01/2017 04:24 PM | Northwest Regional WWTF; FLA 178667 | 8950 N. Campbell Rd ; Lakeland FL; 33810 |  | John A. Belangia | Polk County Utilities | JohnBelangia@polk-county.net | (863) 298-4270 |  | Environmental Specialist II | Todd Potter; Polk County Utilities | (863) 393-8353 |  | ToddPotter@polk-county.net | 07/31/2017 06:55 PM | 08/01/2017 01:00 AM | Polk |  |  | 28.134697 | -81.944028 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=129
Briarwood Estates MHP | 20175804 | Upon arrival to the site on 7/31/2017 @ approximately 4:30 pm, the operator found the effluent pump station filling and discharging chlorinated effluent to the grounds adjancent to the station. There was full power to the station, however operator was unable to get pump to operate and pump down the station. The owner has been notified and they are investigating to determine the best and quickest solution. Currently the estimated volume of discharge is 7000 gallons of treated effluent, no water ways have been affected. The station at Briarwood has returned to normal operations. The Park maintenance staff was able to trouble shoot and correct loose wiring, which corrected the malfunction and allowed the pump to pump down the station and the discharge ceased. (at approximately 10 am on 8/3/2017). It is estimated that an addition 600 gallons of chlorinated effluent was discharged since the report of the initial event. The operator has applied lime to the affected area. | 08/01/2017 02:16 PM | Briarwood Estates | 5310 Deeson road; Lakeland FL; 33810 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 |  | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 07/31/2017 04:10 PM | 08/02/2017 10:00 AM | Polk |  | N | 28.111722 | -82.056017 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=128
Lucy Hamilton | 20175770 | Manhole #J007-005 overflowed approximately 1690 gallons of raw sewage due to debris that had caused the line to surcharge. Found an abandoned sanitary line from Gibbs HS that had apparently been used for the storm drain of one of their parking lots, connecting it to the sanitary system. Cleaned debris to clear line and used vactor truck to remove spill. Work is in progress to correct the problem. NOTE: Two occurrences of this incident, one for 35 minutes and one for 330 minutes. | 08/01/2017 12:09 PM | Manhole #J007-005 | 3350 11th Ave S; St. Petersburg FL; 33712 |  | Frank Niles | Water Reclamation Facility Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Person making public notice. | Lane Longley | (727) 892-5612 |  | lane.longley@stpete.org | 07/30/2017 04:50 PM | 07/31/2017 03:00 PM | Pinellas |  |  | 27.759206 | -82.678859 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=127
GRU Wastewater Collection System | 20175778 | On July 31, 2017 around 4:00 PM, GRU staff was notified by a customer of a wastewater smell in the area of NW 143rd St and Newberry Rd. GRU personnel in the area was not able to locate the source of the odor and called dispatch to send a wastewater crew to inspect the area. Around 7:30 PM, crews located a forcemain break at 415 NW 143rd St and stopped the release. Due to the depth of the pipe, proximity to a heavily traveled road and dark conditions, vacuum trucks were assigned to the area to contain the release until repairs could be safely made in the daylight. The repair was completed on the morning of 8/1/17. Approximately 4,000 gallons was released into a fenced, wooded area through a longitudinal crack in the PVC forcemain. Advisory signs were placed in the area of the spill and lime was applied. No creeks or other bodies of water were impacted. GRU is looking into the cause of the forcemain break. FDEP, ACEPD, and the health department were notified of the incident. The State Watch Office incident number for this event is 2017-5778. The coordinates are 29.657668, -82.495955. The collection system flows to the Kanapaha Water Reclamation Facility (FL0027251). | 08/01/2017 11:40 AM | GRU Wastewater Collection System | 415 NW 143rd St; Newberry FL; 32669 |  | Jennifer McElroy | Supervising Utility Engineer | mcelroyja@gru.com | (352) 393-1291 |  | Supervising Engineer | Tiffany Small | (352) 393-1492 |  | smalltn@gru.com | 07/31/2017 04:00 PM | 07/31/2017 07:30 PM | Alachua |  |  | 29.657269 | -82.495871 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=126
200 Country Club Dr., Largo, FL 33771 | 20175794 | A breaker tripped at the Lift Station causing two (2) manholes & five (5) clean-outs to overflow. Approximately 120 gallons flowed overland into a ditch. City staff responded, the area was washed down, all washwater was vacuumed and disposed of properly. Signs were posted and samples collected. The lift Station is currently under a private contractor and the City is working with the contractor and engineering to resolve the issues. | 08/01/2017 11:14 AM | 200 Country Club Dr. | Same as above; Largo FL; 33771 |  | Donna Dessoir | City of Largo, Environmental Control Supervisor | dodessoi@largo.com | (727) 510-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 07/31/2017 07:15 PM | 07/31/2017 07:30 PM | Pinellas |  |  | 27.913573 | -82.771012 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=125
Tropical Storm Emily Influent Structure Overflow. | 20175789 | Due to Heavy Rains from tropical storm Emily, Influent plant flow exceeded Influent structure capacity; Causing structure to overflow. Our procedure for this problem is to open by-pass valve to Influent structure, however the valve extension to valve malfunctioned causing continued overflow until a backhoe arrived on site and excavated the valve so that we could operate and open with a hand held valve key. Duration of incident 9:00am - 10:00am. Total sewage spilled during that time 50,000 gallons. | 08/01/2017 11:09 AM | City of Bradenton W.W.T.P. | 1810 First Street West; Bradenton FL; 34208 | US41 and 17th Ave. West. | William J. Quigley | Plant Superintendent | bill.quigley@cityofbradenton.com | (941) 708-6352 |  | Operator Of the Facility | William J. Quigley | (941) 628-7855 |  | bill.quigley@cityofbradenton.com | 07/31/2017 09:00 AM | 07/31/2017 10:00 AM | Manatee |  |  | 27.48346 | -82.564258 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=124
City of Lakeland - Southwest | 5765 | Heavy rains associated with Tropical Storm Emily caused excessive flows into the City's Southwest Pump Station which discharged more sewage than the downstream collection system could handle which resulted in the release of approximately 8,000 gallons of sewage to spill into near by storm drains. Control of the station was put into manual operation to control the amount of discharge which eliminated the downstream problem. | 08/01/2017 09:49 AM | City of Lakeland NPDES Permit No FL0039972 | 1825 Glendale Street; Lakeland FL; 33803 |  | Richard Ruede | Manager of Wastewater Collection | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 07/31/2017 11:15 AM | 07/31/2017 03:00 PM | Polk |  |  | 28.011183 | -81.956907 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=123
City of Lakeland - Westside Pump Station | 20175764 | Heavy rains associated with Tropical Storm Emily cause excessive flows into the collection system overwhelming the Westside pump station causing the release of approximately 2,000 gallons of sewage to spill into near by storm drains. Additional pumping equipment was brought into the area to remove excess water which allowed the pump station to handle the remaining flow. | 08/01/2017 09:42 AM | City of Lakeland NPDES Permit No. FL0039772 | 1825 Glendale Street; Lakeland FL; 33803 |  | Richard Ruede | Manager of Wastewater Collection | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 07/31/2017 10:00 AM | 07/31/2017 03:15 PM | Polk |  |  | 28.036884 | -81.989083 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=122
Glendale WWTF | 20175783 | On 31-July 2017 the City of Lakeland's Glendale Wastewater Facility received 4" of rain within a 12 hour period and recorded peak hourly flows in excess of 40mgd. One of the splitter boxes on the facility was unable to handle the peak flow rate and a portion of the flow overtopped the splitter box for an estimated 30 minutes. Staff estimates the amount of flow that overtopped the splitter box to be between 25,000 and 30,000 gallons. The wastewater that was spilled did not reach storm drains but was contained in ditches and retention facilities. The affected area was limed. | 08/01/2017 08:26 AM | Glendale WWRF | 1825 Glendale Street; Lakeland FL; 33803 |  | R. Scott Lewis | Manager of Treatment | scott.lewis@lakelandgov.net | (863) 834-6565 |  | Operator Of the Facility | Scott Lewis | (863) 834-6565 |  | scott.lewis@lakelnadgov.net | 07/31/2017 02:00 PM | 07/31/2017 02:30 PM | Polk |  |  | 28.007448 | -81.92785 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=121
Untreated Domestic Wastewater Overflow - Pump Station 94 | 20175772 | Installation name: Thomas P Smith WRF -Wastewater Collection System Installation address: 4505 Springhill Rd Installation location : Tallahassee FL 32305 Contact person: Charles Ziegmont (850-508-0147) Permit number: FLA010139 Date and time of incident or discovery: 7/31/17 8:03 AM Location of incident or discovery: Pump Station 94 (202 Summer Brook Dr.) Suspected source or cause of incident: At approximately 8:03 AM, the City received a call from a citizen who reported a sewer spill coming from pump station 94. Crews responded and were on-site by 8:20 AM and discovered that the six-inch discharge hose on the bypass pump had split and was leaking on the ground surface when the pump cycled on. It was determined based on SCADA that the bypass pump had cycled on twice for a total of 4 min with 50% of the pumped volume (estimated at 2400 gallons) being spilled onto the ground. The crew immediately repaired the hose and began recovery efforts. Sewage accumulated in a low-lying area and approximately 2000 gallons was recoverable with the remainder being absorbed into the soils. Crews also cleaned and disinfected the affected soils in the area. Type of pollution: Untreated Domestic Wastewater Amount of pollution: 2400 gallons (2000 gallons recovered) Medium affected by pollution: Land surface Potentially affected areas beyond installation property boundary: None identified ¿ overflow contained to immediate area around station manhole. Potential risk to public health, safety, or welfare: None Identification of other parties notified of incident and time notification occurred: State Watch Office: SWP-2017- 5772 Any other information that may be helpful including clean up actions and status: Crews were able to recover approximately 2000 gallons and the remaining volume was absorbed into the surrounding soils. There were no impacts to surface waters. The area was cleaned and disinfected. | 07/31/2017 06:16 PM | Pump Station 94 | 202 Summerbrook Drive; Tallahassee FL; 32312 |  | Hazem Tamimi | Environmental Engineer | hazem.tamimi@talgov.com | (850) 459-7540 |  | Environmental Engineer | Hazem Tamimi | (850) 459-7540 |  | hazem.tamimi@talgov.com | 07/31/2017 08:05 AM | 07/31/2017 08:20 AM | Leon |  |  | 30.574927 | -84.275496 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=120
AT&T Vehicle Hydraulic Spill - Royal Palm Beach | 20175767 | An AT&T Lift Truck had a hydraulic hose failure, spilling approximately 30 gallons on grassy soil in the ROW of 4220 Avocado Blvd, Royal Palm Beach FL. Heritage Environmental Services was contacted at 1500 hours to mobilize a spill response to the site. They assigned the cleanup to their sub, Cliff Berry (CBI), with an ETA of 1730 hours. 8/1/2017 - 0900: CBI provided an initial response yesterday afternoon that involved covering the contaminated area with visqueen to prevent exposure to the rain. They are to return today to dig up the top layer of soil and load into a roll off box to haul away for disposal. They will then re-sod the excavated area. The Project Mgr. reported the dimensions of the impacted area are approximately 15¿ x 25¿ and that there was no release into storm drains of any kind. | 07/31/2017 05:45 PM | ROW | Utiltiy Easement; 4220 Avocado Blvd; West Palm Beach FL; 33411 |  | Ray Garay | Sr. Environmental Field Support Manager | rg8535@att.com | (305) 546-6567 |  | AT&T Spill Incident Response Manager | Ray Garay | (305) 546-6567 |  | rg8535@att.com | 07/31/2017 02:30 PM |  | Palm Beach |  | N | 26.739408 | -80.255572 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=119
11764 Marco Beach Drive Transformer spill | 1185780 | ~ 100 gallons of non-PCB transformer oil leaked from a pad mounted transformer due to being struck by an unknown vehicle. Oil made it to parking lot, grass, catchbasin and a stormwater pond. | 07/31/2017 05:32 PM | 11764 Marco Beach Drive | 11764 Marco Beach Drive; Jacksonville FL; 32224 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 07/31/2017 08:15 AM | 07/31/2017 11:25 AM | Duval |  | N | 30.284233 | -81.51489 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=118
Andy Koebel | 20175758 | Heavy flows during TS Emily call for third pump in station to come on. Third pump had shorted motor so when it tried to come on the main breaker tripped. About 3000 gallons of sewage spilled fro lid. Crews reset main breaker. Spill was contained on site Cleaned and spread lime on the area. | 07/31/2017 05:02 PM | Arroyall master lift station | 27780 Arroyal Rd.; Bonita Springs FL; 34135 | US 41 to crown lake blvd. Head east. Entrance on left behind CVS | Andy Koebel | Director of Operations | AKoebel@bsu.us | (239) 992-0711 |  | Operator Of the Facility | Andy Koebel | (239) 992-0711 |  | AKoebel@bsu.us | 07/31/2017 12:00 PM | 07/31/2017 12:15 PM | Lee |  |  | 26.333332 | -81.804955 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=117
SSO 07/27/2017 | 20175675 | A sanitary sewer overflow was identified on July 27, 2017. The City requested FDOT assistance for recent citizen reports of sewer smell emanating from FDOT storm drain. Initial FDOT findings indicated a potential for leak from a sanitary sewer (6 inch diameter cast iron pipe) traversing an FDOT storm drain conflict structure located near 205 E. Granada. City wastewater collection system crew responded early morning July 28, 2017 to confirm the leak. The source of the sewerage was confirmed as an existing 6 inch cast iron pipe force main currently serving a private lift station from an adjacent commercial plaza facility. Crews repaired the leaking pipe/ fittings and returned to service. Additional future repairs for permanent configuration will be considered due to the condition of the original piping material, piping/conflict structure configuration other unknown piping conditions. It is estimated that a large portion of the sewerage flow continued to flow to the sanitary sewer system. Assuming the private commercial lift station pumped 10 minutes per hour for 16 hours each day @ average 5 gpm leak rate, the estimated daily discharge rate equates to 800 gallons per day. Noting that customer reports for past couple of months and using the daily discharge rate estimated above, a total estimated overflow would result in approximately 50,000 gallons. | 07/31/2017 11:08 AM | City of Ormond Beach WWTP | 550 N Orchard St; Ormond Beach FL; 32174 |  | Sammy Butler Sr | Chief Plant Operator | butler@ormondbeach.org | (386) 676-3592 |  | Operator Of the Facility | Sammy Butler Sr | (386) 676-3592 |  | butler@ormondbeach.org | 07/27/2017 01:30 PM | 07/28/2017 11:00 AM | Volusia |  |  | 29.255479 | -81.155021 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=116
1030 Mill Creek Rd | 20175726 | Approximately 500 gallons of raw sewage overflowed from a manhole near 1030 Mill Creek Rd in Jacksonville due to increased rainfall in the area. The spill entered Strawberry Creek and clean-up actions were completed, signs posted. Environmental sampling of Strawberry Creek was conducted on 7/31/17 and 8/1/17. The results show that the waterway has returned to pre-incident conditions. | 07/31/2017 11:07 AM | JEA Lift Station | 1030 Mill Creek Rd; Jacksonville FL; 32216 |  | J Bowden | Incident Responder | bowdjt@jea.com | (904) 252-5471 |  | Incident Responder | J Bowden | (904) 252-5471 |  | bowdjt@jea.com | 07/30/2017 10:00 AM | 07/30/2017 05:00 PM | Duval |  | N | 30.331898 | -81.560354 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=115
7834 Holiday Rd S | 20175725 | Approximately 90,000 gallons of raw sewage was released from a lift station at 7834 Holiday Rd S in Jacksonville due to increased rainfall in the area. The spill entered Pottsburg Creek and clean-up actions have been completed and signs posted. Environmental sampling of Pottsburg Creek conducted on July 31 and August 1 and the results show that the waterway has returned to pre-incident conditions. | 07/31/2017 10:57 AM | JEA Lift Station | 7834 Holiday Rd S; Jacksonville FL; 32216 |  | J Bowden | Incident Responder | bowdjt@jea.com | (904) 252-5471 |  | Incident Responder | J Bowden | (904) 252-5471 |  | bowdjt@jea.com | 07/30/2017 07:30 AM | 07/30/2017 03:40 PM | Duval |  | N | 30.295267 | -81.573738 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=114
10477 Bradley Rd | 20175724 | Approximately 200,000 gallons of raw sewage was released from a lift station located at 10477 Bradley Rd in Jacksonville due to increased rainfall in the area. The spill entered a nearby storm drain, which leads into Ginhouse Creek. Clean-up actions have been completed. Signs posted. | 07/31/2017 10:47 AM | JEA Lift Station | 10477 Bradley Rd; Jacksonville FL; 32246 |  | J Bowden | Incident Responder | bowdjt@jea.com | (904) 252-5471 |  | Incident Responder | J Bowden | (904) 252-5471 |  | bowdjt@jea.com | 07/30/2017 10:55 AM | 07/30/2017 12:40 PM | Duval |  | N | 30.313089 | -81.526708 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=113
10720 E Broadway Ave Brandon, FL | 20175730 | ¿On 07/30/17 @ 3:30PM a report from a contractor of a valve (ARV) leaking wastewater at 10720 E Broadway Ave in Brandon. A Utilities Maintenance Operator was dispatched to investigate. They found the valve leaking, resulting in a 20,000 gallon overflow that was contained in the valve vault and drainage ditch next to the valve. 15,000 gallons was recovered via pump truck and returned to system. Pump trucks were dispatched and pump stations were isolated at 7:30PM stopping the overflow. The Utilities Maintenance Operators made the repair to the valve. A wash down of the affected area was performed. Regulatory Agency notification was made to the State Warning Point via phone at 12:25AM (incident # 2017-5730), DEP via voicemail at 12:30AM and EPC via voicemail at 12:33AM on 12/31/17. There is no immediate impact to residences or businesses. | 07/31/2017 09:53 AM | Falkenburg AWWTP Permit Number: FL0040614 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | RICHARD CUMMINGS | (813) 209-3003 |  | CUMMINGSR@HILLSBOROUGHCOUNTY.ORG | 07/30/2017 03:30 PM | 07/30/2017 07:30 PM | Hillsborough |  |  | 27.973764 | -82.320112 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=112
Untreated Domestic wastewater Release | 20175699 | The City of Tallahassee is reporting a 2000 gallons of untreated domestic wastewater overflow at 2525 Shumard Oak Blvd on 7/28/2017. The release started around 7:30 PM and t was stopped around 9:30 PM. The release occurred due to a broken Air Release Valve on the Force man associated with Pump Station 65. The ARV is connected to the Force Main by a 2-inch stem. The release occurred through the 2 inch pipe stem. The overlow was contained in a closed stormwater pond and 1800 gallons was recovered, Nor surface waters were affected. The affected area was washed, disinfected and taped off. The State Watch Office was notified of the incident. | 07/29/2017 12:17 PM | Thomas P. Smith WWRF | 3750 chaseridge court; 4505 Sringhill Road; Tallahassee FL; 32305 |  | Hazem Tamimi | Environmental Engineer | hazem.tamimi@talgov.com | (850) 459-7549 |  | work for the City of Tallahassee ESF | Hazem Tamimi | (850) 459-7540 |  | hazem.tamimi@talgov.com | 07/28/2017 07:30 PM | 07/28/2017 09:30 PM | Leon |  |  | 30.387803 | -84.233247 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=111
Sargent Lee Mills Blvd | 20175660 | 1130 EST - Scott Arledge with Palmetto State Transportation reported 50-gallons of diesel fuel and 12-gallons of motor oil released from truck number / trailer number / R16121 on 07/27/2017. The incident occurred off US-41 (Broadstreet) on Sargent Lee Mills Blvd Brooksville, FL 34601 (Hernando County). The closest address to the spill is 2364 Simon Ct, Brooksville, FL 34604, USA. Mechanical failure was the reported cause of the incident. No waterways or drains were reported to have been impacted by the release. At 1200 EST - ERTS left a voicemail Hernando County Department of Public Works contact, Clay Black, to obtain additional information. At 1206 EST - ERTS contacted the FL State Watchpoint and operator Claudia stated that Mr. Black reported the incident on 07/27/2017 at 1700 EST. Mr. Black reported the incident occurred on 07/27/2017 at 1530 EST. Operator Claudia provided FL DEQ incident number 2017-5660 that was issued at the time of the initial report. At 1213 EST - ERTS dispatched Hulls Environmental from Tampa, FL to respond. At 1227 EST - Hulls environmental provided an ETA of 90-minutes to respond. 1450 - The contractor arrived on site. The contractor estimateed 25-gallons petroleum released. The damaged asphalt where the truck burned down has been repaved. Clay Black is on site and stated that one saddle tank was punctured at the top and the other was punctured approximately 3/4 down from the top. The tanks were pumped prior to removing the vehicle from the site. The contractor stated there iwas no smell of petroleum. 8 samples soil samples will be taken across the impacted area and PID meter reading will be taken. 1630 EST - The contractor completed all environmental operations for this incident and departed from the site. PID meter samples taken across 8 separate areas along the site indicate the impacted soil measures 34' by 14' by 1.2'. Poly sheeting was placed over the impacted soil and secured. The contractor will submit an estimate to the ERTS remediation department to excavate and backfill the soil. ERTS will request competitive bids from our network vendors to complete the work. No waste was generated from this response. | 07/28/2017 07:30 PM | n/a | FL |  | John Yant | Project Manager | jyant@ertsonline.com | (216) 904-4781 |  | Environmental Services Vendor | John Yant | (216) 904-4781 |  | jyant@ertsonline.com | 07/27/2017 03:30 PM | 07/27/2017 06:30 PM | Hernando |  | N | 28.458199 | -82.463251 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=110
Jonathan Hughes | 20175680 | Discharge of 2000 gallons of fully treated reclaimed quality water to ground between the 10 million gallon tank and the 5 million gallon tank. As the 10 million gallon tank was filling, the water came out of a stand pipe valve the contractor had recently used for pumping. The contractor quickly closed valve as soon as water was spotted coming out. | 07/28/2017 05:59 PM | Southwest Water Reclamation Facility | 3800 54th Ave S; St. Petersburg FL; 33711 |  | Frank Niles | Water Reclamation Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Public Notice Reporter | Ken Wise | (727) 893-7497 |  | george.wise@stpete.org | 07/28/2017 01:30 PM | 07/28/2017 01:35 PM | Pinellas |  |  | 27.717587 | -82.682832 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=109
1006 North 29th Street |  | Blockage in a gravity sewer main caused a spill on an abandoned property lot that had a broken sewer service line. We unclog the blockage with our Vac Truck, then collected the spill and then spread lime on the contaminated area. | 07/28/2017 05:11 PM | Immokalee Water & Sewer District | 1012 Sanitation Road; 140 White Way; Immokalee FL; 34142 |  | Hector Ramos | Waste Water Collection Supervisor | hectorramos@iw-sd.com | (239) 564-9645 |  | Waste Water Collection Supervisor | Hector Ramos | (239) 564-9645 |  | hectorramos@iw-sd.com | 07/28/2017 11:00 AM | 07/28/2017 12:05 PM | Collier |  |  | 26.430596 | -81.444572 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=108
5755 East Milton Road - Prison Lift Station | 20175681 | This report is to notify you of a sewage spill that occurred on July 28, 2017, at approximately 12:00 a.m. The estimated spillage was approximately 1000 gallons and occurred at 5755 East Milton Road, Milton, FL, 32570. The responsible permittee, City of Milton Water & Sewer Department; WWT Facility Permit #FL0021903, 5438 Alabama Street, Milton, Fl. 32570; Phone (850) 983-5434, Fax: (850) 983-5439, has attempted to contact all appropriate entities. Please note below. The discharge has ceased and, by-pass pumping was not used. The spillage was from the Prison Lift Station, caused by a lightning strike. The untreated domestic spillage was contained, and did not enter a storm drain/body of water. The Water/ Sewer Department disinfected the area of the spill by applying chlorine bleach and Ban-O. | 07/28/2017 05:02 PM | Prison Lift Station | FL |  | Jo Robey Groenenboom | Admin. Assistant | jo.robey@ci.milton.fl.us | (850) 983-5434 |  | employee for the City of Milton | Joe Cook | (850) 698-9244 |  | joe.cook@ci.milton.fl.us | 07/28/2017 12:00 AM | 07/28/2017 01:00 AM | Santa Rosa |  |  | 30.642632 | -86.984097 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=107
Speedway 6519 - Dispenser Sump | 20175678 | Laboratory analytical data collected during underground dispenser containment sump closure sampling on July 14, 2017 indicate a soil sample collected adjacent to Gasoline Dispenser 7/8 contained hydrocarbons in excess of Soil Cleanup Target Levels. A Discharge Reporting Form was forwarded to City of Jacksonville Environmental Quality Division (EQD) on July 28, 2017 following receipt of date. A Closure Assessment Report summarizing closure assessment activities will be forwarded to COJ EQD by September 25, 2017. Pursuant to Chapter 62-780, assessment will be initiated and a Site Assessment Report will be forwarded to EQD within 270 days. Discharge affected: Soil Type of regulated substance discharged: Gasoline Estimated number of gallons discharged: Unknown | 07/28/2017 04:50 PM | Speedway No. 6519 | 5405 Beach Boulevard; Jacksonville FL; 32207 |  | Keith Hughes | Advanced Environmental Representative | keithahughes@speedway.com | (937) 863-7642 |  | Speedway Representative | Keith Hughes | (937) 863-7642 |  | keithahughes@speedway.com | 07/14/2017 12:00 PM | 07/14/2017 05:00 AM | Duval |  | N | 30.295302 | 81.61001 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=106
Speedway 6522 - Dispenser Sump | 20175679 | Laboratory analytical data collected during underground dispenser containment sump closure sampling on July 17, 2017 indicate soil samples collected adjacent to Gasoline Dispensers 1/2 and 5/6 contained hydrocarbons in excess of Soil Cleanup Target Levels. A Discharge Reporting Form was forwarded to City of Jacksonville Environmental Quality Division (EQD) on July 28, 2017 following receipt of data. A Closure Assessment Report summarizing closure assessment activities will be forwarded to COJ EQD by September 25, 2017. Pursuant to Chapter 62-780, assessment will be initiated and a Site Assessment Report will be forwarded to EQD within 270 days. Discharge affected: Soil Type of regulated substance discharged: Gasoline Estimated number of gallons discharged: Unknown | 07/28/2017 04:50 PM | Speedway No. 6522 | 10405 Beach Boulevard; Jacksonville FL; 32246 |  | Keith Hughes | Advanced Environmental Representative | keithahughes@speedway.com | (937) 863-7642 |  | Speedway Representative | Keith Hughes | (937) 863-7642 |  | keithahughes@speedway.com | 07/14/2017 12:00 PM | 07/15/2017 05:00 AM | Duval |  | N | 30.287165 | -81.543789 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=105
1902 Breckinridge Blvd. | 20175616 | Blockage in gravity sewer caused minor overflow at manhole. | 07/28/2017 02:51 PM | Flming Island WWTP Collection System | 1902 Breckinridge Blvd.; Middleburg FL; 32068 | 1233 feet south of intersection of CR220 and Breckinridge Blvd. | Dennis R Martin | Wastewater Superintendent | dmartin@clyutility.org | (904) 626-3893 |  | Operator Of the Facility | Dennis R Martin | (904) 626-3893 |  | dmartin@clayutility.org | 07/28/2017 09:15 AM | 07/28/2017 01:20 PM | Clay |  |  | 30.097753 | -81.761809 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=104
Sanitary Sewer Overspill | 20175613 | At 7:18am a SSO was reported on Central Industrial Drive. Arrived onsite around 7:40am where a hole appeared. Immediately staff arrived with vacuum truck and SSO Trailer. Started cleanup process using lime washed down area and collected the water from storm drain. Station back on line 1:10pm | 07/28/2017 12:48 PM | City of Riviera Beach | 600 West Blue Heron Blvd; Riviera Beach FL; 33404 | North of Blue Heron Blvd & central Industrial Drive | Joseph Jackson | Chief Water/Sewer Mechanic | adavis@rivierabch.com | (561) 845-3485 |  | Operator Of the Facility | Larry Brown | (561) 845-4177 |  | lbrown@rivierabch.com | 07/25/2017 07:15 AM | 07/25/2017 01:10 PM | Palm Beach |  |  | 26.788995 | -80.095906 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=103
Sanitary Sewer Overspill |  | July 19, 2017 at 9:44pm sanitary sewer overspill occurred at Lift Station #50 into a catch basin north of the station. The cause of the spill was from a F.P.L. power failure which caused the pumps to fail which lead to wet well overflowing. | 07/28/2017 12:28 PM | City of Riviera Beach | 600 West Blue Heron Blvd; Riviera Beach FL; 33404 | 900 Avenue U and Martin Luther King Blvd. north | Allen J. Davis | Superintendent | adavis@rivierabch.com | (561) 845-4185 | 4186 | Operator Of the Facility | Joseph Jackson | (561) 845-3485 |  | jjackson@rivierabch.com | 07/19/2017 09:45 PM | 07/19/2017 10:40 PM | Palm Beach |  |  | 26.771777 | -80.084063 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=102
Wastewater Spillage | 20175653 | Sanitary Sewer Overspill at LS#20 due to old asbestos cement pipe collapsed. The 8" line was discovered Thursday morning at 7:00am. SSO Procedures followed, staff started cleaning process by using vacuum truck and SSO Trail. Sample taken, Lime applied. Completed at 1:43pm. | 07/28/2017 11:54 AM | City of Riviera Beach | 600 West Blue Heron Blvd; Riviera Beach FL; 33404 | North of Blue Heron Blvd and Central Industrial Drive. | Allen J. Davis | Superintendent | adavis@rivierabch.com | (561) 845-4185 | 4186 | Operator Of the Facility | Joseph Jackson | (561) 845-3485 |  | jjackson@rivierabch.com | 07/27/2017 07:00 AM | 07/27/2017 01:45 PM | Palm Beach |  |  | 26.788665 | -80.095879 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=101
MSP - LOADER - NPDES OUTFALL 004 - 07172017 | 20175335 | A front-end loader, operated by a Mosaic employee, traveling along a mine road, broke through a berm and overturned within an NPDES out-fall conveyance ditch, which created a sheen on the discharging water. There was visible indication that sheen was passing through the out-fall's V-notch weir. It is undetermined at this time whether the sheen is coming from the exterior of the machine being washed by the discharge effluent; or, if the diesel tank has been compromised. The amount of released fuel has not been determined at this time. | 07/28/2017 10:20 AM | Mosaic South Pasture Mine | 2220 Mineview Road; Bowling Green FL; 33834 |  | Santino Provenzano | Sr. Mgr. EHS | santino.provenzano@mosaicco.com | (863) 486-3762 |  | Sr. Mgr. EHS | Wayne Albritton | (863) 781-6379 |  | wayne.albritton@mosaicco.com | 07/17/2017 05:55 AM | 07/17/2017 08:45 AM | Hardee | Hardee | Y | 27.582454 | -81.948909 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=100
1302 NW 169th ave - 6" FM break | 20175655 | on 7-27-17 at 1230 pm a call was received pertaining to a leak in grassy area between curb and sidewalk, it was deemed to be sewer line was isolated and system shut down to make repair. In time of incident it was estimated that 100 gallons of raw sewer was discharged to the drainage box 200 ft south of break site which dumped into retention lake 50ft to the west of the box. The line was dug up and bad section was removed and replaced. System was leak checked and normal flow resumed. Installed proper bedding and backfilled area with compaction. | 07/28/2017 08:16 AM | City of Pembroke Pines | 8300 S palm Dr; Pembroke Pines FL; 33025 |  | Ron Abel | D&C supervisor | ron.abel@ch2m.com | (321) 288-0037 |  | Operator Of the Facility | Dan Stark | (478) 361-5244 |  | dan.stark@ch2m.com | 07/27/2017 12:30 PM | 07/27/2017 01:00 PM | Broward |  |  | 26.016879 | -80.373262 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=99
Valrico AWWTF, 1167 N. Dover Road, Dover FL, 33527 | 20175649 | On 7/27/17 at 12:00am the Valrico AWWTF lost communication with the NTU and pH meters on SCADA and was not being trended or recorded, however they were working in the field. From 12:00am on 7/27 to 7:00am on 7/27 our NTU and pH readings were not being trended or recorded. The on duty operator did not notice this communication fault. A NTU and pH comparison was taken at 11:20pm on 7/26 and the lab NTU reading was 0.44 and the pH reading was 7.34. One field reading was taken at 05:10am and the NTU and pH was 0.42 and 7.34, respectively. The operators started 15 minute NTU and pH readings at 7:00am until 8:30am on 7/27 and the NTU readings were between 0.40-0.46 and the pH readings were between 7.37-7.40. The SCADA trends for July 26th showed NTU readings between 0.28-0.48 and pH between 7.33-7.43. The SCADA trending for UVT (transmittance/effluent clarity) for the UV system was between 66.09%-66.78% from 12:00am to 7:00am on 7/27. Also, our effluent TSS for this day was 0.1 mg/L. ¿ The amount of water that was not being trended or recorded for NTU and pH was 1,600,000 gallons which went to the reclaim tanks. ¿ Regulatory Agency notification was made to Erica Peck with DEP at 9:10am, David with EPC at 9:15am, and State Warning Point at 9:20am, case #2017-5649. ¿ There is no immediate impact to residences or businesses. | 07/27/2017 04:49 PM | Valrico AWWTF, 1167 N. Dover Road, Dover FL, 33527 FL0040983 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | RICHARD CUMMINGS | (813) 209-3003 |  | CUMMINGSR@HILLSBOROUGHCOUNTY.ORG | 07/27/2017 12:00 AM | 07/27/2017 07:00 AM | Hillsborough |  |  | 27.958369 | -82.229953 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=98
Diesel Fuel Release | 5561 | An MCI Express truck spilled approximately 50 gallons of diesel fuel to the asphalt lot and nearby storm drain. Approximately 300ft x 20ft of asphalt area was impacted. A contractor responded to perform cleanup operations. Granular absorbents were placed to the impacted asphalt lot. The used absorbents and waste debris were containerized into (1) 55 gallon metal drum. Approximately 800 gallons of diesel impacted water was pumped from the affected storm drain using a vac-truck. All waste was taken offsite with the contractor for disposal. | 07/27/2017 01:00 PM | Coca-Cola Beverages Florida | 3350 Pembroke ; Hollywood FL; 33021 |  | Philip Blashford | Project Manager | pblashford@ertsonline.com | (440) 349-2700 | 410 | 3rd Party agent for Coca-Cola | Philip Blashford | (440) 349-2700 | 410 | pblashford@ertsonline.com | 07/24/2017 04:40 AM | 07/24/2017 07:30 AM | Broward |  | N | 25.994861 | -80.176446 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=97
Sump Integrity Test |  | While conducting our annual storage tank testing the STP sump for the gasoline tank failed. We are currently investigating if a release has occurred. Palm Beach CNTY Schools-West Trans 1901 NW 16th Ste. Belle Glade, FL 33430-1201 Facility ID: 8630624 | 07/27/2017 12:31 PM | Palm Beach CNTY Schools-West Trans | 1901 NW 16th St. ; Belle Glade FL; 33430 |  | Anne P. Meador | Environmental Specialist | anne.meador@palmbeachschools.org | (561) 684-5142 |  | Owner Of the Facility | Anne Meador | (561) 684-5142 |  | anne.meador@palmbeachschools.org | 07/26/2017 03:00 PM |  | Palm Beach |  |  | 26.703176 | -80.682893 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=96
Sewer spill Pineapple Park community | 20175623 | Lift station lost power causing the gravity system to surcharge during a force main condition assessment. Manholes over flowed spilling about <500 gal. The spill went into a storm drain that cause a body of water to be affected. Location of the incident was on 3 streets : Delphia, Market, New York and cross street Dock. Estimated affected area: 3 manholes 5'x5' each and 60' area storm drain. Cleaned area with lime, vac truck and disinfectant. Put turbidity barriers a the outflows at the stub canal. | 07/27/2017 10:05 AM | West Palm beach | FL |  | Charles L Phoenix Jr | Superintendent Sanitary Collection | CPhoenix@wpb.org | (561) 822-2181 |  | Operator Of the Facility | Charles L Phoenix Jr | (561) 822-2181 |  | Cphoenix@wpb.org | 07/26/2017 12:30 PM | 07/26/2017 03:30 PM | Palm Beach |  |  | 26.695629 | -80.063921 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=95
Gas Spill from Accident with injury | 2017008880 | Approximately 50 gallons of gasoline spilled on an accident with injury at 11998 Loxahatchee Rd Parkland, FL. | 07/27/2017 09:14 AM | Roadway | 11998 Loxahatchee Rd; Parkland FL |  | Alyssa Picotte | Supervisor | apicotte@coralsprings.org | (954) 344-1800 |  | Coral Springs Police Department Communication Cent | Assistance Fire Chief John Whalen | (754) 224-1978 |  | jwhalen@coralsprings.org | 07/27/2017 08:20 AM |  | Broward |  |  | 26.33454 | -80.227329 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=94
Notification of Wastewater Release 7/25/17 | 20175605 | On July 25, 2017 at approximately 4 PM, GRU was notified of an active wastewater release. The release occurred within a powerline easement in a heavily wooded area in the vicinity of NE 16th Ave and Waldo Rd. By 4:30 PM, GRU crews arrived on site and took immediate action to stop the flow. By 5:30 PM the flow was stopped. Upon inspection it was determined that a section of 14-inch wastewater forcemain had failed. By 7:30 PM GRU crews had the forcemain repaired and returned to service. Due to heavy stormwater flow in the area, it was very difficult to estimate the total volume of the release. Through hydraulic modeling and visual observation, it is estimated that approximately 80,000 gallons of wastewater was released and travelled through an open ditch into Sunnyland Creek. Water quality sampling has begun and will continue until background levels are at an acceptable level. Advisory signs have been placed in the impacted area. The State Watch Office, ACEPD and the Alachua County Health Department were notified in a timely manner. The SWO incident number for this event is 2017-5605. Coordinates for this event are 82¿17'5.743"W, 29¿40'0.178"N. The collection system flows to the Main Street Water Reclamation Facility (FL0027251). | 07/26/2017 03:32 PM | GRU Wastewater Collection System | Vicinity of NE 16th Ave and Waldo Rd; Gainesville FL; 32601 | Release occurred within a power line easement in a heavily wooded area east of NE 16th Ave and Waldo Rd. | Jennifer McElroy | Supervising Utility Enigneer | mcelroyja@gru.com | (352) 393-1291 |  | Supervising Environmental Engineer | Jennifer McElroy | (352) 393-1291 |  | mcelroyja@gru.com | 07/25/2017 04:00 PM | 07/25/2017 05:30 PM | Alachua |  |  | 29.666213 | -82.284464 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=93
3383 S Suncoast Blvd., Homosassa, FL 34446 |  | D.A.B. Construction Inc. / Plus Dewatering Group was installing well point on the Hwy-19 project in Homosassa. Plus Dewatering Group drilled into the 8" force main causing it to rupture. Sewage was contained in the trench where they were working. Citrus County Utilities valved off force-main. The road contractor, D.A.B, had A-Able septic company clean the area using a pump truck, lime the effected area, and then D.A.B repaired the force-main. Spoke with contractor / D.A.B. foreman and he assured us that more care would be used when excavating. Also we identified isolation valves for the contractor. We are going to remark force-main for contractor. | 07/26/2017 09:20 AM | Meadowcrest Collection System | 6000 W. Frontier Lane; Beverly Hills FL; 34465 |  | Charles Thompson | Maintenance Supervisor | Charles.Thompson@citrusbocc.com | (352) 400-0846 |  | Maintenance Supervisor | Charles Thompson | (352) 400-0846 |  | Charles.Thompson@citrusbocc.com | 07/25/2017 03:00 PM | 07/25/2017 03:30 PM | Citrus |  |  | 28.812698 | -82.575934 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=92
Albaa Logistics Inc | 20175406 | Florida Division of Emergency Management State Watch Office Incident Report Main Information Report #: 2017-5406 Status: Assigned Reported to SWO on: 7/18/2017 20:34 ET Severity: Local Incident Description: I-75 NB Closure w/ Diesel Spill This situation involves: Petroleum Spill, Road Closure or DOT Issue Affected Sectors: DEP District - Northeast, DEP OER Jacksonville On-Call Initial Report: Northbound lanes of I-75 are closed near MM 375 in Micanopy due to a semi-truck striking the Wacahoota Road overpass near this location. The driver of the semi-truck suffered non-traumatic injuries, and approximately 100 gallons of diesel also spilled from the saddle tanks of the truck. No waterways were impacted by the spill, and no fires resulted from the crash. Alachua Co SO, Alachua Co FR, and FHP units are all currently on scene. FDOT has been notified by the county, and they will have a crew en route to check the structural integrity of the overpass. Injuries: Yes (1 - routine transport) Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: Yes DEP callback requested: No Incident Occurred: 7/18/2017 20:11 ET Most Recent Update Date/Time: 07/18/2017-20:41 ET Most Recent Update: N/A Affected Counties: Alachua Facility Name or Description: I-75 375N MILE MARKER Incident Location: Address: City: I-75 Zip: USNG: 17RLN7365465720 Coordinates: Lat: 29.5147, Long: -82.30364 | 07/26/2017 08:44 AM | Albaa Logistics Inc | I-75 NB @ Wacahoota Road Overpass; Micanopy FL; 32667 | NB I-75 to Wacahoota Road Overpass | Christopher Gilbert | Senior Environmental Specialist | cgilbert@alachuacounty.us | (352) 264-6842 |  | Alachua County Environmental Protection Dept. | Alan Chandler | (352) 472-7295 |  | alan.chandler@aagenvironmental.com | 07/18/2017 08:00 PM | 07/19/2017 02:00 AM | Alachua |  |  | 29.52253 | -82.309712 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=91
Lift Station Overflow | 20175604 | Lift station overflowed. 2 pumps have been replaced, and area has been cleaned/sanitized. Also, sampling done on creek (spill area, upstream, and downstream) through TestAmerica so make sure pollution has not occured. | 07/25/2017 06:39 PM | Water's Edge Apartment Homes | FL |  | Steven Romulus | Property Manager | sromulus@zrsmanagement.com | (850) 477-0600 |  | Operator Of the Facility | Steven Romulus | (850) 477-0600 |  | sromulus@zrsmanagement.com | 07/25/2017 10:00 AM | 07/27/2017 09:00 AM | Escambia |  | N | 30.529685 | -87.212094 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=90
Village Water Wastewater Treatment Plant Effluent Pond Disch | 20175596 | Received notification from Operator that while he was onsite today (at approx 915 am) found East pond discharging (treated effluent) through the overflow to the adjacent ditch and wetlands area. Heavy rains in the local area are believed to have contributed to the elevated pond levels - the operator has recorded 12 inches of rain received at the plant in July 2017. It is estimated that approx 700 gallons has discharged, but discharge is currently ongoing - SWP# 2017-5596. The discharge is being sampled by the operator for CBOD, TSS, Nitrate and Fecal. In review of the log book, 12 inches of rain have been received at the treatment plant during the month of July 2017; Influent flow for the past seven days was 0.390 MGD total / 0.056 MGD Average Daily flow. Operator will continue to monitor and sample and report as required. The staff gauges are currently at West - 10.4 / East 8.4 | 07/25/2017 01:56 PM | Village Water WWTF | 4411 Maine Avenue; Eaton Park FL; 33801 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 | 207 | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 07/25/2017 09:15 AM |  | Polk |  |  | 28.010933 | -81.864943 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=89
12 inch Force Main Break | 20175248 | Wastewater force main broke, due to a pipe failure. The estimated discharge is 480 gal. An unknown amount reached a storm drain, which leads to a tidal water canal. Lift Stations were shut-down to isolate the break; tanker trucks were used to maintain wastewater system flow. | 07/25/2017 11:50 AM | Broward County NRWWTP | 2401 N. Powerline Road; Pompano Beach FL; 33069 |  | Carlos Morejon | Operations Manager | cmorejon@broward.org | (954) 831-0861 |  | First Responder | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 07/13/2017 08:15 AM | 07/13/2017 10:00 AM | Broward | Broward | Y | 26.28103 | -80.092442 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=88
Septage Facility Sewage Spill | 20175304 | Raw sewage spilled to ground as Mechanics were replacing a clean out valve. Estimated 120 gallons discharged, some reached roadway to the north of the septage plant; no water body impact. Discharge was collected with vac-truck, area clean up completed with HTH disinfectant. | 07/25/2017 11:50 AM | Broward County NRWWTP | 2401 N. Powerline Road; Pompano Beach FL; 33069 |  | Metason Phillip | Operations Superintendent | mphillip@broward.org | (954) 831-0861 |  | First Responder | Clive Haynes | (954) 831-0851 |  | chaynes@broward.org | 07/14/2017 10:20 AM | 07/14/2017 10:21 AM | Broward | Broward | Y | 26.268314 | -80.150892 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=87
Chandler Estates Sewer Forcemain Leak | 20175590 | The forcemain in the Chandler Estates subdivision had a crack in it that was leaking. The forcemain was isolated and repairs were completed. Used a Vac Con truck to suck up all standing water. Lime was applied to the affected area following repairs. | 07/25/2017 11:22 AM | City of Apopka | 748 E Cleveland St; Apopka FL; 32703 |  | Jorge Garcia | Utility Foreman | jgarcia@apopka.net | (407) 703-1731 |  | Operator Of the Facility | Kevin Burgess | (407) 703-1731 |  | kburgess@apopka.net | 07/24/2017 01:15 PM | 07/24/2017 02:30 PM | Orange |  |  | 28.710219 | -81.576273 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=86
4377 Heckscher Dr | 20175593 | Hydrogen seal leaked seal oil into generator floor containment trench. 150 gallons of seal oil were leaked into the containment trench. | 07/25/2017 10:34 AM | JEA Northside Generating Station | 4377 Heckscher Dr; Jacksonville FL; 32226 |  | Christina Jacobs | Environmental Scientist Senior | jacocb@jea.com | (904) 665-6283 |  | Environmental Scientist Senior | Christina Jacobs | (904) 665-6283 |  | jacocb@jea.com | 07/25/2017 07:00 AM | 07/25/2017 10:30 AM | Duval |  | N | 30.41705 | -81.552474 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=85
176115- 111 Burnsed Pl SSO | 20175589 | Summary information for BCC Seminole County Environmental Services (BCCSCESD) Installation Name: Canterbury Cove Lift Station Installation Address: 111 Burnsed PL, Oviedo, Fl 32765 Installation Location: Manhole-PSMH: SE118-2 State Warning Point Report# 2017-5589 Spill Report Incident #: 176115 Point of Contact: Ralph Terrero Permit Number (if facility/installation holds permit): FL0037966 (Iron Bridge) Date and Time of Incident or Discovery: 7-23-17 @1:00pm Date and Time the Spill was Stopped: 7-23-17 @ 1:35pm Location of the Incident or Discovery: 30min Suspected Sources and Cause of Incident or Discovery: Release from manhole SE118-2 due to loss control fuse for pump control circuit @ Canterbury Cove lift station. Type of Pollution, including Substance or Contaminant Name(s):RAW wastewater Amount of Pollution, including Substance or Contaminant Name(s): 50gal Medium (e.g. land, water air) Affected by Pollution: Land Potentially Affected Areas beyond Installation Property Boundary: N/A Potential Risk to the Public Health, Safety or Welfare: None area has been disinfected Identification of other Parties Notified of this Incident is Provided Below: Date and Time Parties were Notified: 7-23-17 @ 3:15pm City of Oviedo: City Manager Bryan Cobb Bcobb@cityofoviedo.net Mayor Dominic Persampiere Dpersampiere@cityofoviedo.net DEP: pollution.notice@dep.state.fl.us Seminole County Personnel for all Spills: Chairman BCC John Horan JHoran@seminolecountyfl.gov County Manager Nicole Guillet nguillet@seminolecountyfl.gov Deputy County Manager Bruce McMenemy bmcmenemy@seminolecountyfl.gov Assistant County Manager Meloney Lung mlung@seminolecountyfl.gov Chief Administrator Tricia Setzer tsetzer@seminolecountyfl.gov Community Relations Officer Ashley Moore Amoore@seminolecountyfl.gov Interim Director ES/Utilities Ops. Manager Ralph Terrero rterrero@seminolecountyfl.gov SW Manager/Interim Utilities Engineering Manager William (Johnny) Edwards WEdwards@seminolecountyfl.gov Chief Wastewater Treatment Plant Operator David Engstrom dengstrom@seminolecountyfl.gov Wastewater Operations Manager Jack Cheney jcheney@seminolecountyfl.gov Utilities Enterprise Asset Manager Mike Riley mriley@seminolecountyfl.gov Utilities Operations Coordinator Robert Green rgreen07@seminolecountyfl.gov Field Operations Manager Bob Green rgreen08@seminolecountyfl.gov Utilities Work Planner Tom Owens towens02@seminolecountyfl.gov Collections Supervisor Jeff Lane JLane@seminolecountyfl.gov CMMS Coordinator Paul Stoute pstoute@seminolecountyfl.gov SCADA SCADA@seminolecountyfl.gov Water & Sewer Customer Service WSCustomerService@seminolecountyfl.gov Utilities Inc. of Florida-Sanlando: Customer Services customerservice@uiwater.com Please do not respond to this email. For more detailed information, see contact below: Seminole County Environmental Services, After Hours Emergency Contact at 407.665.0005. If the spill occurred outside of your jurisdiction, please disregard this email. Should you have any questions, please call 407.665.2767. Regards, Seminole County Environmental Services Department Jeff Lane, Collection Supervisor Seminole County Government Environmental Services Department Water & Waste Water Division Office 407-665-2885 Cell 407-782-1225 | 07/25/2017 08:46 AM | Canterbury Cove lift station | 111 Burnsed Pl; Oviedo FL; 32765 |  | Jeff Lane | Collection Supervisor | jlane@seminolecountyfl.gov | (407) 665-2885 |  | Owner Of the Facility | Jeff lane | (407) 665-2885 |  | jlane@seminolecountyfl.gov | 07/23/2017 01:00 PM | 07/23/2017 01:35 PM | Seminole |  |  | 28.638878 | -81.206524 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=84
2017-5573 Diesel Fuel Release Hialeah, FL | 20175573 | On 7/24/17 at 1055 hours, a CSX employee, advised that a FDOT contractor reported a diesel fuel spill from mobile fueling on the Scale Track in the Hialeah Yard of 20 - 25 gallons. The release affected ballast, railroad subbase, and a portion of the asphalt road. SWS and Arcadis were dispatched to conduct cleanup activities. The affected material was removed via excavation and the excavation was guided by visual observation and OVA measurements using an FID. No free product was observed and no water ways were affected. The final excavation extents were approximately 22 feet long, up to 6 ft wide and 2-inches to 10 inches deep. Post excavation OVA measurements were below 10 parts per million. | 07/24/2017 08:50 PM | Florida Department of Transportation | 9400 NW 37th Avenue; Hialeah FL; 33013 |  | Brooke Martin | Manager Hazardous Materials | brooke_martin@csx.com | (800) 232-0144 |  | CSX Employee | Brooke Martin | (800) 232-0144 |  | brooke_martin@csx.com | 07/24/2017 10:55 AM | 07/24/2017 05:45 PM | Miami-Dade |  |  | 25.855917 | -80.259619 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=83
Eastwood Shores Condominiums | 20175581 | There was a sanitary Sewer Overflow from a privately owned collection system - Eastwood Shores Condominiums (1883 Lichen Lane, Clearwater, FL). Approximately 4,800 gal. of untreated sewage overflowed from a manhole into a a nearby storm drain leading to Tampa Bay. The City of Largo responded, the vac crew jetted and cleaned the line and it was determined that grease caused the overflow. (Water Basin - Long Branch). | 07/24/2017 04:49 PM | Eastwood Shores Condominiums | Bough Ave and Lichen Lane; Clearwater FL; 33760 | A manhole between Bough Ave and Lichen Lane overflowed due a grease blockage. | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 07/24/2017 10:30 AM | 07/24/2017 12:05 PM | Pinellas |  |  | 27.929327 | -82.714397 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=82
3102 St Johns Ave | 20175565 | Broken pipe on a sewer force main caused overflow. 50 gallons of sewer released to storm drain that discharges into the St Johns River. | 07/24/2017 03:19 PM | Private Residence | 3102 St Johns Ave; Jacksonville FL; 32205 |  | J Bowden | Incident Response | bowdjt@jea.com | (904) 252-5471 |  | Incident Responder | J Bowden | (904) 252-5471 |  | bowdjt@jea.com | 07/23/2017 08:30 AM | 07/23/2017 11:15 PM | Duval |  | N | 30.30228 | -81.696862 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=81
12680 Ashly Mellisse | 20175532 | Unknown motor vehicle hit a pad mounted transformer, accident caused transformer to release non-PCB oil. | 07/24/2017 09:59 AM | JEA Transformer | 12680 Ashly Melisse Blvd; Jacksonville FL; 32225 |  | Glenn Davis | Incident Response | Davige@jea.com | (904) 591-4777 |  | Incident Response | Glenn Davis | (904) 591-4777 |  | davige@jea.com | 07/22/2017 05:30 PM | 07/22/2017 09:50 PM | Duval |  |  | 30.334093 | -81.4719 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=80
Berth 7 Fuel Spill |  | Fuel was spilled in the surface water at Berth 7 at Port Manatee during and as a result of vessel fueling operation. The source was immediately discovered and neutralized. Spill quantity was reportedly one gallon. Sheen on the water appeared consistent with the reported quantity. Absorbent boom was used to clean up the spill. Incident was reported to National Response Center. Coast Guard responded. Ship's Engineer reported that the cause of the spill was identified and rectified. The spill has been cleaned up. | 07/24/2017 09:59 AM | Port Manatee | 300 Tampa Bay Way; Palmetto FL; 34221 | West from US 41 on Piney Point Road. Enter Port Manatee at it's Access Control facility on the south side of Piney Point Road. Give the "Berth 7" location to Security Department. | George F. Isiminger, P.E. | Senior Director of Planning, Engineering and Environmental Affairs | gisiminger@portmanatee.com | (941) 650-3451 |  | Member of staff of owner of the overall facility. | Virginia Zimmermann | (941) 722-6621 |  | vzimmermann@portmanatee.com | 07/23/2017 10:45 AM | 07/23/2017 02:00 PM | Manatee |  |  | 27.635031 | -82.558769 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=79
7834 Holiday Road | 20175536 | Sewer lift station was over loaded with storm water intrusion, which caused sewer from the lift station to overflow in Pottsburg Creek.7/27/2017 JEA update to spill volume for Holiday Road SSO ¿ After further analysis from simulated flow models using SCADA data from the affected lift station and nearby lift stations, the SSO that occurred at the Holiday Rd lift station on Saturday 7/22/2017 is estimated to be 22,500 gallons. | 07/24/2017 09:48 AM | JEA Lift Station S545 | 7834 Holiday Road; Jacksonville FL; 32216 |  | Glenn Davis | Incident Response | Davige@jea.com | (904) 591-4777 |  | Incident Response | Glenn Davis | (904) 591-4777 |  | davige@jea.com | 07/22/2017 03:45 PM | 07/22/2017 05:20 PM | Duval | Duval | Y | 30.294359 | -81.574416 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=78
Diesel Spill / L-18 Canal | 20175566 | NATIONAL RESPONSE CENTER 1-800-424-8802 *** For Public Use *** Information released to a third party shall comply with any applicable federal and/or state Freedom of Information and Privacy Laws Incident Report # 1185029 INCIDENT DESCRIPTION *Report taken at 08:53 on 24-JUL-17 Incident Type: FIXED Incident Cause: OPERATOR ERROR Affected Area: L18 CANAL Incident occurred on 23-JUL-17 at 08:30 local incident time. Affected Medium: WATER / L18 CANAL ____________________________________________________________________ SUSPECTED RESPONSIBLE PARTY Organization: SOUTH FLORIDA WATER MGMT DISTRICT WEST PALM BEACH, FL 33406 Type of Organization: STATE GOVERNMENT _____________________________________________________________________ INCIDENT LOCATION 15 MILES 2300 US 27 County: PALM BEACH City: PALM BEACH State: FL Latitude: 26? 20' 08" N Longitude: 080? 32' 12" W ____________________________________________________________________ RELEASED MATERIAL(S) CHRIS Code: ODS Official Material Name: OIL: DIESEL Also Known As: Qty Released: 0 UNKNOWN AMOUNT Qty in Water: 0 UNKNOWN AMOUNT ____________________________________________________________________ DESCRIPTION OF INCIDENT CALLER STATED THAT APPROXIMATE 0.5 GALLONS OF DIESEL FUEL DISCHARGED INTO THE L18 CANAL WHEN A PUMP STATION OPERATOR MISTAKENLY EMPTIED A HOSE INTO THE CANAL. ___________________________________________________________________ INCIDENT DETAILS Package: NO Building ID: S7 PUMP ST Type of Fixed Object: DAM Power Generating Facility: UNKNOWN Generating Capacity: Type of Fuel: NPDES: NPDES Compliance: UNKNOWN ---WATER INFORMATION--- Body of Water: L18 CANAL Tributary of: Nearest River Mile Marker: Water Supply Contaminated: UNKNOWN ____________________________________________________________________ ____________________________________________________________________ REMEDIAL ACTIONS BOOMS APPLIED,ABSORBENTS APPLIED Release Secured: YES Release Rate: Estimated Release Duration: __________________________________________________________________ | 07/24/2017 09:18 AM | South Florida Water Management District - Pump Station S-7 | 23000 US 27 (at Palm Beach/Broward Co. Line); Belle Glade FL; 33440 | On east side of US 27 at Palm Beach/Broward Co. line. | Jeffrey Smith | Lead Environmental Scientist | jesmith@sfwmd.gov | (561) 248-2451 |  | Owner Of the Facility | Jeffrey Smith | (562) 248-2451 |  | jesmith@sfwmd.gov | 07/23/2017 08:30 AM | 07/23/2017 09:30 AM | Palm Beach |  |  | 26.335437 | -80.536713 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=77
Lift Station Overflow | 20175534 | At 1700 a report was made that the lift station at Bens Lake Marina Bldg 2808 located on Eglin AFB was overflowing. The lift station has secondary containment to prevent discharge to Bens Lake water body. However, the amount of flow at the time resulted in an estimated 150 gallons of wastewater to overflow on the ground and some of the flow made it to Bens Lake water body. The lift station was restored to normal operation around 1730. The affected area on land was treated with lime. Approximately 80% of the flow from this lift station comes from the fish cleaning station. The other 20% comes from 2 small restrooms near the boat ramp area. | 07/22/2017 08:58 PM | Bldg 2808 | Boatner Road; Eglin AFB FL; 32542 | Bldg 2808 Boatner Road Eglin AFB Fl. | Travis Adams | Environmental HEalth & Safety Supervisor | travis.adams@ecus.asusinc.com | (850) 333-5614 |  | Utility Privitization Contractor | Travis Adams | (850) 333-5614 |  | travis.adams@ecus.asusinc.com | 07/22/2017 05:00 PM | 07/22/2017 07:00 PM | Okaloosa |  |  | 30.453419 | -86.543035 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=76
City of Lakeland - Skyview Blvd |  | At 17:50 we received a call from a home owner at 1347 Skyview Blvd. of a sewer backup into 3 apartment units along Skyview Blvd. Upon arrival discovered main line was surcharged due to heavy rains in the area. Event stopped at 19:30. The estimated discharge was 250 gallons which was occurring intermittently as upstream pump stations would come on surcharging the downstream main line. | 07/22/2017 02:24 PM | City of Lakeland NPDES Permit No FL0039772 | 1528 Glendale Street; Lakeland FL; 33803 - 4300 |  | Richard Ruede | Manager of Wastewater Collection | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede` | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 07/21/2017 05:50 PM | 07/21/2017 07:30 PM | Polk |  |  | 28.026192 | -81.899287 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=75
City of Lakeland - Westside Pump Station |  | At 16:30 Pm we received a call from a home owner at 1619 Plateau Ave regarding sewer leaking out from a manhole outside our Pump Station. Crew was dispatched to the site and it was stopped at 19:30. Estimated quantity of 800 gallons was spilled into a stormwater drainage ditch running along Plateau Ave. Incident was reported to the City's Lake and Stormwater division on 7/22/2017. Cause of the event was Inflow due to a heavy rain event that had occurred in the area. | 07/22/2017 02:06 PM | City of Lakeland NPDES Permit No FL0039772 | 1825 Glendale Street; Lakeland FL; 33803 - 4300 |  | Richard Ruede | Manager of Wastewater Collection | richard.ruede@lakelandgov.net | (863) 834-8277 |  | Operator Of the Facility | Richard Ruede | (863) 834-8277 |  | richard.ruede@lakelandgov.net | 07/21/2017 04:30 PM | 07/21/2017 07:30 PM | Polk |  |  | 28.036855 | -81.989063 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=74
7-20-17 South Water Reclamation Facility | 20175502 | A construction contractor struck 2 wastewater treatment plant process lines with an excavator. The lines convey chlorinated and public-access-level treated reclaimed water used for disinfection in the wastewater treatment plant process. 1,320 gallons of chlorinated reclaimed water were released. This incident coincided with the onset of an intense storm event, and the discharge mingled with rain water. The spill was contained on-site by high water levels in the storm water system. The storm water system had surcharged and was also discharging into the site. A plug was placed in the storm water system once the rain subsided to prevent the discharge from draining off site. The discharge / rainwater mixture soaked into the ground. | 07/21/2017 04:22 PM | OCU South Water Reclamation Facility | 4760 Sand Lake Road; Orlando FL; 32819 |  | Laura Woodbury | Sr. Engineer | Laura.Woodbury@ocfl.net | (407) 836-6826 |  | Sr. Engineer, Field Services | Mark Robinson | (407) 254-6791 |  | Mark.Robinson@ocfl.net | 07/20/2017 06:10 PM | 07/20/2017 08:10 PM | Orange |  | N | 28.446101 | -81.440857 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=73
Apparent leak in buried piping. | 20175494 | Florida Division of Emergency Management State Watch Office Incident Report Main Information Report #: 2017-5494 Status: Assigned Reported to SWO on: 7/21/2017 11:40 ET Severity: Local Incident Description: Petroleum Release Affected Sectors: DEP District - Southeast, DEP OER West Palm - Day Initial Report: Caller reports a petroleum release in Broward County. An unknown amount of gasoline was released due to corrosion on an underground pipeline in Ft. Lauderdale. The caller reports that the release did not enter any storm systems or waterways. Cleanup actions are in progress. Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: No Incident Occurred: 7/20/2017 11:40 ET Most Recent Update Date/Time: 07/21/2017-11:54 ET | 07/21/2017 02:37 PM | TransMontaigne - Port Everglades FL - South Terminal | 2701 SE 14th Avenue (Berth 13); Fort Lauderdale FL; 33316 |  | Andy McClish | Mgr. Regulatory Compliance - TransMontaigne | amcclish@transmontaigne.com | (770) 518-3701 |  | Environmental/Regulatory Support Staff (see Title) | Andy McClish | (770) 518-3701 |  | amcclish@transmontaigne.com | 07/20/2017 09:00 AM | 07/20/2017 09:05 AM | Broward |  |  | 26.091656 | -80.122899 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=72
reclaimed water discharge |  | At 12:10 am on July 21,2017 a reclaimed water line broke discharging approximately 300 gallons into the collection system. It was stopped at 1am. | 07/21/2017 11:23 AM | bradenton WRF | 1810 first street west ; Bradenton FL; 34208 |  | Bill Waitt | Chief Operator | william.waitt@cityofbradenton.com | (603) 490-8969 |  | Operator Of the Facility | Bill Waitt | (603) 490-8969 |  | william.waitt@cityofbradenton.com | 07/21/2017 10:07 AM | 07/21/2017 11:20 AM | Manatee |  |  | 27.606599 | -82.409157 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=71
DWU WWTP | 20175489 | At about 4pm yesterday afternoon (7/20) for about 6 minutes, DWU had an overflow of our effluent splitter box which occurred while returning the WWTP chlorination system back to service from a planned chlorine system maintenance event. There was a surge of flow into the area caused by a brief downpour immediately prior to the event. The one effluent pump in service was not able to keep up. The water that spilled was treated for Part IV Reclaimed water, but at the time of overflow the water was being rejected, rather than going to our RIBs. The area was limed. This treated Part IV reclaimed water was contained on site in stormwater ponds and swales. There was about 9,000 gallons believed to have overflowed. No reclaimed water entered any water bodies. | 07/21/2017 08:57 AM | Destin Water Users Wastewater Treatment Plant | 14 Industrial Park Lane; Destin FL; 32541 | End of Industrial Park Lane, off Airport Road | Monica Autrey | Operations Manager | mautrey@dwuinc.com | (850) 699-3665 |  | Operator Of the Facility | Lockwood Wernet | (850) 200-2028 |  | lwernet@dwuinc.com | 07/20/2017 04:10 PM | 07/20/2017 04:15 PM | Okaloosa |  |  | 30.394276 | -86.478544 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=70
Sanitary Sewer Overflow | 20175465 | A contractor jacking and boring hit the City's force main, causing a sewer spill. Approximately 2,400 gallons of sewage was spilled. The total recovered volume is unknown at this time; a portion of the spill entered a storm drain connected to the San Sebastian River. | 07/20/2017 07:21 PM | Intersection of Nix Boat Yard Rd and US1 | ; St. Augustine FL |  | Glabra Skipp | Environmental Compliance Analyst | gskipp@citystaug.com | (904) 825-1055 |  | Environmental Compliance Analyst | Glabra Skipp | (904) 825-1055 |  | gskipp@citystaug.com | 07/20/2017 01:30 PM | 07/20/2017 02:35 PM | St. Johns |  |  | 29.870856 | -81.322982 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=69
SIGNET INTRUDER Fuel Spill | 20175445 | At about 0200 this morning while the SIGNET INTRUDER was fueling at NuStar Energy, #3 port fuel tank appeared to ¿burp¿ with 19.5 inches of room left in the fuel tank. This caused the fuel vent containment to overfill. The fuel that spilled on the deck was mostly caught by oil absorbent booms and quick response by the deck crew. At this stage of the fuel transfer, they were topping of #3 fuel tanks and had the #4 fuel tanks cracked open to slow the rate of flow into #3¿s. When the C/E saw the containment overflowing, he ordered that #3 tanks be shut and #4¿s opened the rest of the way. He then instructed the PIC on the dock to shut down the transfer. The deck crew then quickly responded to contain the spill, minimizing anything overboard. It has been reported that 15 gallons went into the water with an additional 25 contained on deck. | 07/20/2017 04:39 PM | NuStar Energy | 5401 Evergreen Avenue; Jacksonville FL; 32208 |  | Grayson Glover | Port Captain | grayson.glover@signetmaritime.com | (904) 738-4601 |  | Owner of vessel SIGNET INTRUDER | Grayson Glover | (904) 738-4601 |  | grayson.glover@signetmaritime.com | 07/20/2017 02:00 AM | 07/20/2017 02:30 AM | Duval |  |  | 30.376006 | -81.635647 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=68
Northeast Regional WRF FL0128937 | 20174954 | The total Spill of Reuse from the Northeast WRF was estimated at 2.179MGD. Email correspondence to FDEP/SWP is listed below. This email is a follow-up to the previous email, sent yesterday, Sunday, June 2, 2017, providing updated information regarding the incident that occurred at our Northeast Water Reclamation Facility. A private contractor, along with City repair crews, have temporarily repaired the leaking, 30¿ ductile iron, Reclaimed Water distribution pipe this evening. This temporary repair will remain in place until the City can engineer can implement a more permanent repair as soon as possible. The water that was discharging into both a storm water retention pond and a nearby reclaimed water storage pond is estimated to be approximately 1.3-million gallons. The initial discovery of the leak was reported as yesterday, June 2, 2017, but with further investigation and review of data, it was ascertained that the leak possibly started sometime Friday, June 30, 2017. Any additional leakage that may possibly occur from the temporary repair will be properly contained and reported in future emails This incident has been reported to the State Warning Point this afternoon. The Incident Number is 2017-4954. This email is a follow-up report providing updated information regarding the incident that occurred at our Northeast Water Reclamation Facility. A private contractor, along with City repair crews, have temporarily repaired the leaking, 30¿ ductile iron, Reclaimed Water distribution pipe. This temporary repair will remain in place until the City can engineer and implement a more permanent repair as soon as possible. This temporary repair is still presently leaking at a rate of approximately 40-gpm. This water is being collected and discharged into a nearby, City-owned, reclaimed water storage pond. This leak is anticipated to continue until the permanent repair can be completed. Since the temporary repair was completed last Monday, July 3, 2017 @ 10:30PM till Tuesday, July 4, 2017 @ 1:00PM, it is estimated that the leak was discharging at a rate of approximately 20-gpm. This was a total of 17,400-gallons. From July 4, 2017 @ 1:00PM till July 5, 2017 @ 3:00PM, the leakage increased to it¿s present rate of 40-gpm for an additional total of 62,400-gallons discharged. A temporary bypass system was installed so that Reuse will not flow through the damaged section of piping into the storm pond. Reuse will flow through the temporary bypass piping till the new relocated ductile iron pipe is installed. A project is on the way to replace the old piping that has failed with new 30" ductile iron pipe. This will also allow us to relocate the line out of the storm pond. Tentatively the estimated completion of the 30" ductile iron pipe is two weeks. | 07/20/2017 04:23 PM | Northeast Regional WRF FL0128937 | 3290 Safety Harbor ; Safety Harbor FL; 34695 |  | Jason Jennings | Wastewater Enviromental Technologies Division Manager | jason.jennings@myclearwater.com | (727) 562-4960 | 7221 | Owner Of the Facility | Dave Porter | (727) 562-4960 |  | david.porter@myclearwater.com | 07/02/2017 10:15 AM | 07/19/2017 03:00 PM | Pinellas |  |  | 28.027118 | -82.705259 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=67
Private Reclaimed Water Overflow - City of Orlando |  | On 07-20-17 at approximately 1137 AM, City of Orlando Environmental Specialist were notified and responded to a Reclaimed Water Overflow originating from a 1" privately owned reclaimed water line in the median of T.G. LEE BLVD approximately 50 feet east of the intersection with State Road 436. The overflow was quickly assessed and nearest shut off valve was isolated at 1150 AM. An estimated 360 gallons of reclaimed water were released during the event, all of which entered the nearest storm drain inlet closest to the overflow, and there was no ability to recapture any material from the storm drain. At this time, the shut off valve for the reclaimed water line will remain isolated until the necessary repairs are made to the private reclaimed line by the responsible party. | 07/20/2017 03:28 PM | City of Orlando | T G Lee Blvd; Orlando FL; 32822 | Take Semoran South towards Orlando International Airport. Turn Left onto T G Lee Blvd and the area of overflow will be in the median 50 feet after the intersection. | Kevin Layne | Environmental Specialist III | kevin.layne@cityoforlando.net | (407) 246-2152 |  | City of Orlando Water Reclamation Div employee | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 07/20/2017 11:35 AM | 07/20/2017 11:50 AM | Orange |  |  | 28.460334 | -81.309411 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=66
Chilled Water | 0 | The PPD Utilities and Energy Services Department have been tracking an increase in make-up water usage to our closed loop chilled water distribution network. After some field investigation (with dyes), we discovered some quantity of the leak was ending up in the sanitary system as indicated by dye showing up in lift stations and at the Waste Water Treatment plant. The system losses have also reached the stormwater system as indicated by dye showing up in storm water infrastructure and eventually in one campus creek at the stormwater outfall. Just as an FYI...we have determined that our leak of 35,000 GPD to 45,000 GPD has been significantly mitigated and may no longer be a storm water issue. As discussed previously, we were not really aware of how much of this volume was going to sanitary versus storm. Through the process of dyeing the chilled water distribution network, we knew some volume was indeed making it to storm. During an exhaustive field investigation, we did find a substantial leak that we traced to sanitary. That particular leak has been fixed and the total volume of leakage dropped to 10,000 GPD. Additionally, by tracing the dye upstream, we also discovered a building drain that was collecting chilled water. That drain was being diverted to an outside building sump drain which is routed to storm as its purpose is to redirect underground water away from the building. We have diverted that drain temporarily to sanitary until a permanent pipe repair can be made. In summary, current total lost volume of water is around 10,000 GPD and we believe that volume is being collected in the sanitary system. We have reviewed the MSD sheets with our WWTP. We hope to have the leak fully fixed in a few weeks. | 07/20/2017 02:48 PM | University of Florida, Lacy Rabon Chilled Water Plant | 1858 MOWRY RD ; Gainesville FL; 32611 | Lacy Rabon Chilled Water Plant 1858 Mowry Road | Matthew Doty | Hazardosu Materials Program Manager | mdoty@ehs.ufl.edu | (352) 392-8400 |  | Hazardous Material Program Manager | Matthew DOty | (352) 392-8400 |  | mdoty@ehs.ufl.edu | 07/20/2017 02:31 PM |  | Alachua |  |  | 29.640287 | -82.347546 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=65
Sheldon Rd. 200 yards South of W. Linebaugh Ave. | 20175434 | On 7-19-17 at 14:30 we received a call reporting a ruptured sewer line under Sheldon Rd. about 200 yards South of W. Linebaugh Ave. Upon arrival I (Jason Makinson) called ACME barricades for a double lane closure and then called HCSO for immediate support of closing down the traffic lanes due to the line being ruptured under the roadway. Once the lanes were closed and excavation was underway, the leak was found to be a nickel size hole in the side of the 8" DIP sludge line. Approximately 1800 gallons escaped the line before we were able to safely excavate the area. The team was able to install a full circle repair clamp on the line and stop the leak without isolating anything. All the soiled spoil was removed from the site and clean dry fill was brought for backfilling the area in lifts with the top layer being a load of millings. ACME barricades was called and the roadway was opened up. | 07/20/2017 10:34 AM | NORTHWEST RESIDUALS FL0041670001 | FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | JON JOHANSON | (813) 209-3088 |  | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | 07/19/2017 02:30 PM | 07/19/2017 06:00 PM | Hillsborough |  |  | 28.042463 | -82.582932 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=64
Northwest Regional Water Reclamation Facility FL0041670 | 20175435 | ¿ At 1000, contractor was digging around the NWRWRF plant Anox Basins when they hit and broke a six inch valve on a reclaim water line which released 15,000 gallons of reclaim. The operations staff shut down the in plant reuse (reclaim) pumps. The spill lasted for 10 minutes. All of the water was contained on the plant. Contractor replaced the valve at 1600. The in plant reuse (reclaim) was turned back on and the plant resumed normal operations. ¿ Hillsborough County is completing the SIR/SSO Report for the incident. The NWRWRF Plant Manager made contact with regulatory agencies as required. Regulatory Agency Notification: State Warning Point @ 1650, Operator #317 / Incident #2017-5435. FDEP @ 1654, left message for Erica Peck. EPC @ 1658, spoke to Daniel Moore. PUD Environmental @ 1704, left message for Adam Wood. | 07/20/2017 09:28 AM | Northwest Regional Water Reclamation Facility | 11005 Dale Stitik Dr., Tampa, Fl. 33626 FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | JON JOHANSON | (813) 203-3088 |  | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | 07/19/2017 10:00 AM | 07/19/2017 10:10 AM | Hillsborough |  |  | 28.07271 | -82.610062 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=63
Chateaubriand Ave, Orlando FL, 32836 | 20175417 | Broken Reclaimed Water Main ¿ ¿Possibly caused by a lightning strike to a tree adjacent to the reclaimed water main.¿ The broken main overflowed 6,000 gallons of reclaimed water. The affected areas include the paved road surface on Chateaubriand Avenue, Sidewalk, grass related storm drain inlet boxes and possibly the storm water retention pond on the north end of Wakeworth Street. There is minimal risk to Public Health, Safety or Welfare at this time. Field Services staff performed a complete wash down and cleaned all affected areas. Additionally Field Services staff made a complete recovery from the storm drain system (30,000 gallons) | 07/19/2017 05:18 PM | Orange County Utilities Water Reclamation System | FL |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Owner Of the Facility | Troy E. Layton | (407) 254-9794 |  | Tory.Layton@ocfl.net | 07/18/2017 05:10 PM | 07/18/2017 06:20 PM | Orange |  |  | 28.43065 | -81.554947 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=62
1621 South Alafaya Trail, Orlando, FL 32828 | 20175405 | The Eastern Service Area received over 2 inches of rain causing the influent of the plant to peek at over 40 MGD for over 4 hours. The influent channel capacity is not rated for that flow rate without opening the channel by-pass. Before staff can open the by-pass, the other effluent pipes are required to be opened or the problem will just move to the chlorine contact chamber which will over flow at even a faster rate than the ABW influent channel. The majority of the overflow filled up the adjacent construction area and unpaved ground / grass areas near the ABW Influent Channel.There is minimal to no risk to public health, safety and welfare. A recovery of 90,000 gallons was made and the remainder of the overflow (10,000 gallons) was absorbed into the ground. | 07/19/2017 05:06 PM | East Water Reclamation Facility | 1621 S. Alafaya Trail; Orlando FL; 32828 |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Owner Of the Facility | Troy E. Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 07/18/2017 07:10 PM | 07/18/2017 08:15 PM | Orange |  |  | 28.521159 | -81.202182 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=61
City of Pembroke Pines 16" FM break SW 145Ave and SW 5th St. | 20175177 | Communications utility bored 3-4¿ hole in 16" force main. All lift stations were immediately shut down that fed the force main. 9 isolation valves were closed to minimize discharge. Approximately 7,500 gallons discharged to stormwater system. Stormwater system retained the water behind a sediment baffle wall which is located before stormwater is discharged into a retention pond. Storm water system was pumped back to sanitary system for treatment. It is estimated that approximately 78,000 gallons of storm water and wastewater discharge mixture was returned to the sanitary sewer system. There was no physical evidence that the wastewater discharge flowed into the retention pond. As a precautionary measure, the retention pond was aerated and samples were taken for 4 consecutive days. | 07/19/2017 04:35 PM | City of Pembroke Pines | SW 145 Ave; SW 5th St.; Pembroke Pines FL; 33027 | Located between Pines Blvd. and Pembroke Rd. | Daniel Stark | Project Director | dan.stark@ch2m.com | (478) 361-5244 |  | Operator Of the Facility | Ron Abel | (321) 288-0037 |  | ron.abel@ch2m.com | 07/10/2017 05:45 PM | 07/10/2017 08:15 PM | Broward |  |  | 26.003668 | -80.333192 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=60
SSO | 21075424 | Spill on 207 South Delaware;2000-3000 gallons; 8 inch gravity mainline was blocked; section of collection system was isolated and blockage was cleared by use of vac con. Cleaned up all standing water. | 07/19/2017 02:24 PM | Loxahatchee River District | 2500 Jupiter Park Drive; Jupiter FL; 33458 |  | Adrian Sanchez | Field Foreman | adrian.sanchez@lrecd.org | (561) 747-5700 | 129 | collection system foreman | Albrey Arrington | (561) 747-5700 |  | albrey@lrecd.org | 07/18/2017 10:00 PM | 07/18/2017 11:15 PM | Palm Beach |  |  | 26.932128 | -80.117958 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=59
Fuel spill @ 1600 East Las Olas Blvd 07192017 Q#216165 | 20175411 | A tow truck's 25 gallon fuel tank dislodged from the brackets and was breached on contact with the street at 8:00am 7/19/2017. The contents of the tank spilled onto the street and into a storm drain. Police and the Fire Department spread adsorbent and cleaned the street. The storm drain was vacuumed with a vactor truck and there was no impact to the water body. This incident was also given the NRC# 1184499. | 07/19/2017 01:49 PM | SW storm drain @ the intersection of SE 16th Ave. & ELO blvd | 1600 East Las Olas Blvd; Fort Lauderdale FL; 33301 |  | Troy Balint | Environmental Program Coordinator | tbalint@fortlauderdale.gov | (954) 828-7845 |  | Reporting Authority | Troy Balint | (954) 828-7845 |  | tbalint@fortlauderdale.gov | 07/19/2017 08:00 AM | 07/19/2017 01:40 PM | Broward |  |  | 26.119311 | -80.127207 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=58
Hydraulic oil spill / Water Control Structure S-176 | 20175422 | NATIONAL RESPONSE CENTER 1-800-424-8802 *** For Public Use *** Information released to a third party shall comply with any applicable federal and/or state Freedom of Information and Privacy Laws Incident Report # 1184529 INCIDENT DESCRIPTION *Report taken at 11:17 on 19-JUL-17 Incident Type: FIXED Incident Cause: EQUIPMENT FAILURE Affected Area: C-111 CANAL Incident was discovered on 19-JUL-17 at 07:30 local incident time. Affected Medium: WATER C-111 CANAL _____________________________________________________________________ SUSPECTED RESPONSIBLE PARTY Organization: SOUTH FLORIDA WATER MGMT DISTRICT WEST PALM BEACH, FL 33406 Type of Organization: PRIVATE ENTERPRISE _____________________________________________________________________ INCIDENT LOCATION SEE LAT/LONG County: DADE C-111 CANAL State: FL Latitude: 25? 28' 58" N Longitude: 080? 33' 46" W WATER CONTROL STRUCTURE S-176 _____________________________________________________________________ RELEASED MATERIAL(S) CHRIS Code: OHY Official Material Name: HYDRAULIC OIL Also Known As: Environ AW-68 Oil Qty Released: 25 GALLON(S) Qty in Water: 25 GALLON(S) _____________________________________________________________________ DESCRIPTION OF INCIDENT CALLER IS REPORTING THAT A TEMPORARY PUMP LEAKED HYDRAULIC OIL AS A RESULT OF A HOSE FAILURE. THE PRODUCT WAS DISCHARGED INTO THE C-111 CANAL. Pump was secured and removed from water body upon discovery. Booms were deployed in C-111 Canal downstream of discharge point. Update on 7/21/17: After further investigation the release volume was likely between 55 to 70 gallons. This was based on filling the hydraulic oil reservoir during repair to the pump unit. Update on 7/21/17: The spill event reported within this notification was from a temporary surface water pump installed and operated under authorization obtain from the State of Florida Department of Environmental Protection Emergency Final Order (OCG N0. 17-0867) to aid in the reduction of high water conditions and flooding in the Everglades Protection Area, especially in Water Conservation Area 3A. | 07/19/2017 11:49 AM | South Florida Water Management District | 3301 Gun Club Road; West Palm Beach, FL 33406; Miami FL; 33030 | Western unincorporated Miami-Dade Co. Discharge in C-111 Canal. Near junction of SW 308th Street and SW 228th Ave. | Jeffrey Smith | Lead Environmental Scientist | jesmith@sfwmd.gov | (561) 682-2516 |  | Owner Of the Facility | Jeffrey Smith | (561) 682-2516 |  | jesmith@sfwmd.gov | 07/19/2017 03:00 AM | 07/19/2017 04:00 AM | Miami-Dade |  | N | 25.482753 | -80.562843 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=57
Broken air release - Vehicle crash @ Minton Rd & Henry Ave | 20175408 | 7/18/2017 - A one car crash hit and broke a Force Main air release at the intersection of Henry Ave & Minton Rd. Call out tech isolated break and cleaned up affected area. Estimated spill of 200 gallons of Raw sewage entered into the adjacent canal system. | 07/18/2017 09:43 PM | Ray Bullard Water Reclamation Facility | 1415 Henry Ave West Melbourne florida 32904; West Melbourne FL; 32904 | Incident occurred at the N.W intersection of Henry Ave & Minton Rd, West Melbourne Florida 32904. | Brian Mascher | Project Manager | Brian.Mascher@ch2m.com | (321) 984-0485 |  | Operator Of the Facility | Brian Mascher | (321) 288-0047 |  | Brian.Mascher@ch2m.com | 07/18/2017 07:30 PM | 07/18/2017 08:15 PM | Brevard |  |  | 28.072151 | -80.670933 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=56
PS3498 Orangewood East - West Taft Vineland Road | 20175400 | Pump Station 3498 Orangewood East experienced a backup panel / float ball failure which caused the station to run at a reduced capacity allowing the wet well to fill and overflow out of the wet well doors. A volume of 2000 gallons of untreated wastewater overflowed onto the surrounding concrete working surface and adjacent gravel areas inside of the Pump station property. Most of the overflowed volume was absorbed into the ground underneath the gravel areas. Field Services staff performed a complete wash down and cleaned all affected areas. A recovery of 1200 gallons was made by field staff. | 07/18/2017 06:55 PM | Orange County Utilities PS3498 Orangewood East | 3104 W. Taft Vineland Road; Orlando FL; 32837 |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Owner Of the Facility | Troy E. Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 07/17/2017 06:55 PM | 07/17/2017 08:25 PM | Orange |  |  | 28.416024 | -81.421841 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=55
Wayside Sewer Spill | 20175393 | Jackson County Utilities was notified of a bad odor near the vicinity of Wayside Park at the intersection of Hwy 90 and Merritt's Mill Road on the South side of Hwy 90. A 8" sewer force main has broke and was found by turning the lift station on to get a visual on the escaping sewer. This force main in in a swamp along with an 8" gravity sewer and a 12" water main. A backhoe cannot get to the location due to the instability of the soil. Two attempts were made an failed. The Road Department is transporting a track hoe to the incident site to try to get to the damaged pipe to excavate in order to repair the damaged pipe. | 07/18/2017 05:01 PM | Jackson County Utilities Jackson County Board of County Comm | 2864 Madison Street; Marianna FL; 32448 |  | Steve Croxton | Jackson County Utilities Manager | scroxton@jacksoncountyfl.com | (850) 482-9633 |  | Operator Of the Facility | Steve Croxton | (850) 482-9633 |  | scroxton@jacksoncountyfl.com | 07/18/2017 01:15 PM |  | Jackson |  |  | 30.754052 | -85.195065 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=54
Southbridge Street, Windermere, FL 34786 | 20175391 | Cause of Incident was a combination of electrical power and SCADA system failures at pump station 3961 "Stillwater Crossing." The failure caused the gravity collection system to surcharge and overflow untreated wastewater out of four Orange County Utilities manholes (Asset #'s - 39610030,39610031,39610062 and 39610063). The affected areas include pavement, "Miami curbing," storm drain systems on both Little Lake Sawyer Drive and South Bridge Street and possibly two storm water retention ponds on the aforementioned streets. Approximately 2,350 gallons of untreated wastewater overflowed from this event and Orange County Utilities recovered 45,000 gallons from the storm water systems at both locations. There is minimal risk to Public Health, Safety or Welfare at this time. OCU responders have recovered over five times the overflowed volume of wastewater at this time and washed down and cleaned all affected areas. | 07/18/2017 03:06 PM | Orange County Utilities Wastewater Collection System | FL |  | Eduardo C. Hernandez | Engineer II | Eduardo.Hernandez@ocfl.net | (407) 836-6839 |  | Owner Of the Facility | Troy E. Layton | (407) 254-9794 |  | Troy.Layton@ocfl.net | 07/16/2017 11:40 PM | 07/17/2017 01:35 AM | Orange |  |  | 28.47542 | -81.588699 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=53
Kings Cove Subdivision WWTP | 20175389 | Upon performing routine visit to the Kings Cove WWTP this morning, maintenance staff found solids discharging onto the ground around the aeration tanks. (found at approximately 9:15 am) Upon further investigation, it was found that the transfer line between the final two aeration bays was clogged, creating a discharge of solids over the top and along the seems of the aeration bays. It is estimated that between 3000- 5000 gallons was discharged. The discharge remained on property, no water ways were affected. The clogg was freed and the discharge stopped by 930 am; the contents of the wastewater tanks returned to normal operating level. The affected area of the spill has been limed and is in the process of being cleaned. | 07/18/2017 11:30 AM | Kings Cove WWTP | Royal Oaks Drive; Leesburg FL; 34748 |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 | 207 | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 07/18/2017 09:15 AM | 07/18/2017 09:30 AM | Lake |  |  | 28.862195 | -81.867611 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=52
city of holly hill | 20175383 | water system shut down to make repair on damaged water line | 07/18/2017 09:38 AM | holly hill water system | holly hill fl 32117 FL |  | james kenney | water plant operator | jkenney@hollyhillfl.org | (386) 248-9463 |  | Operator Of the Facility | walt smyser | (386) 248-9463 |  | wsymser@hollyhillfl.org | 07/17/2017 03:00 PM | 07/18/2017 12:15 AM | Volusia |  |  | 29.259337 | -81.073749 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=51
2017-5337 Diesel Fuel Releasae Baldwin, FL | 20175337 | On 7/17/17 at 0755 hours, CSX employee, reported an approximately 200 gallon diesel fuel release from an unknown locomotive. This is located in the CSX Baldwin Yard, 1347 US-301, Baldwin, Florida. The release is onto the ballast and soil along the tracks. There are no drains, ditches or waterways impacted. A response contractor was dispatched to clean up the release. Upon initial clean up activities, approximately 800 gallons of diesel fuel was released. | 07/18/2017 07:50 AM | CSX Baldwin Yard, Baldwin, FL | 1347 US HWY 301 South; Baldwin FL; 32234 |  | Brooke Martin | Manager Hazardous Materials | brooke_martin@csx.com | (800) 232-0144 |  | CSX Employee | Brooke Martin | (800) 232-0144 |  | brooke_martin@csx.com | 07/17/2017 07:55 AM |  | Duval |  |  | 30.283925 | -81.982367 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=50
release on 07/13/2017 | 0 | Repected sir notify you about the release happen on the 07/13/2017 what we find out that nozzel has been broken by on customer while filling up fuel because of that spill happen but in this situation it spill approx 3 to 5 gallon gasoline spill but quiet of good amount has been collected in bottom sump because we have pump which if it break from hose it will automatically stop release so it does went to ground and little quality which went on concerte it got evaporated and very little travel to side so there is no more then 3 to 5 gallon spillied thankyou jennis patel | 07/17/2017 06:28 PM | 8735283/gulf coast petro #129llc | 956 hwy 20 E; freeport FL; 32439 | gas station | jennis patel | operator | yugshakti.inc@gmail.com | (850) 625-6645 |  | Operator Of the Facility | jennis patel | (850) 625-6645 |  | yugshakti.inc@gmail.com | 07/13/2017 05:50 PM | 07/13/2017 05:50 PM | Walton |  |  | 30.490831 | -86.122593 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=49
10418 New Berlin Road JEA SSO | 20175363 | ~1000 gallons of wastewater to railroad easement from a broken 4" forcemain. No impacts to surface water or storm systems. Will complete repair and clean up tomorrow (7/18/17). Coordinating work with CSX due to proximity to rail line. Forcemain has been valved off. | 07/17/2017 04:20 PM | CSX railroad easement | 10418 New Berlin Road ; Jacksonville FL; 32226 |  | Eesa Ali | Environmental Specialist | alieg@jea.com | (904) 518-7943 |  | responder | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 07/17/2017 10:55 AM | 07/17/2017 12:10 PM | Duval |  |  | 30.421222 | -81.566863 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=48
Private Reclaimed Water Overflow - City of Orlando | 20175310 | A pipe joint on a private reclaimed water line disconnected and an overflow of reclaimed water impacted the surrounding area. A total of 90,000 gallons was released from the direct area. The valve to the reclaimed water line was isolated to control water loss to the area and the valve is to remain shut until the proper corrective actions have been taken by the owner of the private reclaimed water line. At this time the contractor has not made in changes to the line. | 07/17/2017 02:36 PM | Private Reclaimed Water Line | 722 TPC DRIVE; Orlando FL; 32822 | Turn Right on Semoran Blvd and proceed Southward until the Lee Vista Blvd Intersection. Turn left and then turn right on Tpc Drive. The address is on the left side of the road. | Scott Smith | Environmental Specialist I | scott.c.smith@cityoforlando.net | (407) 246-3063 |  | Employee of the City of Orlando Water Reclamation | Daniel Friedline | (407) 246-2657 |  | daniel.friedline@cityoforlando.net | 07/15/2017 02:00 PM | 07/15/2017 03:30 PM | Orange | Orange | Y | 28.463077 | -81.296219 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=47
Metal Container Corp - Lime Slurry Spill | 20175329 | At approximately 4 pm on July 16th, an Operator found that a lime sludge pump had failed and released lime sludge onto cement containment area. Due to heavy rainfall, the containment area was being drained through permitted stormwater outfall (FLR05A035). The lime sludge mixed with stormwater was discharged to the adjacent property to the south. It is estimated that the discharge duration was 30 minutes before the operator closed the outfall. The Facility immediately began recovering material and continues to do today. Notification was made to the State Warning Point via telephone, DEP & COJ via email, and CSX, adjacent property owner. by telephone. It is estimated that 150 gallons of sludge mixed with stormwater with an unknown amount being released through the outfall. In an abundance of caution this was reported to the State Warning Point. | 07/17/2017 01:09 PM | Metal Container Corp | 1100 Ellis Rd N; Jacksonville FL; 32254 |  | Vincent Seibold | EHS Manager | vincent.seibold@anheuser-busch.com | (904) 234-7865 |  | EHS Manager | Vincent Seibold | (904) 234-7865 |  | vincent.seibold@anheuser-busch.com | 07/16/2017 04:00 PM | 07/16/2017 04:30 PM | Duval |  |  | 30.338114 | -81.745118 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=46
Destin Water Users WWTP | 20175339 | At about 8:40am yesterday morning (7/16), DWU experienced severe weather and several lightning strikes at our WWTP. The lightning damaged several RTUs (SCADA components) that had to be repaired/replace. Until about 4:40pm, DWU experienced 3 overflows of Part IV Reclaimed Water (Restricted Access) that escaped onsite channels and a pump station. This treated Part IV effluent was contained on site in stormwater ponds and swales. There was about 85,500 gallons over the three events that spilled on the ground. No wastewater entered any water bodies. | 07/17/2017 09:04 AM | Destin Water Users Wastewater Treatment Plant | 14 Industrial Park Lane; Destin FL; 32541 | End of Industrial Park Lane | Monica Autrey | Operations Manager | mautrey@dwuinc.com | (850) 699-3665 |  | Operator Of the Facility | Monica Autrey | (850) 699-3665 |  | mautrey@dwuinc.com | 07/16/2017 08:40 AM | 07/16/2017 04:40 PM | Okaloosa |  |  | 30.394153 | -86.478619 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=45
12469 Corrine Ave |  | An electrical failure at the Corrine Main Lift Station occurred on 07/15/17 around 1:30 pm causing a sewage spill of about 500 gallons. Crews made needed repairs in about 2 hours. Effected area was cleaned and limed. | 07/17/2017 08:34 AM | Corrine Main Lift Station | 12469 Corrine Ave; Springhill FL; 34608 |  | Darrell Rose | Wastewater Collection Foreman | drose@hernandocounty.us | (352) 754-4812 |  | Owner Of the Facility | Darrell Rose | (352) 754-4812 |  | drose@hernandocounty.us | 07/15/2017 01:30 PM | 07/15/2017 04:30 PM | Hernando |  |  | 28.508012 | -82.518771 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=44
Sodium hypochlorite leak | 20175318 | We discovered a small sodium hypochlorite leak from our secondary containment tank on July15 at 4:00 pm. We immediately brought in fill dirt to contain the 50 gallons that is seeping from the tank. The fill dirt is on a concrete slab adjacent to the leaking tank. We are not expecting the sodium hypochlorite to leave this area. Odyssey Manufacturing company (813-635-0339) is scheduled to arrive July 19 by 6:00 am to evacuate the sodium hypochlorite which will allow us to take the tank out of service and inspect so we can repair or replace. | 07/16/2017 10:39 AM | St. Lucie West Services District WWTF (FLA013993) | 450 SW Utility Drive; Port St. Lucie FL; 34986 |  | Thomas Stirtzinger | Chief Wastewater Operator | tstirtzinger@slwsd.org | (772) 618-3531 |  | Operator Of the Facility | Thomas Stirtzinger | (772) 618-3531 |  | tstirtzinger@slwsd.org | 07/15/2017 04:00 PM | 07/17/2017 11:30 AM | St. Lucie |  | N | 27.312267 | -80.387073 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=43
Sewage Spill near Keller Canal | 20175244 | We had a sewer main line break on along Keller Canal south of 10th avenue North. The leak has been contained. A contractor was being notified to make the necessary repairs. Fecal samples were being collected on the contaminated water body/ retention pond of Avesta Casa Del Sol apartments. | 07/14/2017 02:26 PM | Village Of Palm Springs | 226 Cypress Lane; Palm Springs FL; 33461 |  | Don Ray | Superintendent | dray@vpsfl.org | (561) 601-1449 |  | Superintendent/Utilities | Don Ray | (561) 601-1449 |  | dray@vpsfl.org | 07/13/2017 02:00 PM | 07/13/2017 03:00 PM | Palm Beach |  |  | 26.626831 | -80.080036 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=42
George K. Wise | 20175222 | Plant under construction for increased capacity. Heavy rain caused large and fast inflow to plant with one of the chlorine contact chambers out of service for construction. This overwhelmed the single(1/2) tank with chlorinated effluent breeching the sidewalls. Approximately 50,000 of chlorinated effluent hit the ground. All of the spill was contained within the facility percolated into the ground. | 07/14/2017 01:08 PM | Southwest Water Reclamation Facility | 3800 54th Ave S; St. Petersburg FL; 33711 |  | Frank Niles | Water Reclamation Operations Specialist | frank.niles@stpete.org | (727) 892-5640 |  | Submitting Report of Pollution Notice | George K. Wise | (727) 892-5121 |  | george.wise@stpete.org | 07/12/2017 08:50 PM | 07/12/2017 09:10 PM | Pinellas |  |  | 27.716768 | -82.683031 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=41
20175232 - 07/13/17 | 20175232 | At 10:05 AM on 7/13/17, a facility representative found a trimethylamine (TMA) release from a leaking block valve on the #4 TMA column. Representatives halted the leak and notified the required authorities that an unknown quantity was released into the atmosphere. | 07/13/2017 05:14 PM | Taminco US LLC | 4575 Hwy 90 East; Pace FL; 32571 |  | Amy Adams | Health Safety Environmental Security Manager | amyadams@eastman.com | (850) 995-5559 |  | Health Safety Environmental Security Manager | Amy Adams | (950) 995-5559 |  | amyadams@eastman.com | 07/12/2017 12:00 AM | 07/13/2017 10:05 AM | Santa Rosa |  |  | 30.589395 | -87.132893 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=40
CS071317 | 20175239 | Sanitary sewer overflow (SSO) CS071317 occurred when a force main located near 2150 Bay Drive in Bradenton broke and discharged untreated wastewater to the surrounding area. This force main break was attributed to a failure in an older section of the wastewater force main and may have been exacerbated by temporary pressure fluctuations in the line. A final estimated volume for this SSO event is 181,000 gallons. Manatee County staff were able to stop the SSO discharge around 1400 by installing a sleeve around the broken force main. Tanker trucks were employed throughout the event to limit the amount of wastewater that was discharged as well as recover as much of the discharged wastewater as possible (approximately 100,000 gallons of wastewater and surrounding water was recovered from an affected canal during cleanup efforts). The area affected by the SSO was cleaned up and necessary areas were disinfected. Sarasota Bay has been impacted by this event and Compliance staff were on site on both 7/13/17 and 7/14/17 to collect samples in the bay to be analyzed for fecal coliform and enterococcus in an effort to determine the extent of the impact. | 07/13/2017 03:50 PM | FLA012619 | FL |  | Karen Briden | Wastewater Compliance Supervisor | karen.briden@mymanatee.org | (941) 792-8811 | 5180 | Owner Representative | Ed Ference | (941) 792-8811 | 5015 | ed.ference@mymanatee.org | 07/13/2017 10:00 AM | 07/13/2017 02:00 PM | Manatee | Manatee | Y | 27.418437 | -82.583223 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=39
6457 Ft Caroline Road | 20175240 | ARV failed and released sewer onto ground and stormwater drain. | 07/13/2017 03:17 PM | 6457 Fort Caroline Road | 6457 Fort Caroline Road; Jacksonville FL; 32277 |  | Jason Hermening for Eesa Ali | Environmental Scientist Senior | hermjs@jea.com | (904) 376-5164 |  | Employee of Owner | Eesa Ali | (904) 518-7943 |  | alieg@jea.com | 07/13/2017 09:50 AM |  | Duval |  |  | 30.369538 | -81.591682 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=38
Cadd Balogh | 1183919 | Florida Division of Emergency Management State Watch Office Incident Report Maps Attachments Attachment: NRC#1183919 Main Information Report #: 2017-5224 Status: Closed Assigned To: DEP / Nick Roff Reported to SWO on: 7/13/2017 08:39 ET Severity: Local Incident Description: Petroleum Release This situation involves: Petroleum Spill Affected Sectors: DEP District - South, DEP OER Ft. Myers - Day Initial Report: PER NRC #1183919 VERBATIM: "CALLER STATED WHILE MOVING A DIESEL STORAGE CONTAINER, THE CONTAINER FELL OFF OF A FORKLIFT AND RELEASED 50 GALLONS OF DIESEL FUEL ONTO THE GROUND." Injuries: No Fatalities (Unconfirmed by State Medical Examiner): No Environmental impact: No Incident Occurred: 7/13/2017 08:10 ET Most Recent Update Date/Time: 07/13/2017-10:03 ET Most Recent Update: N/A Affected Counties: Lee Facility Name or Description: Incident Location: Address: 16001 Airport Haul Rd City: Ft. Myers Coordinates: Lat: 26.64084, Long: -81.86807 Contact Information Reporting Party: Not Available Responsible Party: Unknown On-Scene Contact: Unknown Petroleum Spill Sub-Type: On Land Situation: Active, release contained Description: Petroleum Spill Petroleum Type: Fuel Name or Description: Diesel Source / Container: Aboveground Tank Quantity released: 50 gallons Released: Outside environment Cause of release: Container fell off forklift Storm drains affected: No Waterways affected: No Major roadways closed: No Cleanup actions been taken: Yes Notification 07/13/2017-08:50 / DEM-Harvey | 07/13/2017 12:24 PM | Green Meadows WTP PWS 5364048-5 | 16001 Alico Road; Fort Myers FL; 33913 | I-75 South to Alico Road Alico Road East to Airport Haul Road (turn left) Airport Haul Road to stop sign and turn right Road will dead end into facility | Cadd Balogh | Water Manager | cbalogh@leegov.com | (239) 281-7632 |  | Owner Of the Facility | Josh Petro | (407) 877-5903 |  | jpetro@garney.com | 07/13/2017 08:10 AM | 07/13/2017 08:20 AM | Lee |  |  | 26.511985 | -81.724917 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=37
TWA South Bermuda WRF Service Area Spill LS#15 | 20175217 | On 7/12/17 starting at 3:30 p.m. and ending at approximately 4:00 p.m., a raw wastewater spill occurred from several manholes near Birchwood Circle, in the Buenaventura Lakes community in Kissimmee, FL. The lift station (LS#15) by-pass pumps failed during repairs, leading to the estimated 120,000 gallon spill, of which 10,000 gallons went to a nearby drainage ditch and stormwater pond. The backup float system was corrected; the affected area was washed down with potable water. The ditch and pond are being sampled for fecal coliform bacteria, a letter with the results will follow. The State Watch Office was notified and gave incident report #2017-5217. | 07/13/2017 08:28 AM | TWA South Bermuda WRF | FL |  | Phil Roberts | Mechanic | PROBERTS@tohowater.com | (407) 944-1414 |  | System Mechanic, Lift Stations | Richard Haynes | (407) 944-5037 |  | rhaynes@tohowater.com | 07/12/2017 03:30 PM | 07/12/2017 04:00 PM | Osceola |  |  | 28.326704 | -81.372793 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=36
Valrico AWWTF, 1167 N. Dover Road, Dover FL, 33527 | 20175214 | ¿ On 7/11/17 at 4:45pm the Valrico AWWTF lost power to the plant and the generators came on due to a severe thunderstorm which resulted in the NTU pump to stop working. ¿ From 4:45pm on 7/11 to 7:30am on 7/12 the NTU sample pump was not working. The on duty operators did not notice this pump stopped working because SCADA was showing normal readings. One reading was taken at 11:40pm and the NTU was 0.32. The operators started 15 minute NTU readings at 7:30am on 7/12 and the NTU readings were between 0.23-0.37. Before the pump stopped working the NTU readings were between 0.25-0.27. The SCADA trending for UVT (transmittance/effluent clarity) for the UV system was between 69.8%-72.5%. Also, our effluent TSS for this day was <0.5 mg/L. ¿ The amount of water that was not being recorded for NTU was 3,933,333 gallons which went to the reclaim tanks. ¿ Regulatory Agency notification was made to DEP via voice mail at 2:42pm, EPC at 2:44pm, and State Warning Point at 3:40pm, case #2017-5214. | 07/12/2017 04:39 PM | Valrico AWWTF, 1167 N. Dover Road, Dover FL, 33527 FL0040983 | 1167 N. Dover Road, Dover FL, 33527 FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | JON JOHANSON | (813) 209-3088 |  | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | 07/11/2017 04:45 PM | 07/12/2017 02:45 PM | Hillsborough |  |  | 27.957057 | -82.229551 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=35
7039 Alachua Ave | 20175190 | JEA contractor broke sewer force main causing sewer to be released to ground, No water ways or storm drains impacted, | 07/12/2017 03:16 PM | JEA Lift Station | ; JAcksonville FL; 32210 |  | Glenn Davis | Incident Response | Davige@jea.com | (904) 591-4777 |  | Incident response | Glenn Davis | (904) 591-4777 |  | davige@jea.com | 07/11/2017 09:05 AM | 07/11/2017 11:55 AM | Duval |  |  | 30.293677 | -81.763484 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=34
Lift Station # 20 - City of Largo WWRF | 20175204 | There was a lightening strike on 7/11/17 affecting Lift Station # 20, located at 13455 Wilcox Rd., Largo, FL (Pinellas County). The strike caused a breaker to trip and the pumps to shut off. As a result 4 manholes overflowed allowing approximately 30,000 gallons of untreated sewage to overflow into the storm drains and ditches leading to Church Creek (McKay Creek Drainage Basin). City staff arrived at 1:40pm, reset the electrical panels and restarted the pumps, stopping the overflow at 2:05pm. The area was washed down, signs were posted and samples were collected; lime will be applied 7/12/17. | 07/12/2017 01:14 PM | Lift Station #20 - City of Largo WWRF | 13455 Wilcox Rd.; Largo FL; 33774 |  | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 07/11/2017 01:40 PM | 07/11/2017 02:05 PM | Pinellas | Pinellas | Y | 27.891418 | -82.825497 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=33
Bill Johnston | 20175203 | Name, address, and phone number of person reporting the spill. Bill Johnston, 801 Bates Ave. Eustis, FL. 32726. Wastewater Superintendent. 352-357-3777 X1900. Date and time of the discharge and status of discharge (ongoing or ceased). Discovered 12:00 pm 7/11/17 and repairs were completed approx. 3:00 pm 7/11/17. Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater). Domestic wastewater untreated. Estimated amount of the discharge. Between 4,000 and 8,000 gallons. Location or address of the discharge. Remote area along CR44 approximately 400yds East of intersection with Hicks Ditch Rd. in Eustis Florida 32726 Source and cause of the discharge. Source was an 8¿ PVC sewer main blowout. Believed to be caused by a lightning strike as supported by burns on a nearby oak, and scorch patterns in the grass. Whether the discharge was contained on-site and any cleanup actions taken to date. Contained on site (City property & right of way), spill area bounds of 25¿ x 30¿. Action includes distribution of lime and liquid sodium hypochlorite. Description of area affected by the discharge, including name of water body affected if any. Discharge happened in a remote rural area within 50¿ of CR44. Discharge remained on site and did approach any bodies of water. Other persons or agencies contacted. Florida Warn ID# 2017-5203 Additional information. Treatment Facility Permit # FLA-010507. | 07/12/2017 10:31 AM | Eustis WWTP | FL |  | Bill Johnston | Superintendent | johnstonb@ci.eustis.fl.us | (352) 357-3777 | 1900 | Operator Of the Facility | Bill Johnston | (352) 357-3777 |  | johnstonb@ci.eustis.fl.us | 07/11/2017 12:20 PM | 07/11/2017 03:00 PM | Lake |  |  | 28.875223 | -81.676294 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=31
Wastewater Main Broken | 20175163 | On Monday, July 10, 2017, at 12:00 PM, Palm Beach County Water Utilities Department (PBCWUD) Communications was informed of a forcemain break at Mizner Pointe of Boca. A sewage spill resulted from a hairline crack in the existing 8-inch pipe. From the time that PBCWUD was notified at 12:00 PM, until 7:00 PM when 18 Lift Stations were shut off to make the repair, the discharge amount for the sewage spill going into the canal was calculated to be 19,000 gallons. PBCWUD mobilized by 4:30 PM to repair the broken forcemain. The defective pipe was replaced and the repair was completed by 9:00 PM. Report #: 2017-5163 | 07/11/2017 04:59 PM | MIZNER POINTE OF BOCA 1 (W/D)(M) | 8230 210TH ST S; BOCA RATON FL; 33433 |  | Nicole Gumbs | Professional Engineer | ngumbs@pbcwater.com | (561) 493-6103 |  | PBCWUD Employee - Environmental Health and Safety | Juan Guevarez | (561) 493-6039 |  | JGuevarez@pbcwater.com | 07/10/2017 12:00 PM | 07/10/2017 09:00 PM | Palm Beach |  | N | 26.364001 | -80.17419 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=30
Wastewater Overflow at 8301 North Dale Mabry Hwy., Tampa, FL | 20175157 | On July 10, 2017 - The City of Tampa Wastewater Department became aware of wastewater overflow at 8301 North Dale Mabry due to a broken check valve on a privately maintained wastewater pumping station. The broken check valve allowed wastewater to discharge from the pumping station due to the back pressure in the City's force main along Dale Mabry Hwy. Department crews responded to the location and used vactor trucks to recover the wastewater until the pumping station could be isolated from the City's force main. The owner of the privately maintained pumping station is the process of replacing the broken check valve. The connection to the City's force main will remain isolated until the repairs have been completed. The volume of the overflow is estimated at 2,160 gallons and it is estimated that 1,000 gallons were recovered. The overflow discharged into the parking lot adjacent to the pumping station and into the pond located east of the property. | 07/11/2017 04:35 PM | Private lift station at 8301 North Dale Mabry Hwy | 8301 North Dale Mabry Hwy; Tampa FL; 33614 |  | Charlie Lynch | Chief Engineer City of Tampa Wastewater Department | charlie.lynch@tampagov.net | (813) 274-8916 |  | Chief Engineer City of Tampa Wastwater Department | Eric Weiss | (813) 274-8070 |  | eric.weiss@tampagov.net | 07/10/2017 11:30 AM | 07/10/2017 04:00 PM | Hillsborough |  |  | 28.024196 | -82.503983 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=29
10901 Dale Stitik Dr Tampa Fla 33626 | 1183751 | ¿ On 07/11/2017 at 1:30pm a lawn mower struck a 1 ¿ sample line connected to Digester #3, this caused a discharge of 1200 gallons on sludge to spill onto the grounds, a barrier of a 14 radius berm was installed around the area of discharge until the leak was contained and sealed. The spill was contained on site and stopped at 2:00pm. ¿ Enviro-Waste services group was notified to clean and vacuumed up spilt areas. ¿ Regulatory Agency notification was made at to the DEP ¿ Erica Peck 2:14pm, EPC- Daniel Moore 2:20pm and State Warning point at 2:30pm case # 1183751 | 07/11/2017 04:07 PM | NORTHWEST REGINAL WRF FL0041670 | 10901 Dale Stitik Dr Tampa Fla 33626 FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | PROJECT MANAGER II | JON JOHANSON | (813) 209-3088 |  | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | 07/11/2017 01:30 PM | 07/11/2017 02:00 PM | Hillsborough |  |  | 28.072939 | -82.609998 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=28
Phoenix Estates WWTF - Deland |  | Wastewater Treatment Plant located at Phoenix Estates MHP at 269 Lingering Lane, Deland, FL 32724... activated sludge lost from final effluent tank due to plant malfunction. Malfunction caused by others (repairmen) leaving control valves in incorrect position. Lost Sludge lost was chlorinated so is likely to be inert. Lost Sludge was also contained in a small holding pond - amount lost was approximately 1000 wet gallons since it is mixed with effluent water (or approximately 50 dry gallons once it is dried and removed to the digester). Once pond is dry, the sludge will be manually removed from the pond and delivered to the onsite digester at the WWTF for removal by sludge hauling truck. Any questions, please call Lee Cain at ESI (407) 928-1555 (Cell). Local county Health Department was contacted. | 07/11/2017 12:14 PM | Phoenix Estates WWTF - Deland | 269 Lingering Lane; Deland FL; 32724 |  | Lee Cain | Operator | lee.cain@esi-usa.net | (407) 928-1555 |  | Manager of the operator of the facility | Lee Cain | (407) 928-1555 |  | lee.cain@esi-usa.net | 07/11/2017 10:45 AM | 07/11/2017 10:45 AM | Volusia |  |  | 29.091668 | -81.326074 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=27
Oak Hill Manor Dr, Orlando FL 32839 | 20174934 | A lightening strike caused a power failure at Orange County pump station #3444, disabling the pumping system and the SCADA alarm system. The power failure allowed the gravity system to surcharge, resulting in wastewater discharges from the pump station wet well, associated Orange County Utilities manholes and six private manholes in the Canongate Apartment complex. Estimated volume discharged: 3,000 gallons. Volume recovered: 45,000 gallons. No wastewater discharged to surface water. Affected areas include pavement, Miami curbing and storm drain systems on Ravencreek Drive, Oak Hill Manor, and Long Iron Drive. Potential Risk to the Public Health, Safety or Welfare: There is minimal risk to Public Health, Safety or Welfare at this time. OCU responders recovered over five times the overflowed volume of wastewater and washed down and cleaned all affected areas. | 07/11/2017 11:34 AM | Orange County Utilities wastewater collection system | FL |  | Laura Woodbury | Senior Engineer, Field Services | Laura.Woodbury@ocfl.net | (407) 836-6826 |  | Engineer for Orange County Utilities | Troy Layton, Manager, Field Services | (407) 254-9977 |  | troy.layton@ocfl.net | 07/01/2017 12:00 PM | 07/01/2017 01:15 PM | Orange |  | N | 28.513081 | -81.30066 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=26
502 2nd Avenue NE Ruskin | 20174976 | At about 11:30AM on Monday, 07/03/2017, a citizen called Base 1 and reported that sewer had been flowing in her front yard at 502 2nd Avenue NE in Ruskin, . She also stated that she thought her neighbor had called the situation in. Upon receipt of the call, the LPSS Team was dispatched to investigate. Upon arrival they found two storm ditches full of sewer and a leak coming from the ground in front of the address above. The LPSS team was able to isolate the LPSS Force Main and stop the SSO at about 12:00PM. The LPSS Team began removing the sewer from the storm ditches using the LPSS pump truck. After collecting the accumulated sewer they reported a 2000 gallon SSO with 1,800 gallons recovered and put back into the system. After recovering the SSO the LPSS team excavated the site of the leak and found a broken PVC saddle tap on the 4 inch force main. The broken saddle tap was replaced and the force main put back in service. After the excavation site was filled in the area was spread with lime. | 07/11/2017 08:43 AM | SOUTH COUNTY WWTF FL0028061 | 520 TECO RD RUSKIN FL; RUSKIN FL |  | JON JOHANSON | PROJECT MANAGER II | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | (813) 209-3088 |  | HILLSBOROUGH COUNTY PROJECT MANAGER II | JON JOHANSON | (813) 209-3088 |  | JOHANSONJ@HILLSBOROUGHCOUNTY.ORG | 07/03/2017 11:30 AM | 07/03/2017 12:00 PM | Hillsborough |  |  | 27.71975 | -82.427661 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=25
5620 Collins Road | 20175169 | Force main failed and released an estimated 30,000 gallons of sewer onto the ground. Release has seized and line repairs underway. All released sewer will be recovered and hydrated lime will be place onto impacted area. No evidence of surface water impacts at this time but sampling will occur on 7/11 to verify. | 07/11/2017 12:46 AM | Courtney Manor Apartment Complex | 5620 Collins Road; Jacksonville FL; 32244 | Back of apartment complex near I-295/Blanding Blvd ramp near billboard. | Jason Hermening | Environmental Scientist Senior | hermjs@jea.com | (904) 376-5164 |  | Environmental Coordinator for Owner of line. | Jason Hermening | (904) 376-5164 |  | hermjs@jea.com | 07/11/2017 12:42 AM |  | Duval |  |  | 30.193689 | -81.730298 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=24
Solid Waste Site Storm Water Pond 2 Overflow | 20175152 | Storm water from the facility¿s solid waste site storm water pond #2 overflowed into an adjacent wetlands area following rainfall of approximately two inches. The pumping system was found to be running, but not pumping water out. Operators were contacted immediately and got the pump working again, pumping the pond level down and stopping the overflow. Estimated storm water overflow was 31,000 gallons. Due to the nature of the storm water, there are no public health or environment impact concerns. A sample was collected and will be analyzed for Chemical Oxygen Demand. Upon receipt, results will be sent to FDEP, NE District. | 07/10/2017 05:00 PM | Georgia-Pacific Consumer Operations LLC | 215 County Road 216; Palatka FL; 32177 |  | James Eckenrode | Environmental Manager | jpeckenr@gapac.com | (770) 843-3302 |  | Owner Of the Facility | James Eckenrode | (770) 843-3302 |  | jpeckenr@gapac.com | 07/09/2017 06:15 PM | 07/10/2017 11:25 AM | Putnam |  |  | 29.676343 | -81.691571 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=23
2017-5136 RCRX 2704 7-9-17 Tampa, FL | 20175136 | On 07/09/17 at 2000 hours, CSX, Terminal Manager, reported a slosh leak from the top of loaded Hydrochloric acid tank car RCRX 2704 at MP S 841.00 on the Tampa Terminal Subdivision. This is located inside Yeomen Yard, track Y23, in Tampa, Florida. The release was estimated to be approximately less than a gallon. Response contractor was dispatched and found two nut and bolt assemblies on the loading / unloading liquid closure flange that had corroded and were broken. The leak from the liquid line was secured by replacing the two nut and bolt assemblies. Approximately one gallon of Hydrochloric acid spilled onto the ground and was cleaned up and appropriately secured for disposal. | 07/10/2017 04:43 PM | CSX Transportation, Yeoman Yard, Track Y23 | 5656 Adamo Drive; Tampa FL; 33619 |  | Brooke Martin | Manager Hazardous Materials | brooke_martin@csx.com | (800) 232-0144 |  | CSX Employee | Brooke Martin | (800) 232-0144 |  | brooke_martin@csx.com | 07/09/2017 08:00 PM | 07/10/2017 12:45 AM | Hillsborough |  |  | 27.954506 | -82.384636 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=22
Sewer overflow from manhole | 20175147 | Wastewater Incident Notification 1. SWO Incident Number: 2017-5147 2. Date/Time Reported: 7/10/2017 @ 9:05am 3. Description: Sewer overflow from manhole 4. Incident Date/Time: 7/9/2017 @ 11:45am 5. Incident Location: 540 E. 6th Street 6. County: Bay (03) 7. District: Northwest District 8. Caller Name: Ed Turner 9. Affiliation: Lift Stations Superintendent 10. Permitted Utility?: Yes 11. Permitted Utility Name: Millville WWTP 12. Permitted Utility ID: 0170909 13. Non Permitted Satellite Collection Systems: 14. Facility Type: Domestic Wastewater 15. Wastewater Characteristics: Untreated 16. Cause: LS #41 Electrical failure 17. Initial Spill Volume: 10,000 gallons 18. Volume Recovered: 0 19. Final Spill Volume: 10,000 gallons 20. Water Body Affected: Massalina Bayou 21. Clean-up Actions: Washed down street and added lime 22. Clean-up Actions Status: Completed 23. Notes: Relay for alarm burnt. Shorted tripped control breaker 24. Location Physical Address and/or Latitude/Longitude: 540 E. 6th Street | 07/10/2017 12:52 PM | Lift Station #41 | 540 E. 6th Street; Panama City FL; 32401 | Location of Lift Station is on Business Highway 98/6th Street just west of Massalina Dr. | Ed Turner | Lift Station Superintendent | ed.turner@pcgov.org | (850) 872-3037 |  | Lift Station Superintendent | Ed Turner | (850) 872-3037 |  | ed.turner@pcgov.org | 07/09/2017 11:45 AM | 07/09/2017 12:30 PM | Bay |  |  | 30.158551 | -85.653688 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=21
TWA Camelot WRF Effluent Spill | 20175125 | On 07.09.17 early a.m., Pine Island holding ponds water level rose up flowed backwards into Camelot's storm water drains. The water over flowed by Camelot's office and into the street; then flowing out the gate that leads into Sherwood Forrest community. The water flowed down a sloped grade and then into Bonnet Creek approximately 500 feet from Camelot. The water was treated with lime. Operators put sand bags to divert flow into Northeast corner where the water is pumped back into the Ponds. Made manual adjustments to the plant and diverting effluent into the GST then sending the water to the Imperial RIB site. Reclaim water valve closed manually and opened RIB valve 100%. Called in a spill report to the State Warning Point, incident #2017-5125 | 07/09/2017 06:08 PM | TWA Camelot WRF | FL |  | Rick Vester | Chief Wastewater Operator | rvester@tohowater.com | (407) 944-5000 |  | Operator Of the Facility | Adrian Brene | (407) 944-5016 |  | environmental@tohowater.com | 07/09/2017 04:00 AM | 07/09/2017 07:00 AM | Osceola |  |  | 28.319403 | -81.498513 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=20
Beneva Road and BahiaVista Street 070717 | 20175094 | The ARV at Bahia Vista Street and Beneva Road had deteriorated and blown apart. this caused a discharge of waste water to the surrounding areas and Phillippi Creek. Samples were taken from the receiving waters and the results will be submitted. | 07/09/2017 06:08 PM | Beneva Road and Bahia Vista Street | ; Sarasota FL |  | Patricia Nihart | ES III | pnihart@scgov.net | (941) 650-8288 |  | Environmental Specialist for Utility | Patricia Nihart | (941) 650-8288 |  | pnihart@scgov.net | 07/07/2017 05:20 PM | 07/07/2017 06:00 PM | Sarasota |  |  | 27.184846 | -82.403907 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=19
TWA Lake Marion EQ Tank Spill | 20175102 | On 7/8/17 the EQ tank spilled due to PLC fault. Operator called the state warning point at 10:30 a.m. to report a spill of approximately 400,000 gal. of raw wastewater. The spill was contained on TOHO property and no waterways were affected. The affected area was cleaned and lime was applied. Incident number is 2017-5102. When the operator arrived on site at 0600, Andrew, was on site working on the PLC. | 07/09/2017 06:00 PM | TWA Lake Marion WRF | FL |  | Ricardo Rodriguez | Wastewater Operator | rrodriguez@tohowater.com | (407) 944-5000 |  | Operator Of the Facility | Adrian Brene | (407) 944-5016 |  | environmental@tohowater.com | 07/08/2017 10:30 AM | 07/09/2017 06:00 AM | Polk |  |  | 28.063584 | -81.492797 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=18
DWU WWTP | 20175103 | Approximately 5,000 gallons of treated effluent from the WWTP overflowed onsite channels due to a power outage. All treated effluent was contained on the treatment plant. No effluent entered any water bodies or storm drains. The flow was stopped, power was restored and the area was limed. | 07/08/2017 11:04 AM | Destin Water Users Wastewater Treatment Plant | 14 Industrial Park Lane; Destin FL; 32541 |  | Monica Autrey | Operations Manager | mautrey@dwuinc.com | (850) 699-3665 |  | Operator Of the Facility | Monica Autrey | (850) 699-3665 |  | mautrey@dwuinc.com | 07/08/2017 08:30 AM | 07/08/2017 09:00 AM | Okaloosa |  |  | 30.394121 | -86.478668 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=17
Small Digester sludge spill |  | The Anaerobic Digester tank # 3 leaked rainwater mixed with a small amount of sludge from the scum seal, where the metal lid and cement tank are joined. The fluid ran down the outside wall of the tank and onto the ground. Only 5 gallons were spilled. The fluid was recovered with a shop-vac and returned to the plant influent stream. This tank is presently off-line but is full of undigested sludge. The cause of the spill was from Rainwater runoff from the metal lid running into cracks in the scum seal, filling the tank above the high level mark. The Digester fluid level was immediately lowered by pumping into an adjacent tank. | 07/07/2017 02:03 PM | Water Conserv II WRF | 5420 L.B. McLeod Rd.; Orlando FL; 32811 | Digester Tank # 3 is located at the West side of the facility. The spill occurred at the NW side of the tank. | Keith T Jordan | Chief Operator | keith.jordan@cityoforlando.net | (407) 435-5214 |  | Operator Of the Facility | Athena Tipaldos, Water Reclamation Compliance | (407) 246-4086 |  | athena.tipaldos@cityoforlando.net | 07/06/2017 09:00 AM | 07/06/2017 09:10 AM | Orange |  |  | 28.54667 | -81.41272 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=16
L/S #NE4 Overflow |  | Lift Station malfunctioned causing wet well to overflow raw sewage. Approximately 100 gallons was discharged on the ground surrounding the lift station. All of the overflow was contained and captured with Vac truck. Overflow did not make it to any waterways or waters of the state. | 07/07/2017 09:42 AM | City of Pinellas Park L/S# NE 4 | 3700 126th Ave; Clearwater FL; 33762 |  | Ryan Gonzalez | Utilities Foreman | Rgonzalez@pinellas-park.com | (727) 214-7831 |  | Operator Of the Facility | Ryan Gonzalez | (727) 214-7831 |  | Rgonzalez@pinellas-park.com | 07/06/2017 10:00 AM | 07/06/2017 11:00 AM | Pinellas |  |  | 27.886434 | -82.68388 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=15
Howard F. Curran AWTP Chlorine Exceedance |  | Start date and time & End date and time cannot be entered - will only except current Start 7/5/17 22:19 - Stop 7/5/17 22:23 On July 5th the filter building operator tried to pull a vacuum on Cl2 evaporator #3 using chlorinator #3, not realizing that both chlorinators 2 & 3 were valved into that evaporator. Because of this the Cl2 feed dropped out causing the Pre-SO2 residual to drop below 1.0 mg/L for 5 minutes from 22:19 to 22:23. A grab sample was taken at the lowest residual with a result of 0.94 mg/L. The flow was immediately slowed by shutting off all but one nitrification pump and diverting flow into the empty contact chamber. Although most of the flow was diverted it is estimated that 62,000 gallons of <1.0 mg/L residual water went over the weir before the residual was reestablished. | 07/06/2017 02:58 PM | Howard F. Curran AWTP | 2700 Maritime Blvd; Tampa FL; 33605 |  | Jeff Hilton | Wastewater Palnning | jeffrey.hilton@tampagov.net | (813) 274-7844 |  | Wastewater Planning | Jeff Hilton | (813) 274-7844 |  | jeffrey.hilton@tampagov.net | 07/06/2017 02:55 PM | 07/06/2017 02:55 PM | Hillsborough |  |  | 27.924427 | -82.439343 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=14
1345 Court Street |  | N/A | 07/06/2017 02:52 PM | Reclaimed water sytem / owner side | N/A; Clearwater FL |  | Michael Vacca | Public Utiltites supervisor | mike.vacca@myclearwater.com | (727) 562-4960 | 7213 | reclaimed water on citizen side / private irrigati | michael Vacca | (727) 562-4960 |  | mike.vacca@myclearwater.com | 07/05/2017 03:40 PM | 07/05/2017 04:00 PM | Pinellas |  |  | 27.96922 | -82.782518 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=13
Mosaic Big Bend Dustrol (Coating Oil) Spill | 20174996 | Approxiamtely 75 gallons of Dustrol (coating oil) was released into an on-site retention pond from a storage tote inadvertently left open. All product (Dustrol Coating Oil) is contained on-site. Remediation is underway. | 07/06/2017 07:30 AM | Mosaic Fertilizer/Big Bend Terminal | 12839 Wyandotte Road; Gibsonton FL; 33534 |  | Wesley Williams | Senior EHS Specialist | wesley.williams@mosaicco.com | (813) 417-1494 |  | Environmental Contact for the site | Bill Wilhelm | (813) 675-0925 |  | william.wilhelm@mosaicco.com | 07/05/2017 08:15 AM | 07/05/2017 08:16 AM | Hillsborough |  | N | 27.805961 | -82.384436 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=12
Climatic Lab Incident at Eglin AFB | 20175004 | A fire occurred in an air handling unit causing damage to the facility and its cooling system. As a result of the damage to the cooling system, methylene chloride used as a refrigerant, was released. It is estimated that 10,000 gals of methylene chloride was released during the fire and its subsequent response. | 07/06/2017 11:03 AM | Eglin AFB | Bldg 440; Eglin AFB FL; 32542 |  | Brian Kelly | Pollution Prevention Manager | brian.kelly.6@us.af.mil | (850) 699-9153 |  | Emergency Response personnel | Brian Kelly | (850) 699-9153 |  | brian.kelly.6@us.af.mil | 07/05/2017 10:45 AM | 07/05/2017 05:50 PM | Okaloosa |  |  | 30.477186 | -86.507438 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=11
Eastfield Slopes Condominium | 20175007 | Upon performing operational visit at 8 am this morning, the operator found the RAS line on the clarifier clogged and solids discharging in the air and falling ontop of the facility tanks and adjacent grounds. Operator was able to shut off RAS line and discontinue the discharge upon arrival (by 810 am). The RAS line was unclogged and the return re-established. It is estimated that 1500 gallons discharged ontop of the tanks and subsequently to the facility grounds adjacent to the tanks. No water ways were affected, all contents of the spill remained onsite. The operator was able to clean the top of the facility tanks and lime the affected area of the ground, to be further raked and cleaned upon drying. | 07/05/2017 01:20 PM | East Field Slopes Condominium Association | 9519 Fieldview Circle; Thonotosassa FL |  | Melisa Rotteveel | US Water Services | mrotteveel@uswatercorp.net | (866) 753-8292 | 207 | Operator Of the Facility | Melisa Rotteveel | (866) 753-8292 |  | mrotteveel@uswatercorp.net | 07/05/2017 08:00 AM | 07/05/2017 08:10 AM | Hillsborough |  | N | 28.044962 | -82.331536 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=8
1327 Lodge Cir. Spring Hill, FL |  | Force main break on a 6'' line. Spill was approximately 480 gallons. | 07/05/2017 10:04 AM | Hernando County Utilities Department | 15400 Wiscon Rd Brooksville, FL 34601; 1327 Lodge Cir. Spring Hill FL | Off of Spring Hill Dr. | Bruce Batten | Foreman | bbatten@co.hernando.fl.us | (352) 754-4490 |  | Operator Of the Facility | Larry Cooper | (352) 754-4490 |  | lcooper@co.hernando.fl.us | 07/04/2017 09:00 AM | 07/04/2017 01:00 PM | Hernando |  |  | 28.450475 | -82.596227 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=7
725 Balmoral Rd. | 20174952 | Power outage/ lightning, burnt components in lift station control cabinet | 07/05/2017 09:36 AM | Lift Station #8 | 724 Balmoral Rd.; Winter Park FL |  | Lon C. Katschor | Utility Maintenance Division Chief | lkatschor@cityofwinterpark.org | (407) 599-3570 |  | Manager of the Facility/Installation | Lon C. Katschor | (407) 599-3570 |  | lkatschor@cityofwinterpark.org | 07/01/2017 03:30 PM | 07/01/2017 05:30 PM | Orange |  |  | 28.586309 | -81.329568 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=6
6903 Muinicipal Dr. | 20174963 | This report is to notify you of a sewage spill that occurred on June 30, 2017, at approximately 7:00 p.m. The estimated spillage was approximately 10,000 gallons and occurred at 6903 Municipal Dr., Milton, FL, 32570. The responsible permittee, City of Milton Water & Sewer Department; WWT Facility Permit #FL0021903, 5438 Alabama Street, Milton, Fl. 32570; Phone (850) 983-5434, Fax: (850) 983-5439, has attempted to contact all appropriate entities. Please note below. The discharge ceased around 10:30 a.m. on July 1, 2017, by-pass pumping was not used. The spillage was from a manhole caused by a dirt blockage. The untreated domestic spillage was not contained. It ran into a drainage ditch that is approximately 1030 feet long and empties into the Blackwater River. The Water/ Sewer Department has cleaned the area of the spill by applying chlorine bleach and disinfected the area using Ban-O. Water samples will be collected and the results will be faxed over to Dana Vestal with FL. D.E.P. @ 850-595-8097. | 07/03/2017 01:07 PM | Manhole on the side of the road, by 6903 Municipal Dr. | FL |  | Jo Robey Groenenboom | Admin. Assistant | jo.robey@ci.milton.fl.us | (850) 983-5434 |  | Employee @ the City of Milton Utilities Department | Joe Cook | (850) 698-9244 |  | joe.cook@ci.milton.fl.us | 06/30/2017 07:00 PM | 07/01/2017 10:30 AM | Santa Rosa |  |  | 30.617649 | -87.035726 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=5
OUA, force main leak 1619 SW 35th Circle 07032017 | 20174971 | Force Main broke behind 1619 SW 35th Circle, 34974 Addendum 7/5/2017: upstream lift station was immediately shut off to stop the flow; pipe was repaired and placed back into service by 1530 on 7/3/2017. | 07/03/2017 12:48 PM | Okeechobee Utility Authority Cemetery Road WWTF FLA013888 | FL | This spill did not occur at the treatment plant site. | Jamie Gamiotea | WWTF Supervisor | jgamiotea@ouafl.com | (863) 763-3322 |  | Operator Of the Facility | Jamie Gamiotea | (863) 763-3322 |  | jgamiotea@ouafl.com | 07/03/2017 11:30 AM | 07/03/2017 03:30 PM | Okeechobee |  | N | 27.210057 | -80.836762 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=4
Lift station electrical failure | 20174966 | Lift Station fail to operator due to a electrical problem, which cause the pumps to malfunction. resulting in raw sewage overflow estimated 100 gallons, the area impacted was cleaned and treat with lime. | 07/03/2017 10:57 AM | Lift Station # 7 | 205 Jeffords Street; Clearwatr FL |  | Kervin St Aimie | Utilites Maintenance Coordinator | kervin.staimie@myclearwater.com | (727) 642-1693 |  | Operator Of the Facility | Kervin St Aimie | (727) 642-1693 |  | kervin.staimie@myclearwater.com | 07/02/2017 01:30 PM | 07/02/2017 02:00 PM | Pinellas |  |  | 27.959445 | -82.836768 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=3
MDV-Spartannash | 20174943 | N\NATIONAL RESPONSE CENTER 1-800-424-8802 *** For Public Use *** Information released to a third party shall comply with any applicable federal and/or state Freedom of Information and Privacy Laws Incident Report # 1182893 INCIDENT DESCRIPTION *Report taken at 00:41 on 02-JUL-17 Incident Type: FIXED Incident Cause: EQUIPMENTFAILURE AffectedArea: Incident occurred on 01-JUL-17 at 21:30 local incident time. Affected Medium: AIR ATMOSPHERE _______________________________________________________________________ SUSPECTED RESPONSIBLE PARTY Organization: SPARTANNASH PENSACOLA, FL32505 Type of Organization: PRIVATE ENTERPRISE ________________________________________________________________________ INCIDENT LOCATION 4150 WEST BLOUNT County:ESCAMBIA City: PENSACOLA State: FL Zip:32505 GROCERY WAREHOUSE _______________________________________________________________________ RELEASED MATERIAL(S) CHRIS Code:AMA Official Material Name: AMMONIA, ANHYDROUS Also Known As: Qty Released: 100 POUND(S) ________________________________________________________________________ DESCRIPTION OF INCIDENT OVER 100 POUNDS OF ANHYDROUS AMMONIA RELEASED FROM A REFRIGERATION SYSTEM DUE TO A TANK FAILURE. ________________________________________________________________________ INCIDENT DETAILS Package:N/A BuildingID: Type of Fixed Object:WAREHOUSE Power Generating Facility:NO GeneratingCapacity: Type ofFuel: NPDES: NPDES Compliance:UNKNOWN ______________________________________________________________________ IMPACT Fire Involved: NO Fire Extinguished: UNKNOWN INJURIES: NO Hospitalized: Empl/Crew: Passenger: FATALITIES: NO Empl/Crew: Passenger: Occupant: EVACUATIONS:NO Who Evacuated: Radius/Area: Damages: NO Hours Direction of Closure Type Description of Closure Closed Closure N Air: N Major Road: Artery:N N Waterway: N Track: Environmental Impact:UNKNOWN Media Interest: UNKNOWN Community Impact due to Material: ______________________________________________________________________ REMEDIAL ACTIONS FIRE DEPT IS ONSITE AND THE BUILDING IS CLOSED OFF. Release Secured:YES ReleaseRate: Estimated Release Duration: 3.5HOUR ______________________________________________________________________ WEATHER Weather: CLEAR,81?F ______________________________________________________________________ ADDITIONAL AGENCIES NOTIFIED Federal: State/Local: State/Local On Scene: FIRE DEPT State Agency Number: _______________________________________________________________________ | 07/02/2017 12:32 PM | MDV-Spartannash | 4150 West Blount Strret; Pensacola FL; 32505 |  | Robert Kelly | Distribution Director | Robert.Kelly@spartannash.com | (337) 230-8557 |  | Operator Of the Facility | Robert Kelly | (337) 230-8557 |  | Robert.Kelly@spartannash.com | 07/01/2017 09:10 PM | 07/02/2017 12:10 AM | Escambia | Escambia | Y | 30.428163 | -87.262838 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=2
200 Country Club Drive | 20174927 | There was a pump failure at the Lift Station that caused 5 manholes to overflow downstream of the lift station. Approximately 3,750 gallons flowed overland into a ditch leading to a retention pond. | 07/02/2017 11:00 AM | City of Largo WWRF | 5100 150th Ave N; Clearwater FL |  | Donna Dessoir | Environmental Control Supervisor | dodessoi@largo.com | (727) 507-4491 |  | Environmental Control Supervisor for the Facility | Donna Dessoir | (727) 507-4491 |  | dodessoi@largo.com | 06/30/2017 04:30 PM | 06/30/2017 04:45 PM | Pinellas |  |  | 27.913382 | -82.770905 | https://prodenv.dep.state.fl.us:443/DepPNP/reports/viewMapDirectLink?point=yes&incidentDetailKey=1